## Protected Zone
Surge Arrestors Local To Grid Transformer - Assessment Of Required Position
Instructions
1 Enter appropriate figures in blue cells; see notes.
2 Read off total acceptable length for d+d1+d2+dA; see figures.
Notes
N = No. of lines connected to substation (take account of typical outages) |  |  |  |  | 1 | line(s) | Typically 1 or 2. | Line Type |  |  | Factor A (kV)
A = Lightning performance voltage for the line voltage/type |  |  |  |  | 4500 | kV | See Table 1. | Transmission | Single conductor |  | 4500
Urw = Equipment rated lightning impulse withstand voltage (BIL) |  |  |  |  | 550 | kV | See EE Spec 1/2. |  | Double conductor bundle (twin) |  | 7000
Upl = Arrester Lightning Impulse Level |  |  |  |  | 311 | kV | See Table 2 or 3. |  | Four conductor bundle (quad) |  | 11000
Lsp = Span length of first span of overhead line |  |  |  |  | 300 | m |  | Distribution | Unearthed wood pole |  | 2700
Lf = Overhead line section with outage rate equal to acceptable failure rate |  |  |  |  | 50 |  |  |  | Earthed construction wood pole |  | 900
Ra = Acceptable failure rate of protected equipment | 1 | failure in | 1000 | years | 0.001 | failures/year |  | Table 1 (taken from EN 60099-5)
r = Line outage rate for first km out | 2 | fault(s) per | 100 | km per year/circuit | 2e-05 | failures/year/m
[8 empty] | Arrestor Type | Rated Arrestor | Rated Discharge | Upl (kV)
Lp = arrester protective zone = Lt = total acceptable length d+d1+d2+dA |  |  |  |  | 13.0092 | m |  |  | Voltage (kV) | Current
[8 empty] | ABB type | 132 | 10kA | 311
PEXLIMQ132-WV145
[8 empty] | Bowthorpe type | 132 | 10kA | 333
2P4SR132
[8 empty] | Bowthorpe | 36 | 10kA | 102
[8 empty] | Metal-oxide gapless | 45 | 10kA | 123
Table 2
[8 empty] | Arrestor Type | Rated Arrestor | Rated Discharge | Upl (kV)
[9 empty] | Voltage (kV) | Current
[8 empty] | Gapped to IEC 99-1 | 132 | 10kA Heavy-duty | 343.2
[9 empty] | 36 | 10kA Heavy-duty | 100.8
[8 empty] | Metal-oxide gapless | 132 | 10kA | 303.6-435.6
[8 empty] | to IEC 99-4 | 36 | 10kA | 82.8-118.8
[9 empty] | 45 | 10kA | 103.5-148.5
Table 3
NB Assumes interconnected earth grid.
Calculation method as per EN 60099-5, IEC 99-5 & IEC 71-2:
Eq 1.0 Lp = N/A((Urw/1.15)-Upl)(Lsp+Lf)
Eq 2.0 Lf = Ra/r