## Arrangement B
ARRANGEMENT B
Transformer Rating: | 1000 | kVA
Cabinet Type: | XIII | 800A MCCB & 2 additional fuseways
HV Fault Level | 50 | MVA
Load Type | Power (kVA) | Power Factor |  | Current (A)
Load connected to metering MCCB:
Maximum Import | 300 | 0.98 | Lagging | 434.7826
Maximum Export | 0 | 1 | Lagging | 0
Total load connected to fuseways:
Maximum Import | 200 | 0.98 | Lagging | 289.8551
Maximum Export | 0 | 1 | Lagging | 0
Total substation load:
Maximum Import | 500 | 0.98 | Lagging | 724.6377
Maximum Export | 0 | 1 | Leading | 0
| Settings for T/F MCCB |  |  |  | Settings for Metering MCCB
|  | Trip Unit: | Micrologic 5.0 |  |  | Trip Unit: | Micrologic 5.0
|  | ACB Rating, In : | 800A |  |  | ACB Rating, In : | 800A
|  | Ir : | 560A (i.e. 0.7xIn) |  |  | Ir : | 480A (i.e. 0.6xIn)
|  | tr : | 8s |  |  | tr : | 8s
|  | Isd : | 3360A (i.e. 6xIr) |  |  | Isd : | 2400A (i.e. 5xIr)
|  | tsd : | 0.2s, IxIxt on |  |  | tsd : | 0.1s, IxIxt on
|  | Ii : | 8000A (i.e. 10xIn) |  |  | Ii : | 6400A (i.e. 8xIn)
|  | Ig : | N/A |  |  | Ig : | N/A
|  | tg : | N/A |  |  | tg : | N/A
MCCB CIRCUIT 1
[5 empty] | Laid |  | Sustained Ratings (A) |  |  |  | Cyclic Ratings (A)
Cable Type: | 4 x 600 sqmm (SOLIDAL) | [5 empty] | Spring | Summer | Autumn | Winter | Spring | Summer | Autumn | Winter
[5 empty] | In Ground |  | 726 | 673 | 712 | 785 | 840 | 784 | 826 | 900
Maximum Cable Length (m): |  | 150 |  |  | In PVC Duct |  | 601 | 572 | 595 | 628 | 671 | 646 | 667 | 692
[5 empty] | In Rigiduct |  | 557 | 533 | 552 | 579 | 611 | 590 | 608 | 628
Cable Length Limited by: |  | Practical Considerations |  |  | In Air |  | 912 | 838 | 912 | 947 | 912 | 838 | 912 | 947
NOTE: SOLIDALS MUST BE LAID IN TREFOIL ARRANGEMENT |  |  |  |  | MCCB Connection 1 - Characteristics
[5 empty] | Proposed Cable Length (m): |  |  |  | 50
[5 empty] | Maximum Voltage drop (% of 230V): |  |  |  | 2.3964
[5 empty] | Maximum Voltage Rise (% of 230V): |  |  |  | 0
[5 empty] | Prospective 3 Phase Fault Current (A): |  |  |  | 14147.7366
[5 empty] | Prospective Earth Fault Current (A): |  |  |  | 11455.9499 |  | Note: Fault levels exclude any generator Infeed
[5 empty] | Maximum 3ph Fault Impedance (Ω): |  |  |  | 0.017671
[5 empty] | Maximum Earth Fault Loop Impednace (Ω): |  |  |  | 0.021823
MCCB CIRCUIT 2
[5 empty] | Laid |  | Sustained Ratings (A) |  |  |  | Cyclic Ratings (A)
Cable Type: | 4 x 600 sqmm (SOLIDAL) | [5 empty] | Spring | Summer | Autumn | Winter | Spring | Summer | Autumn | Winter
[5 empty] | In Ground |  | 726 | 673 | 712 | 785 | 840 | 784 | 826 | 900
Maximum Cable Length (m): |  | 150 |  |  | In PVC Duct |  | 601 | 572 | 595 | 628 | 671 | 646 | 667 | 692
[5 empty] | In Rigiduct |  | 557 | 533 | 552 | 579 | 611 | 590 | 608 | 628
Cable Length Limitation: |  | Practical Considerations |  |  | In Air |  | 912 | 838 | 912 | 947 | 912 | 838 | 912 | 947
NOTE: SOLIDALS MUST BE LAID IN TREFOIL ARRANGEMENT |  |  |  |  | MCCB Connection 2 - Characteristics
[5 empty] | Proposed Cable Length (m): |  |  |  | 100
[5 empty] | Maximum Voltage drop (% of 230V): |  |  |  | 2.7895
[5 empty] | Maximum Voltage Rise (% of 230V): |  |  |  | 0
[5 empty] | Prospective 3 Phase Fault Current (A): |  |  |  | 10883.8204
[5 empty] | Prospective Earth Fault Current (A): |  |  |  | 8254.0507 |  | Note: Fault levels exclude generator Infeed
[5 empty] | Maximum 3ph Fault Impedance (Ω): |  |  |  | 0.02297
[5 empty] | Maximum Earth Fault Loop Impednace (Ω): |  |  |  | 0.030288

## Arrangement C
ARRANGEMENT C
Transformer Rating: | 500 | kVA |  |  |  | Settings for Metering MCCB
HV Fault Level | 50 | MVA
[7 empty] | Trip Unit: | Micrologic 5.0
Load Type | Power (kVA) | Power Factor |  | Current (A) |  |  | ACB Rating, In : | 800A
[7 empty] | Ir : | 760A (i.e. 0.95xIn)
Maximum Import | 500 | 0.98 | Lagging | 724.6377 |  |  | tr : | 8s
Maximum Export | 0 | 1 | Lagging | 0 |  |  | Isd : | 2280A (i.e. 3xIr)
[7 empty] | tsd : | 0.1s, IxIxt on
[7 empty] | Ii : | 6400A (i.e. 6xIn)
[7 empty] | Ig : | N/A
[7 empty] | tg : | N/A
CIRCUIT
[5 empty] | Laid |  | Sustained Ratings (A) |  |  |  | Cyclic Ratings (A)
Cable Type: | 7 x 600 sqmm (SOLIDAL) | [5 empty] | Spring | Summer | Autumn | Winter | Spring | Summer | Autumn | Winter
[5 empty] | In Ground |  | 1288 | 1190 | 1234 | 1396 | 1544 | 1438 | 1488 | 1662
Maximum Cable Length (m): |  | 20 |  |  | In PVC Duct |  | 1122 | 1062 | 1088 | 1180 | 1282 | 1230 | 1250 | 1332
[5 empty] | In Rigiduct |  | 1052 | 1034 | 1020 | 1098 | 1178 | 1134 | 1148 | 1216
Comment: |  |  |  |  | In Air |  | 1824 | 1676 | 1824 | 1894 | 1824 | 1676 | 1824 | 1894
Connection Characteristics
NOTE: SOLIDALS MUST BE LAID IN TREFOIL ARRANGEMENT |  |  |  |  | Proposed Cable Length (m): |  |  |  | 20
[5 empty] | Maximum Voltage drop (% of 230V): |  |  |  | 2.6437
[5 empty] | Maximum Voltage Rise (% of 230V): |  |  |  | 0
[5 empty] | Prospective 3 Phase Fault Current (A): |  |  |  | 11120.8805
[5 empty] | Prospective Earth Fault Current (A): |  |  |  | 10699.8837 |  | Note: Fault levels exclude generator Infeed
[5 empty] | Maximum 3ph Fault Impedance (Ω): |  |  |  | 0.02248
[5 empty] | Maximum Earth Fault Loop Impednace (Ω): |  |  |  | 0.023365

## B_Calculations (hidden)
Arrangement B - Power
Circuit 1 Import | [7 empty] | Circuit 2 Import | [7 empty] | Total Import
Phase Current |  |  |  | Neutral Current |  |  |  | Phase Current |  |  |  | Neutral Current |  |  |  | Phase Current |  |  |  | Neutral Current
Ipz1 | Ipr1 | Ipx1 | qph1 | Inz1 | Inr1 | Inx1 | qn1 | Ipz2 | Ipr2 | Ipx2 | qph2 | Inz2 | Inr2 | Inx2 | qn2 | Ipzt | Iprt | Ipxt | qpht | Inzt | Inrt | Inxt | qnt
434.7826 | 426.087 | 86.5206 | 11.4783 | 217.3913 | 213.0435 | 43.2603 | 11.4783 | 289.8551 | 284.058 | 57.6804 | 11.4783 | 144.9275 | 142.029 | 28.8402 | 11.4783 | 724.6377 | 710.1449 | 144.2011 | 11.4783 | 362.3188 | 355.0725 | 144.2011 | 11.4783
Circuit 1 Export | [7 empty] | Circuit 2 Export | [7 empty] | Total Export
Phase Current |  |  |  | Neutral Current |  |  |  | Phase Current |  |  |  | Neutral Current |  |  |  | Phase Current |  |  |  | Neutral Current
Ipz1 | Ipr1 | Ipx1 | qph1 | Inz1 | Inr1 | Inx1 | qn1 | Ipz2 | Ipr2 | Ipx2 | qph2 | Inz2 | Inr2 | Inx2 | qn2 | Ipzt | Iprt | Ipxt | qpht | Inzt | Inrt | Inxt | qnt
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[24 empty] | T/F Resistance: | 0.00219 | Ω
[24 empty] | T/F Reactance: | 0.00863 | Ω
[24 empty] | T/F Voltage Drop: | 2.7997 | V
[24 empty] | T/F Voltage Rise: | 0 | V
Source Impedance
[27 empty] | Source R: | 0 | Ω
[27 empty] | Source X: | 0.0037498 | Ω
Circuit 1 Voltage Drop calculation
[30 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[30 empty] | 0.028548 | 0.0076138 | 0.014274 | 0.0038069 | 287.6036
Circuit 1 Voltage Rise Calculation
[30 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[30 empty] | 0 | 0 | 0 | 0 | 10000
Circuit 2 Voltage Drop Calculation
[30 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[30 empty] | 0.019032 | 0.0050759 | 0.0095159 | 0.0025379 | 508.8264
Circuit 2 Voltage Rise Calculation
[30 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[30 empty] | 0 | 0 | 0 | 0 | 10000
Circuit 1 Fault Calculation
[37 empty] | Cable Impedance (Ω) |  |  |  | T/F + Cable Impedance (Ω) | [5 empty] | Maximum Cable Length: | 151
[35 empty] | FL Lookup | Cable Length (m) | RC1 | XC1 | RC0 | XC0 | R1 | X1 | R0 | X0 | Earth Fault level (A) | 3 Ph Fault level (A)
[35 empty] | 0 | 151 | 0.010117 | 0.013288 | 0.040468 | 0.053152 | 0.012307 | 0.025668 | 0.042658 | 0.061782 | 5698.6695 | 8782.4937
[35 empty] | 5698.6695 | 150 | 0.01005 | 0.0132 | 0.0402 | 0.0528 | 0.01224 | 0.02558 | 0.04239 | 0.06143 | 5727.3596 | 8816.0376
[35 empty] | 5727.3596 | 149 | 0.009983 | 0.013112 | 0.039932 | 0.052448 | 0.012173 | 0.025492 | 0.042122 | 0.061078 | 5756.338 | 8849.8332
[35 empty] | 5756.338 | 148 | 0.009916 | 0.013024 | 0.039664 | 0.052096 | 0.012106 | 0.025404 | 0.041854 | 0.060726 | 5785.6092 | 8883.8832
[35 empty] | 5785.6092 | 147 | 0.009849 | 0.012936 | 0.039396 | 0.051744 | 0.012039 | 0.025316 | 0.041586 | 0.060374 | 5815.1775 | 8918.1905
[35 empty] | 5815.1775 | 146 | 0.009782 | 0.012848 | 0.039128 | 0.051392 | 0.011972 | 0.025228 | 0.041318 | 0.060022 | 5845.0475 | 8952.7579
[35 empty] | 5845.0475 | 145 | 0.009715 | 0.01276 | 0.03886 | 0.05104 | 0.011905 | 0.02514 | 0.04105 | 0.05967 | 5875.2238 | 8987.5883
[35 empty] | 5875.2238 | 144 | 0.009648 | 0.012672 | 0.038592 | 0.050688 | 0.011838 | 0.025052 | 0.040782 | 0.059318 | 5905.7111 | 9022.6846
[35 empty] | 5905.7111 | 143 | 0.009581 | 0.012584 | 0.038324 | 0.050336 | 0.011771 | 0.024964 | 0.040514 | 0.058966 | 5936.5141 | 9058.0498
[35 empty] | 5936.5141 | 142 | 0.009514 | 0.012496 | 0.038056 | 0.049984 | 0.011704 | 0.024876 | 0.040246 | 0.058614 | 5967.6379 | 9093.6869
[35 empty] | 5967.6379 | 141 | 0.009447 | 0.012408 | 0.037788 | 0.049632 | 0.011637 | 0.024788 | 0.039978 | 0.058262 | 5999.0873 | 9129.5991
[35 empty] | 5999.0873 | 140 | 0.00938 | 0.01232 | 0.03752 | 0.04928 | 0.01157 | 0.0247 | 0.03971 | 0.05791 | 6030.8675 | 9165.7894
[35 empty] | 6030.8675 | 139 | 0.009313 | 0.012232 | 0.037252 | 0.048928 | 0.011503 | 0.024612 | 0.039442 | 0.057558 | 6062.9836 | 9202.2611
[35 empty] | 6062.9836 | 138 | 0.009246 | 0.012144 | 0.036984 | 0.048576 | 0.011436 | 0.024524 | 0.039174 | 0.057206 | 6095.4411 | 9239.0172
[35 empty] | 6095.4411 | 137 | 0.009179 | 0.012056 | 0.036716 | 0.048224 | 0.011369 | 0.024436 | 0.038906 | 0.056854 | 6128.2452 | 9276.0611
[35 empty] | 6128.2452 | 136 | 0.009112 | 0.011968 | 0.036448 | 0.047872 | 0.011302 | 0.024348 | 0.038638 | 0.056502 | 6161.4017 | 9313.396
[35 empty] | 6161.4017 | 135 | 0.009045 | 0.01188 | 0.03618 | 0.04752 | 0.011235 | 0.02426 | 0.03837 | 0.05615 | 6194.916 | 9351.0254
[35 empty] | 6194.916 | 134 | 0.008978 | 0.011792 | 0.035912 | 0.047168 | 0.011168 | 0.024172 | 0.038102 | 0.055798 | 6228.7941 | 9388.9526
[35 empty] | 6228.7941 | 133 | 0.008911 | 0.011704 | 0.035644 | 0.046816 | 0.011101 | 0.024084 | 0.037834 | 0.055446 | 6263.0418 | 9427.181
[35 empty] | 6263.0418 | 132 | 0.008844 | 0.011616 | 0.035376 | 0.046464 | 0.011034 | 0.023996 | 0.037566 | 0.055094 | 6297.6651 | 9465.7143
[35 empty] | 6297.6651 | 131 | 0.008777 | 0.011528 | 0.035108 | 0.046112 | 0.010967 | 0.023908 | 0.037298 | 0.054742 | 6332.6702 | 9504.5559
[35 empty] | 6332.6702 | 130 | 0.00871 | 0.01144 | 0.03484 | 0.04576 | 0.0109 | 0.02382 | 0.03703 | 0.05439 | 6368.0634 | 9543.7094
[35 empty] | 6368.0634 | 129 | 0.008643 | 0.011352 | 0.034572 | 0.045408 | 0.010833 | 0.023732 | 0.036762 | 0.054038 | 6403.8511 | 9583.1786
[35 empty] | 6403.8511 | 128 | 0.008576 | 0.011264 | 0.034304 | 0.045056 | 0.010766 | 0.023644 | 0.036494 | 0.053686 | 6440.04 | 9622.9672
[35 empty] | 6440.04 | 127 | 0.008509 | 0.011176 | 0.034036 | 0.044704 | 0.010699 | 0.023556 | 0.036226 | 0.053334 | 6476.6366 | 9663.0789
[35 empty] | 6476.6366 | 126 | 0.008442 | 0.011088 | 0.033768 | 0.044352 | 0.010632 | 0.023468 | 0.035958 | 0.052982 | 6513.648 | 9703.5176
[35 empty] | 6513.648 | 125 | 0.008375 | 0.011 | 0.0335 | 0.044 | 0.010565 | 0.02338 | 0.03569 | 0.05263 | 6551.0811 | 9744.2871
[35 empty] | 6551.0811 | 124 | 0.008308 | 0.010912 | 0.033232 | 0.043648 | 0.010498 | 0.023292 | 0.035422 | 0.052278 | 6588.9431 | 9785.3915
[35 empty] | 6588.9431 | 123 | 0.008241 | 0.010824 | 0.032964 | 0.043296 | 0.010431 | 0.023204 | 0.035154 | 0.051926 | 6627.2414 | 9826.8347
[35 empty] | 6627.2414 | 122 | 0.008174 | 0.010736 | 0.032696 | 0.042944 | 0.010364 | 0.023116 | 0.034886 | 0.051574 | 6665.9834 | 9868.6209
[35 empty] | 6665.9834 | 121 | 0.008107 | 0.010648 | 0.032428 | 0.042592 | 0.010297 | 0.023028 | 0.034618 | 0.051222 | 6705.1769 | 9910.7542
[35 empty] | 6705.1769 | 120 | 0.00804 | 0.01056 | 0.03216 | 0.04224 | 0.01023 | 0.02294 | 0.03435 | 0.05087 | 6744.8297 | 9953.2388
[35 empty] | 6744.8297 | 119 | 0.007973 | 0.010472 | 0.031892 | 0.041888 | 0.010163 | 0.022852 | 0.034082 | 0.050518 | 6784.9499 | 9996.079
[35 empty] | 6784.9499 | 118 | 0.007906 | 0.010384 | 0.031624 | 0.041536 | 0.010096 | 0.022764 | 0.033814 | 0.050166 | 6825.5457 | 10039.2791
[35 empty] | 6825.5457 | 117 | 0.007839 | 0.010296 | 0.031356 | 0.041184 | 0.010029 | 0.022676 | 0.033546 | 0.049814 | 6866.6255 | 10082.8435
[35 empty] | 6866.6255 | 116 | 0.007772 | 0.010208 | 0.031088 | 0.040832 | 0.009962 | 0.022588 | 0.033278 | 0.049462 | 6908.1979 | 10126.7767
[35 empty] | 6908.1979 | 115 | 0.007705 | 0.01012 | 0.03082 | 0.04048 | 0.009895 | 0.0225 | 0.03301 | 0.04911 | 6950.2718 | 10171.0834
[35 empty] | 6950.2718 | 114 | 0.007638 | 0.010032 | 0.030552 | 0.040128 | 0.009828 | 0.022412 | 0.032742 | 0.048758 | 6992.8561 | 10215.768
[35 empty] | 6992.8561 | 113 | 0.007571 | 0.009944 | 0.030284 | 0.039776 | 0.009761 | 0.022324 | 0.032474 | 0.048406 | 7035.9603 | 10260.8354
[35 empty] | 7035.9603 | 112 | 0.007504 | 0.009856 | 0.030016 | 0.039424 | 0.009694 | 0.022236 | 0.032206 | 0.048054 | 7079.5936 | 10306.2902
[35 empty] | 7079.5936 | 111 | 0.007437 | 0.009768 | 0.029748 | 0.039072 | 0.009627 | 0.022148 | 0.031938 | 0.047702 | 7123.7659 | 10352.1374
[35 empty] | 7123.7659 | 110 | 0.00737 | 0.00968 | 0.02948 | 0.03872 | 0.00956 | 0.02206 | 0.03167 | 0.04735 | 7168.487 | 10398.3818
[35 empty] | 7168.487 | 109 | 0.007303 | 0.009592 | 0.029212 | 0.038368 | 0.009493 | 0.021972 | 0.031402 | 0.046998 | 7213.7671 | 10445.0286
[35 empty] | 7213.7671 | 108 | 0.007236 | 0.009504 | 0.028944 | 0.038016 | 0.009426 | 0.021884 | 0.031134 | 0.046646 | 7259.6168 | 10492.0827
[35 empty] | 7259.6168 | 107 | 0.007169 | 0.009416 | 0.028676 | 0.037664 | 0.009359 | 0.021796 | 0.030866 | 0.046294 | 7306.0466 | 10539.5493
[35 empty] | 7306.0466 | 106 | 0.007102 | 0.009328 | 0.028408 | 0.037312 | 0.009292 | 0.021708 | 0.030598 | 0.045942 | 7353.0675 | 10587.4338
[35 empty] | 7353.0675 | 105 | 0.007035 | 0.00924 | 0.02814 | 0.03696 | 0.009225 | 0.02162 | 0.03033 | 0.04559 | 7400.6907 | 10635.7414
[35 empty] | 7400.6907 | 104 | 0.006968 | 0.009152 | 0.027872 | 0.036608 | 0.009158 | 0.021532 | 0.030062 | 0.045238 | 7448.9278 | 10684.4777
[35 empty] | 7448.9278 | 103 | 0.006901 | 0.009064 | 0.027604 | 0.036256 | 0.009091 | 0.021444 | 0.029794 | 0.044886 | 7497.7906 | 10733.648
[35 empty] | 7497.7906 | 102 | 0.006834 | 0.008976 | 0.027336 | 0.035904 | 0.009024 | 0.021356 | 0.029526 | 0.044534 | 7547.2911 | 10783.2581
[35 empty] | 7547.2911 | 101 | 0.006767 | 0.008888 | 0.027068 | 0.035552 | 0.008957 | 0.021268 | 0.029258 | 0.044182 | 7597.4418 | 10833.3136
[35 empty] | 7597.4418 | 100 | 0.0067 | 0.0088 | 0.0268 | 0.0352 | 0.00889 | 0.02118 | 0.02899 | 0.04383 | 7648.2554 | 10883.8204
[35 empty] | 7648.2554 | 99 | 0.006633 | 0.008712 | 0.026532 | 0.034848 | 0.008823 | 0.021092 | 0.028722 | 0.043478 | 7699.745 | 10934.7843
[35 empty] | 7699.745 | 98 | 0.006566 | 0.008624 | 0.026264 | 0.034496 | 0.008756 | 0.021004 | 0.028454 | 0.043126 | 7751.924 | 10986.2114
[35 empty] | 7751.924 | 97 | 0.006499 | 0.008536 | 0.025996 | 0.034144 | 0.008689 | 0.020916 | 0.028186 | 0.042774 | 7804.8062 | 11038.1077
[35 empty] | 7804.8062 | 96 | 0.006432 | 0.008448 | 0.025728 | 0.033792 | 0.008622 | 0.020828 | 0.027918 | 0.042422 | 7858.4056 | 11090.4795
[35 empty] | 7858.4056 | 95 | 0.006365 | 0.00836 | 0.02546 | 0.03344 | 0.008555 | 0.02074 | 0.02765 | 0.04207 | 7912.7367 | 11143.333
[35 empty] | 7912.7367 | 94 | 0.006298 | 0.008272 | 0.025192 | 0.033088 | 0.008488 | 0.020652 | 0.027382 | 0.041718 | 7967.8145 | 11196.6748
[35 empty] | 7967.8145 | 93 | 0.006231 | 0.008184 | 0.024924 | 0.032736 | 0.008421 | 0.020564 | 0.027114 | 0.041366 | 8023.6543 | 11250.5112
[35 empty] | 8023.6543 | 92 | 0.006164 | 0.008096 | 0.024656 | 0.032384 | 0.008354 | 0.020476 | 0.026846 | 0.041014 | 8080.2717 | 11304.8489
[35 empty] | 8080.2717 | 91 | 0.006097 | 0.008008 | 0.024388 | 0.032032 | 0.008287 | 0.020388 | 0.026578 | 0.040662 | 8137.6828 | 11359.6947
[35 empty] | 8137.6828 | 90 | 0.00603 | 0.00792 | 0.02412 | 0.03168 | 0.00822 | 0.0203 | 0.02631 | 0.04031 | 8195.9042 | 11415.0554
[35 empty] | 8195.9042 | 89 | 0.005963 | 0.007832 | 0.023852 | 0.031328 | 0.008153 | 0.020212 | 0.026042 | 0.039958 | 8254.953 | 11470.9381
[35 empty] | 8254.953 | 88 | 0.005896 | 0.007744 | 0.023584 | 0.030976 | 0.008086 | 0.020124 | 0.025774 | 0.039606 | 8314.8467 | 11527.3498
[35 empty] | 8314.8467 | 87 | 0.005829 | 0.007656 | 0.023316 | 0.030624 | 0.008019 | 0.020036 | 0.025506 | 0.039254 | 8375.6032 | 11584.2978
[35 empty] | 8375.6032 | 86 | 0.005762 | 0.007568 | 0.023048 | 0.030272 | 0.007952 | 0.019948 | 0.025238 | 0.038902 | 8437.241 | 11641.7893
[35 empty] | 8437.241 | 85 | 0.005695 | 0.00748 | 0.02278 | 0.02992 | 0.007885 | 0.01986 | 0.02497 | 0.03855 | 8499.7792 | 11699.8319
[35 empty] | 8499.7792 | 84 | 0.005628 | 0.007392 | 0.022512 | 0.029568 | 0.007818 | 0.019772 | 0.024702 | 0.038198 | 8563.2373 | 11758.4332
[35 empty] | 8563.2373 | 83 | 0.005561 | 0.007304 | 0.022244 | 0.029216 | 0.007751 | 0.019684 | 0.024434 | 0.037846 | 8627.6354 | 11817.601
[35 empty] | 8627.6354 | 82 | 0.005494 | 0.007216 | 0.021976 | 0.028864 | 0.007684 | 0.019596 | 0.024166 | 0.037494 | 8692.9942 | 11877.343
[35 empty] | 8692.9942 | 81 | 0.005427 | 0.007128 | 0.021708 | 0.028512 | 0.007617 | 0.019508 | 0.023898 | 0.037142 | 8759.3351 | 11937.6674
[35 empty] | 8759.3351 | 80 | 0.00536 | 0.00704 | 0.02144 | 0.02816 | 0.00755 | 0.01942 | 0.02363 | 0.03679 | 8826.6799 | 11998.5822
[35 empty] | 8826.6799 | 79 | 0.005293 | 0.006952 | 0.021172 | 0.027808 | 0.007483 | 0.019332 | 0.023362 | 0.036438 | 8895.0513 | 12060.0958
[35 empty] | 8895.0513 | 78 | 0.005226 | 0.006864 | 0.020904 | 0.027456 | 0.007416 | 0.019244 | 0.023094 | 0.036086 | 8964.4724 | 12122.2167
[35 empty] | 8964.4724 | 77 | 0.005159 | 0.006776 | 0.020636 | 0.027104 | 0.007349 | 0.019156 | 0.022826 | 0.035734 | 9034.9672 | 12184.9533
[35 empty] | 9034.9672 | 76 | 0.005092 | 0.006688 | 0.020368 | 0.026752 | 0.007282 | 0.019068 | 0.022558 | 0.035382 | 9106.5604 | 12248.3146
[35 empty] | 9106.5604 | 75 | 0.005025 | 0.0066 | 0.0201 | 0.0264 | 0.007215 | 0.01898 | 0.02229 | 0.03503 | 9179.2773 | 12312.3093
[35 empty] | 9179.2773 | 74 | 0.004958 | 0.006512 | 0.019832 | 0.026048 | 0.007148 | 0.018892 | 0.022022 | 0.034678 | 9253.1441 | 12376.9466
[35 empty] | 9253.1441 | 73 | 0.004891 | 0.006424 | 0.019564 | 0.025696 | 0.007081 | 0.018804 | 0.021754 | 0.034326 | 9328.1878 | 12442.2356
[35 empty] | 9328.1878 | 72 | 0.004824 | 0.006336 | 0.019296 | 0.025344 | 0.007014 | 0.018716 | 0.021486 | 0.033974 | 9404.4363 | 12508.1859
[35 empty] | 9404.4363 | 71 | 0.004757 | 0.006248 | 0.019028 | 0.024992 | 0.006947 | 0.018628 | 0.021218 | 0.033622 | 9481.918 | 12574.8069
[35 empty] | 9481.918 | 70 | 0.00469 | 0.00616 | 0.01876 | 0.02464 | 0.00688 | 0.01854 | 0.02095 | 0.03327 | 9560.6627 | 12642.1084
[35 empty] | 9560.6627 | 69 | 0.004623 | 0.006072 | 0.018492 | 0.024288 | 0.006813 | 0.018452 | 0.020682 | 0.032918 | 9640.7008 | 12710.1003
[35 empty] | 9640.7008 | 68 | 0.004556 | 0.005984 | 0.018224 | 0.023936 | 0.006746 | 0.018364 | 0.020414 | 0.032566 | 9722.0639 | 12778.7926
[35 empty] | 9722.0639 | 67 | 0.004489 | 0.005896 | 0.017956 | 0.023584 | 0.006679 | 0.018276 | 0.020146 | 0.032214 | 9804.7842 | 12848.1958
[35 empty] | 9804.7842 | 66 | 0.004422 | 0.005808 | 0.017688 | 0.023232 | 0.006612 | 0.018188 | 0.019878 | 0.031862 | 9888.8955 | 12918.3202
[35 empty] | 9888.8955 | 65 | 0.004355 | 0.00572 | 0.01742 | 0.02288 | 0.006545 | 0.0181 | 0.01961 | 0.03151 | 9974.4322 | 12989.1766
[35 empty] | 9974.4322 | 64 | 0.004288 | 0.005632 | 0.017152 | 0.022528 | 0.006478 | 0.018012 | 0.019342 | 0.031158 | 10061.4301 | 13060.7757
[35 empty] | 10061.4301 | 63 | 0.004221 | 0.005544 | 0.016884 | 0.022176 | 0.006411 | 0.017924 | 0.019074 | 0.030806 | 10149.9261 | 13133.1287
[35 empty] | 10149.9261 | 62 | 0.004154 | 0.005456 | 0.016616 | 0.021824 | 0.006344 | 0.017836 | 0.018806 | 0.030454 | 10239.9583 | 13206.2467
[35 empty] | 10239.9583 | 61 | 0.004087 | 0.005368 | 0.016348 | 0.021472 | 0.006277 | 0.017748 | 0.018538 | 0.030102 | 10331.5661 | 13280.1413
[35 empty] | 10331.5661 | 60 | 0.00402 | 0.00528 | 0.01608 | 0.02112 | 0.00621 | 0.01766 | 0.01827 | 0.02975 | 10424.7903 | 13354.8241
[35 empty] | 10424.7903 | 59 | 0.003953 | 0.005192 | 0.015812 | 0.020768 | 0.006143 | 0.017572 | 0.018002 | 0.029398 | 10519.6729 | 13430.3071
[35 empty] | 10519.6729 | 58 | 0.003886 | 0.005104 | 0.015544 | 0.020416 | 0.006076 | 0.017484 | 0.017734 | 0.029046 | 10616.2575 | 13506.6024
[35 empty] | 10616.2575 | 57 | 0.003819 | 0.005016 | 0.015276 | 0.020064 | 0.006009 | 0.017396 | 0.017466 | 0.028694 | 10714.589 | 13583.7222
[35 empty] | 10714.589 | 56 | 0.003752 | 0.004928 | 0.015008 | 0.019712 | 0.005942 | 0.017308 | 0.017198 | 0.028342 | 10814.7141 | 13661.6792
[35 empty] | 10814.7141 | 55 | 0.003685 | 0.00484 | 0.01474 | 0.01936 | 0.005875 | 0.01722 | 0.01693 | 0.02799 | 10916.6809 | 13740.4862
[35 empty] | 10916.6809 | 54 | 0.003618 | 0.004752 | 0.014472 | 0.019008 | 0.005808 | 0.017132 | 0.016662 | 0.027638 | 11020.5393 | 13820.1563
[35 empty] | 11020.5393 | 53 | 0.003551 | 0.004664 | 0.014204 | 0.018656 | 0.005741 | 0.017044 | 0.016394 | 0.027286 | 11126.341 | 13900.7027
[35 empty] | 11126.341 | 52 | 0.003484 | 0.004576 | 0.013936 | 0.018304 | 0.005674 | 0.016956 | 0.016126 | 0.026934 | 11234.1394 | 13982.139
[35 empty] | 11234.1394 | 51 | 0.003417 | 0.004488 | 0.013668 | 0.017952 | 0.005607 | 0.016868 | 0.015858 | 0.026582 | 11343.9899 | 14064.4789
[35 empty] | 11343.9899 | 50 | 0.00335 | 0.0044 | 0.0134 | 0.0176 | 0.00554 | 0.01678 | 0.01559 | 0.02623 | 11455.9499 | 14147.7366
[35 empty] | 11455.9499 | 49 | 0.003283 | 0.004312 | 0.013132 | 0.017248 | 0.005473 | 0.016692 | 0.015322 | 0.025878 | 11570.079 | 14231.9263
[35 empty] | 11570.079 | 48 | 0.003216 | 0.004224 | 0.012864 | 0.016896 | 0.005406 | 0.016604 | 0.015054 | 0.025526 | 11686.4387 | 14317.0627
[35 empty] | 11686.4387 | 47 | 0.003149 | 0.004136 | 0.012596 | 0.016544 | 0.005339 | 0.016516 | 0.014786 | 0.025174 | 11805.0929 | 14403.1607
[35 empty] | 11805.0929 | 46 | 0.003082 | 0.004048 | 0.012328 | 0.016192 | 0.005272 | 0.016428 | 0.014518 | 0.024822 | 11926.108 | 14490.2353
[35 empty] | 11926.108 | 45 | 0.003015 | 0.00396 | 0.01206 | 0.01584 | 0.005205 | 0.01634 | 0.01425 | 0.02447 | 12049.5528 | 14578.302
[35 empty] | 12049.5528 | 44 | 0.002948 | 0.003872 | 0.011792 | 0.015488 | 0.005138 | 0.016252 | 0.013982 | 0.024118 | 12175.4986 | 14667.3765
[35 empty] | 12175.4986 | 43 | 0.002881 | 0.003784 | 0.011524 | 0.015136 | 0.005071 | 0.016164 | 0.013714 | 0.023766 | 12304.0194 | 14757.475
[35 empty] | 12304.0194 | 42 | 0.002814 | 0.003696 | 0.011256 | 0.014784 | 0.005004 | 0.016076 | 0.013446 | 0.023414 | 12435.1923 | 14848.6136
[35 empty] | 12435.1923 | 41 | 0.002747 | 0.003608 | 0.010988 | 0.014432 | 0.004937 | 0.015988 | 0.013178 | 0.023062 | 12569.097 | 14940.8091
[35 empty] | 12569.097 | 40 | 0.00268 | 0.00352 | 0.01072 | 0.01408 | 0.00487 | 0.0159 | 0.01291 | 0.02271 | 12705.8166 | 15034.0784
[35 empty] | 12705.8166 | 39 | 0.002613 | 0.003432 | 0.010452 | 0.013728 | 0.004803 | 0.015812 | 0.012642 | 0.022358 | 12845.4372 | 15128.4387
[35 empty] | 12845.4372 | 38 | 0.002546 | 0.003344 | 0.010184 | 0.013376 | 0.004736 | 0.015724 | 0.012374 | 0.022006 | 12988.0484 | 15223.9078
[35 empty] | 12988.0484 | 37 | 0.002479 | 0.003256 | 0.009916 | 0.013024 | 0.004669 | 0.015636 | 0.012106 | 0.021654 | 13133.7433 | 15320.5034
[35 empty] | 13133.7433 | 36 | 0.002412 | 0.003168 | 0.009648 | 0.012672 | 0.004602 | 0.015548 | 0.011838 | 0.021302 | 13282.6189 | 15418.244
[35 empty] | 13282.6189 | 35 | 0.002345 | 0.00308 | 0.00938 | 0.01232 | 0.004535 | 0.01546 | 0.01157 | 0.02095 | 13434.7759 | 15517.1481
[35 empty] | 13434.7759 | 34 | 0.002278 | 0.002992 | 0.009112 | 0.011968 | 0.004468 | 0.015372 | 0.011302 | 0.020598 | 13590.319 | 15617.2347
[35 empty] | 13590.319 | 33 | 0.002211 | 0.002904 | 0.008844 | 0.011616 | 0.004401 | 0.015284 | 0.011034 | 0.020246 | 13749.3573 | 15718.5231
[35 empty] | 13749.3573 | 32 | 0.002144 | 0.002816 | 0.008576 | 0.011264 | 0.004334 | 0.015196 | 0.010766 | 0.019894 | 13912.0044 | 15821.033
[35 empty] | 13912.0044 | 31 | 0.002077 | 0.002728 | 0.008308 | 0.010912 | 0.004267 | 0.015108 | 0.010498 | 0.019542 | 14078.3784 | 15924.7846
[35 empty] | 14078.3784 | 30 | 0.00201 | 0.00264 | 0.00804 | 0.01056 | 0.0042 | 0.01502 | 0.01023 | 0.01919 | 14248.6026 | 16029.7982
[35 empty] | 14248.6026 | 29 | 0.001943 | 0.002552 | 0.007772 | 0.010208 | 0.004133 | 0.014932 | 0.009962 | 0.018838 | 14422.8051 | 16136.0946
[35 empty] | 14422.8051 | 28 | 0.001876 | 0.002464 | 0.007504 | 0.009856 | 0.004066 | 0.014844 | 0.009694 | 0.018486 | 14601.1196 | 16243.6952
[35 empty] | 14601.1196 | 27 | 0.001809 | 0.002376 | 0.007236 | 0.009504 | 0.003999 | 0.014756 | 0.009426 | 0.018134 | 14783.6853 | 16352.6214
[35 empty] | 14783.6853 | 26 | 0.001742 | 0.002288 | 0.006968 | 0.009152 | 0.003932 | 0.014668 | 0.009158 | 0.017782 | 14970.6475 | 16462.8954
[35 empty] | 14970.6475 | 25 | 0.001675 | 0.0022 | 0.0067 | 0.0088 | 0.003865 | 0.01458 | 0.00889 | 0.01743 | 15162.1576 | 16574.5395
[35 empty] | 15162.1576 | 24 | 0.001608 | 0.002112 | 0.006432 | 0.008448 | 0.003798 | 0.014492 | 0.008622 | 0.017078 | 15358.3734 | 16687.5766
[35 empty] | 15358.3734 | 23 | 0.001541 | 0.002024 | 0.006164 | 0.008096 | 0.003731 | 0.014404 | 0.008354 | 0.016726 | 15559.4596 | 16802.03
[35 empty] | 15559.4596 | 22 | 0.001474 | 0.001936 | 0.005896 | 0.007744 | 0.003664 | 0.014316 | 0.008086 | 0.016374 | 15765.5881 | 16917.9232
[35 empty] | 15765.5881 | 21 | 0.001407 | 0.001848 | 0.005628 | 0.007392 | 0.003597 | 0.014228 | 0.007818 | 0.016022 | 15976.9381 | 17035.2804
[35 empty] | 15976.9381 | 20 | 0.00134 | 0.00176 | 0.00536 | 0.00704 | 0.00353 | 0.01414 | 0.00755 | 0.01567 | 16193.6968 | 17154.1262
[35 empty] | 16193.6968 | 19 | 0.001273 | 0.001672 | 0.005092 | 0.006688 | 0.003463 | 0.014052 | 0.007282 | 0.015318 | 16416.0595 | 17274.4856
[35 empty] | 16416.0595 | 18 | 0.001206 | 0.001584 | 0.004824 | 0.006336 | 0.003396 | 0.013964 | 0.007014 | 0.014966 | 16644.2301 | 17396.3839
[35 empty] | 16644.2301 | 17 | 0.001139 | 0.001496 | 0.004556 | 0.005984 | 0.003329 | 0.013876 | 0.006746 | 0.014614 | 16878.4214 | 17519.8472
[35 empty] | 16878.4214 | 16 | 0.001072 | 0.001408 | 0.004288 | 0.005632 | 0.003262 | 0.013788 | 0.006478 | 0.014262 | 17118.8559 | 17644.9016
[35 empty] | 17118.8559 | 15 | 0.001005 | 0.00132 | 0.00402 | 0.00528 | 0.003195 | 0.0137 | 0.00621 | 0.01391 | 17365.7655 | 17771.5739
[35 empty] | 17365.7655 | 14 | 0.000938 | 0.001232 | 0.003752 | 0.004928 | 0.003128 | 0.013612 | 0.005942 | 0.013558 | 17619.3927 | 17899.8916
[35 empty] | 17619.3927 | 13 | 0.000871 | 0.001144 | 0.003484 | 0.004576 | 0.003061 | 0.013524 | 0.005674 | 0.013206 | 17879.9904 | 18029.8822
[35 empty] | 17879.9904 | 12 | 0.000804 | 0.001056 | 0.003216 | 0.004224 | 0.002994 | 0.013436 | 0.005406 | 0.012854 | 18147.8229 | 18161.574
[35 empty] | 18147.8229 | 11 | 0.000737 | 0.000968 | 0.002948 | 0.003872 | 0.002927 | 0.013348 | 0.005138 | 0.012502 | 18423.166 | 18294.9956
[35 empty] | 18423.166 | 10 | 0.00067 | 0.00088 | 0.00268 | 0.00352 | 0.00286 | 0.01326 | 0.00487 | 0.01215 | 18706.3077 | 18430.1761
[35 empty] | 18706.3077 | 9 | 0.000603 | 0.000792 | 0.002412 | 0.003168 | 0.002793 | 0.013172 | 0.004602 | 0.011798 | 18997.5483 | 18567.1452
[35 empty] | 18997.5483 | 8 | 0.000536 | 0.000704 | 0.002144 | 0.002816 | 0.002726 | 0.013084 | 0.004334 | 0.011446 | 19297.2014 | 18705.9329
[35 empty] | 19297.2014 | 7 | 0.000469 | 0.000616 | 0.001876 | 0.002464 | 0.002659 | 0.012996 | 0.004066 | 0.011094 | 19605.5939 | 18846.5698
[35 empty] | 19605.5939 | 6 | 0.000402 | 0.000528 | 0.001608 | 0.002112 | 0.002592 | 0.012908 | 0.003798 | 0.010742 | 19923.0665 | 18989.0869
[35 empty] | 19923.0665 | 5 | 0.000335 | 0.00044 | 0.00134 | 0.00176 | 0.002525 | 0.01282 | 0.00353 | 0.01039 | 20249.9743 | 19133.5156
[35 empty] | 20249.9743 | 4 | 0.000268 | 0.000352 | 0.001072 | 0.001408 | 0.002458 | 0.012732 | 0.003262 | 0.010038 | 20586.6869 | 19279.8879
[35 empty] | 20586.6869 | 3 | 0.000201 | 0.000264 | 0.000804 | 0.001056 | 0.002391 | 0.012644 | 0.002994 | 0.009686 | 20933.5888 | 19428.2363
[35 empty] | 20933.5888 | 2 | 0.000134 | 0.000176 | 0.000536 | 0.000704 | 0.002324 | 0.012556 | 0.002726 | 0.009334 | 21291.0798 | 19578.5935
[35 empty] | 21291.0798 | 1 | 6.7e-05 | 8.8e-05 | 0.000268 | 0.000352 | 0.002257 | 0.012468 | 0.002458 | 0.008982 | 21659.5746 | 19730.9928
[35 empty] | 21659.5746 | 0 | 0 | 0 | 0 | 0 | 0.00219 | 0.01238 | 0.00219 | 0.00863 | 22039.5034 | 19885.468
Circuit 2 Fault Calculation
[37 empty] | Cable Impedance (Ω) |  |  |  | T/F + Cable Impedance (Ω) | [5 empty] | Maximum Cable Length: | 151
[35 empty] | FL Lookup | Cable Length (m) | RC1 | XC1 | RC0 | XC0 | R1 | X1 | R0 | X0 | Earth Fault level (A) | 3 Ph Fault level (A)
[35 empty] | 0 | 151 | 0.010117 | 0.013288 | 0.040468 | 0.053152 | 0.012307 | 0.025668 | 0.042658 | 0.061782 | 5698.6695 | 8782.4937
[35 empty] | 5698.6695 | 150 | 0.01005 | 0.0132 | 0.0132 | 0.0528 | 0.01224 | 0.02558 | 0.01539 | 0.06143 | 6279.2787 | 8816.0376
[35 empty] | 6279.2787 | 149 | 0.009983 | 0.013112 | 0.013112 | 0.052448 | 0.012173 | 0.025492 | 0.015302 | 0.061078 | 6309.485 | 8849.8332
[35 empty] | 6309.485 | 148 | 0.009916 | 0.013024 | 0.013024 | 0.052096 | 0.012106 | 0.025404 | 0.015214 | 0.060726 | 6339.9829 | 8883.8832
[35 empty] | 6339.9829 | 147 | 0.009849 | 0.012936 | 0.012936 | 0.051744 | 0.012039 | 0.025316 | 0.015126 | 0.060374 | 6370.7765 | 8918.1905
[35 empty] | 6370.7765 | 146 | 0.009782 | 0.012848 | 0.012848 | 0.051392 | 0.011972 | 0.025228 | 0.015038 | 0.060022 | 6401.8702 | 8952.7579
[35 empty] | 6401.8702 | 145 | 0.009715 | 0.01276 | 0.01276 | 0.05104 | 0.011905 | 0.02514 | 0.01495 | 0.05967 | 6433.2684 | 8987.5883
[35 empty] | 6433.2684 | 144 | 0.009648 | 0.012672 | 0.012672 | 0.050688 | 0.011838 | 0.025052 | 0.014862 | 0.059318 | 6464.9755 | 9022.6846
[35 empty] | 6464.9755 | 143 | 0.009581 | 0.012584 | 0.012584 | 0.050336 | 0.011771 | 0.024964 | 0.014774 | 0.058966 | 6496.9961 | 9058.0498
[35 empty] | 6496.9961 | 142 | 0.009514 | 0.012496 | 0.012496 | 0.049984 | 0.011704 | 0.024876 | 0.014686 | 0.058614 | 6529.335 | 9093.6869
[35 empty] | 6529.335 | 141 | 0.009447 | 0.012408 | 0.012408 | 0.049632 | 0.011637 | 0.024788 | 0.014598 | 0.058262 | 6561.9968 | 9129.5991
[35 empty] | 6561.9968 | 140 | 0.00938 | 0.01232 | 0.01232 | 0.04928 | 0.01157 | 0.0247 | 0.01451 | 0.05791 | 6594.9864 | 9165.7894
[35 empty] | 6594.9864 | 139 | 0.009313 | 0.012232 | 0.012232 | 0.048928 | 0.011503 | 0.024612 | 0.014422 | 0.057558 | 6628.3088 | 9202.2611
[35 empty] | 6628.3088 | 138 | 0.009246 | 0.012144 | 0.012144 | 0.048576 | 0.011436 | 0.024524 | 0.014334 | 0.057206 | 6661.969 | 9239.0172
[35 empty] | 6661.969 | 137 | 0.009179 | 0.012056 | 0.012056 | 0.048224 | 0.011369 | 0.024436 | 0.014246 | 0.056854 | 6695.9721 | 9276.0611
[35 empty] | 6695.9721 | 136 | 0.009112 | 0.011968 | 0.011968 | 0.047872 | 0.011302 | 0.024348 | 0.014158 | 0.056502 | 6730.3235 | 9313.396
[35 empty] | 6730.3235 | 135 | 0.009045 | 0.01188 | 0.01188 | 0.04752 | 0.011235 | 0.02426 | 0.01407 | 0.05615 | 6765.0284 | 9351.0254
[35 empty] | 6765.0284 | 134 | 0.008978 | 0.011792 | 0.011792 | 0.047168 | 0.011168 | 0.024172 | 0.013982 | 0.055798 | 6800.0924 | 9388.9526
[35 empty] | 6800.0924 | 133 | 0.008911 | 0.011704 | 0.011704 | 0.046816 | 0.011101 | 0.024084 | 0.013894 | 0.055446 | 6835.5211 | 9427.181
[35 empty] | 6835.5211 | 132 | 0.008844 | 0.011616 | 0.011616 | 0.046464 | 0.011034 | 0.023996 | 0.013806 | 0.055094 | 6871.3201 | 9465.7143
[35 empty] | 6871.3201 | 131 | 0.008777 | 0.011528 | 0.011528 | 0.046112 | 0.010967 | 0.023908 | 0.013718 | 0.054742 | 6907.4954 | 9504.5559
[35 empty] | 6907.4954 | 130 | 0.00871 | 0.01144 | 0.01144 | 0.04576 | 0.0109 | 0.02382 | 0.01363 | 0.05439 | 6944.0527 | 9543.7094
[35 empty] | 6944.0527 | 129 | 0.008643 | 0.011352 | 0.011352 | 0.045408 | 0.010833 | 0.023732 | 0.013542 | 0.054038 | 6980.9983 | 9583.1786
[35 empty] | 6980.9983 | 128 | 0.008576 | 0.011264 | 0.011264 | 0.045056 | 0.010766 | 0.023644 | 0.013454 | 0.053686 | 7018.3383 | 9622.9672
[35 empty] | 7018.3383 | 127 | 0.008509 | 0.011176 | 0.011176 | 0.044704 | 0.010699 | 0.023556 | 0.013366 | 0.053334 | 7056.079 | 9663.0789
[35 empty] | 7056.079 | 126 | 0.008442 | 0.011088 | 0.011088 | 0.044352 | 0.010632 | 0.023468 | 0.013278 | 0.052982 | 7094.2269 | 9703.5176
[35 empty] | 7094.2269 | 125 | 0.008375 | 0.011 | 0.011 | 0.044 | 0.010565 | 0.02338 | 0.01319 | 0.05263 | 7132.7887 | 9744.2871
[35 empty] | 7132.7887 | 124 | 0.008308 | 0.010912 | 0.010912 | 0.043648 | 0.010498 | 0.023292 | 0.013102 | 0.052278 | 7171.7711 | 9785.3915
[35 empty] | 7171.7711 | 123 | 0.008241 | 0.010824 | 0.010824 | 0.043296 | 0.010431 | 0.023204 | 0.013014 | 0.051926 | 7211.181 | 9826.8347
[35 empty] | 7211.181 | 122 | 0.008174 | 0.010736 | 0.010736 | 0.042944 | 0.010364 | 0.023116 | 0.012926 | 0.051574 | 7251.0254 | 9868.6209
[35 empty] | 7251.0254 | 121 | 0.008107 | 0.010648 | 0.010648 | 0.042592 | 0.010297 | 0.023028 | 0.012838 | 0.051222 | 7291.3116 | 9910.7542
[35 empty] | 7291.3116 | 120 | 0.00804 | 0.01056 | 0.01056 | 0.04224 | 0.01023 | 0.02294 | 0.01275 | 0.05087 | 7332.0469 | 9953.2388
[35 empty] | 7332.0469 | 119 | 0.007973 | 0.010472 | 0.010472 | 0.041888 | 0.010163 | 0.022852 | 0.012662 | 0.050518 | 7373.2389 | 9996.079
[35 empty] | 7373.2389 | 118 | 0.007906 | 0.010384 | 0.010384 | 0.041536 | 0.010096 | 0.022764 | 0.012574 | 0.050166 | 7414.8952 | 10039.2791
[35 empty] | 7414.8952 | 117 | 0.007839 | 0.010296 | 0.010296 | 0.041184 | 0.010029 | 0.022676 | 0.012486 | 0.049814 | 7457.0238 | 10082.8435
[35 empty] | 7457.0238 | 116 | 0.007772 | 0.010208 | 0.010208 | 0.040832 | 0.009962 | 0.022588 | 0.012398 | 0.049462 | 7499.6327 | 10126.7767
[35 empty] | 7499.6327 | 115 | 0.007705 | 0.01012 | 0.01012 | 0.04048 | 0.009895 | 0.0225 | 0.01231 | 0.04911 | 7542.7302 | 10171.0834
[35 empty] | 7542.7302 | 114 | 0.007638 | 0.010032 | 0.010032 | 0.040128 | 0.009828 | 0.022412 | 0.012222 | 0.048758 | 7586.3246 | 10215.768
[35 empty] | 7586.3246 | 113 | 0.007571 | 0.009944 | 0.009944 | 0.039776 | 0.009761 | 0.022324 | 0.012134 | 0.048406 | 7630.4247 | 10260.8354
[35 empty] | 7630.4247 | 112 | 0.007504 | 0.009856 | 0.009856 | 0.039424 | 0.009694 | 0.022236 | 0.012046 | 0.048054 | 7675.0391 | 10306.2902
[35 empty] | 7675.0391 | 111 | 0.007437 | 0.009768 | 0.009768 | 0.039072 | 0.009627 | 0.022148 | 0.011958 | 0.047702 | 7720.177 | 10352.1374
[35 empty] | 7720.177 | 110 | 0.00737 | 0.00968 | 0.00968 | 0.03872 | 0.00956 | 0.02206 | 0.01187 | 0.04735 | 7765.8476 | 10398.3818
[35 empty] | 7765.8476 | 109 | 0.007303 | 0.009592 | 0.009592 | 0.038368 | 0.009493 | 0.021972 | 0.011782 | 0.046998 | 7812.0604 | 10445.0286
[35 empty] | 7812.0604 | 108 | 0.007236 | 0.009504 | 0.009504 | 0.038016 | 0.009426 | 0.021884 | 0.011694 | 0.046646 | 7858.8251 | 10492.0827
[35 empty] | 7858.8251 | 107 | 0.007169 | 0.009416 | 0.009416 | 0.037664 | 0.009359 | 0.021796 | 0.011606 | 0.046294 | 7906.1515 | 10539.5493
[35 empty] | 7906.1515 | 106 | 0.007102 | 0.009328 | 0.009328 | 0.037312 | 0.009292 | 0.021708 | 0.011518 | 0.045942 | 7954.0498 | 10587.4338
[35 empty] | 7954.0498 | 105 | 0.007035 | 0.00924 | 0.00924 | 0.03696 | 0.009225 | 0.02162 | 0.01143 | 0.04559 | 8002.5304 | 10635.7414
[35 empty] | 8002.5304 | 104 | 0.006968 | 0.009152 | 0.009152 | 0.036608 | 0.009158 | 0.021532 | 0.011342 | 0.045238 | 8051.604 | 10684.4777
[35 empty] | 8051.604 | 103 | 0.006901 | 0.009064 | 0.009064 | 0.036256 | 0.009091 | 0.021444 | 0.011254 | 0.044886 | 8101.2816 | 10733.648
[35 empty] | 8101.2816 | 102 | 0.006834 | 0.008976 | 0.008976 | 0.035904 | 0.009024 | 0.021356 | 0.011166 | 0.044534 | 8151.5742 | 10783.2581
[35 empty] | 8151.5742 | 101 | 0.006767 | 0.008888 | 0.008888 | 0.035552 | 0.008957 | 0.021268 | 0.011078 | 0.044182 | 8202.4933 | 10833.3136
[35 empty] | 8202.4933 | 100 | 0.0067 | 0.0088 | 0.0088 | 0.0352 | 0.00889 | 0.02118 | 0.01099 | 0.04383 | 8254.0507 | 10883.8204
[35 empty] | 8254.0507 | 99 | 0.006633 | 0.008712 | 0.008712 | 0.034848 | 0.008823 | 0.021092 | 0.010902 | 0.043478 | 8306.2585 | 10934.7843
[35 empty] | 8306.2585 | 98 | 0.006566 | 0.008624 | 0.008624 | 0.034496 | 0.008756 | 0.021004 | 0.010814 | 0.043126 | 8359.1289 | 10986.2114
[35 empty] | 8359.1289 | 97 | 0.006499 | 0.008536 | 0.008536 | 0.034144 | 0.008689 | 0.020916 | 0.010726 | 0.042774 | 8412.6747 | 11038.1077
[35 empty] | 8412.6747 | 96 | 0.006432 | 0.008448 | 0.008448 | 0.033792 | 0.008622 | 0.020828 | 0.010638 | 0.042422 | 8466.9087 | 11090.4795
[35 empty] | 8466.9087 | 95 | 0.006365 | 0.00836 | 0.00836 | 0.03344 | 0.008555 | 0.02074 | 0.01055 | 0.04207 | 8521.8444 | 11143.333
[35 empty] | 8521.8444 | 94 | 0.006298 | 0.008272 | 0.008272 | 0.033088 | 0.008488 | 0.020652 | 0.010462 | 0.041718 | 8577.4955 | 11196.6748
[35 empty] | 8577.4955 | 93 | 0.006231 | 0.008184 | 0.008184 | 0.032736 | 0.008421 | 0.020564 | 0.010374 | 0.041366 | 8633.8758 | 11250.5112
[35 empty] | 8633.8758 | 92 | 0.006164 | 0.008096 | 0.008096 | 0.032384 | 0.008354 | 0.020476 | 0.010286 | 0.041014 | 8690.9998 | 11304.8489
[35 empty] | 8690.9998 | 91 | 0.006097 | 0.008008 | 0.008008 | 0.032032 | 0.008287 | 0.020388 | 0.010198 | 0.040662 | 8748.8823 | 11359.6947
[35 empty] | 8748.8823 | 90 | 0.00603 | 0.00792 | 0.00792 | 0.03168 | 0.00822 | 0.0203 | 0.01011 | 0.04031 | 8807.5383 | 11415.0554
[35 empty] | 8807.5383 | 89 | 0.005963 | 0.007832 | 0.007832 | 0.031328 | 0.008153 | 0.020212 | 0.010022 | 0.039958 | 8866.9836 | 11470.9381
[35 empty] | 8866.9836 | 88 | 0.005896 | 0.007744 | 0.007744 | 0.030976 | 0.008086 | 0.020124 | 0.009934 | 0.039606 | 8927.234 | 11527.3498
[35 empty] | 8927.234 | 87 | 0.005829 | 0.007656 | 0.007656 | 0.030624 | 0.008019 | 0.020036 | 0.009846 | 0.039254 | 8988.306 | 11584.2978
[35 empty] | 8988.306 | 86 | 0.005762 | 0.007568 | 0.007568 | 0.030272 | 0.007952 | 0.019948 | 0.009758 | 0.038902 | 9050.2165 | 11641.7893
[35 empty] | 9050.2165 | 85 | 0.005695 | 0.00748 | 0.00748 | 0.02992 | 0.007885 | 0.01986 | 0.00967 | 0.03855 | 9112.9826 | 11699.8319
[35 empty] | 9112.9826 | 84 | 0.005628 | 0.007392 | 0.007392 | 0.029568 | 0.007818 | 0.019772 | 0.009582 | 0.038198 | 9176.6224 | 11758.4332
[35 empty] | 9176.6224 | 83 | 0.005561 | 0.007304 | 0.007304 | 0.029216 | 0.007751 | 0.019684 | 0.009494 | 0.037846 | 9241.154 | 11817.601
[35 empty] | 9241.154 | 82 | 0.005494 | 0.007216 | 0.007216 | 0.028864 | 0.007684 | 0.019596 | 0.009406 | 0.037494 | 9306.5962 | 11877.343
[35 empty] | 9306.5962 | 81 | 0.005427 | 0.007128 | 0.007128 | 0.028512 | 0.007617 | 0.019508 | 0.009318 | 0.037142 | 9372.9684 | 11937.6674
[35 empty] | 9372.9684 | 80 | 0.00536 | 0.00704 | 0.00704 | 0.02816 | 0.00755 | 0.01942 | 0.00923 | 0.03679 | 9440.2906 | 11998.5822
[35 empty] | 9440.2906 | 79 | 0.005293 | 0.006952 | 0.006952 | 0.027808 | 0.007483 | 0.019332 | 0.009142 | 0.036438 | 9508.5831 | 12060.0958
[35 empty] | 9508.5831 | 78 | 0.005226 | 0.006864 | 0.006864 | 0.027456 | 0.007416 | 0.019244 | 0.009054 | 0.036086 | 9577.867 | 12122.2167
[35 empty] | 9577.867 | 77 | 0.005159 | 0.006776 | 0.006776 | 0.027104 | 0.007349 | 0.019156 | 0.008966 | 0.035734 | 9648.1639 | 12184.9533
[35 empty] | 9648.1639 | 76 | 0.005092 | 0.006688 | 0.006688 | 0.026752 | 0.007282 | 0.019068 | 0.008878 | 0.035382 | 9719.4962 | 12248.3146
[35 empty] | 9719.4962 | 75 | 0.005025 | 0.0066 | 0.0066 | 0.0264 | 0.007215 | 0.01898 | 0.00879 | 0.03503 | 9791.8868 | 12312.3093
[35 empty] | 9791.8868 | 74 | 0.004958 | 0.006512 | 0.006512 | 0.026048 | 0.007148 | 0.018892 | 0.008702 | 0.034678 | 9865.3594 | 12376.9466
[35 empty] | 9865.3594 | 73 | 0.004891 | 0.006424 | 0.006424 | 0.025696 | 0.007081 | 0.018804 | 0.008614 | 0.034326 | 9939.9382 | 12442.2356
[35 empty] | 9939.9382 | 72 | 0.004824 | 0.006336 | 0.006336 | 0.025344 | 0.007014 | 0.018716 | 0.008526 | 0.033974 | 10015.6483 | 12508.1859
[35 empty] | 10015.6483 | 71 | 0.004757 | 0.006248 | 0.006248 | 0.024992 | 0.006947 | 0.018628 | 0.008438 | 0.033622 | 10092.5156 | 12574.8069
[35 empty] | 10092.5156 | 70 | 0.00469 | 0.00616 | 0.00616 | 0.02464 | 0.00688 | 0.01854 | 0.00835 | 0.03327 | 10170.5666 | 12642.1084
[35 empty] | 10170.5666 | 69 | 0.004623 | 0.006072 | 0.006072 | 0.024288 | 0.006813 | 0.018452 | 0.008262 | 0.032918 | 10249.8288 | 12710.1003
[35 empty] | 10249.8288 | 68 | 0.004556 | 0.005984 | 0.005984 | 0.023936 | 0.006746 | 0.018364 | 0.008174 | 0.032566 | 10330.3306 | 12778.7926
[35 empty] | 10330.3306 | 67 | 0.004489 | 0.005896 | 0.005896 | 0.023584 | 0.006679 | 0.018276 | 0.008086 | 0.032214 | 10412.1009 | 12848.1958
[35 empty] | 10412.1009 | 66 | 0.004422 | 0.005808 | 0.005808 | 0.023232 | 0.006612 | 0.018188 | 0.007998 | 0.031862 | 10495.1701 | 12918.3202
[35 empty] | 10495.1701 | 65 | 0.004355 | 0.00572 | 0.00572 | 0.02288 | 0.006545 | 0.0181 | 0.00791 | 0.03151 | 10579.5689 | 12989.1766
[35 empty] | 10579.5689 | 64 | 0.004288 | 0.005632 | 0.005632 | 0.022528 | 0.006478 | 0.018012 | 0.007822 | 0.031158 | 10665.3296 | 13060.7757
[35 empty] | 10665.3296 | 63 | 0.004221 | 0.005544 | 0.005544 | 0.022176 | 0.006411 | 0.017924 | 0.007734 | 0.030806 | 10752.4852 | 13133.1287
[35 empty] | 10752.4852 | 62 | 0.004154 | 0.005456 | 0.005456 | 0.021824 | 0.006344 | 0.017836 | 0.007646 | 0.030454 | 10841.0697 | 13206.2467
[35 empty] | 10841.0697 | 61 | 0.004087 | 0.005368 | 0.005368 | 0.021472 | 0.006277 | 0.017748 | 0.007558 | 0.030102 | 10931.1185 | 13280.1413
[35 empty] | 10931.1185 | 60 | 0.00402 | 0.00528 | 0.00528 | 0.02112 | 0.00621 | 0.01766 | 0.00747 | 0.02975 | 11022.668 | 13354.8241
[35 empty] | 11022.668 | 59 | 0.003953 | 0.005192 | 0.005192 | 0.020768 | 0.006143 | 0.017572 | 0.007382 | 0.029398 | 11115.7558 | 13430.3071
[35 empty] | 11115.7558 | 58 | 0.003886 | 0.005104 | 0.005104 | 0.020416 | 0.006076 | 0.017484 | 0.007294 | 0.029046 | 11210.4207 | 13506.6024
[35 empty] | 11210.4207 | 57 | 0.003819 | 0.005016 | 0.005016 | 0.020064 | 0.006009 | 0.017396 | 0.007206 | 0.028694 | 11306.703 | 13583.7222
[35 empty] | 11306.703 | 56 | 0.003752 | 0.004928 | 0.004928 | 0.019712 | 0.005942 | 0.017308 | 0.007118 | 0.028342 | 11404.6443 | 13661.6792
[35 empty] | 11404.6443 | 55 | 0.003685 | 0.00484 | 0.00484 | 0.01936 | 0.005875 | 0.01722 | 0.00703 | 0.02799 | 11504.2876 | 13740.4862
[35 empty] | 11504.2876 | 54 | 0.003618 | 0.004752 | 0.004752 | 0.019008 | 0.005808 | 0.017132 | 0.006942 | 0.027638 | 11605.6773 | 13820.1563
[35 empty] | 11605.6773 | 53 | 0.003551 | 0.004664 | 0.004664 | 0.018656 | 0.005741 | 0.017044 | 0.006854 | 0.027286 | 11708.8594 | 13900.7027
[35 empty] | 11708.8594 | 52 | 0.003484 | 0.004576 | 0.004576 | 0.018304 | 0.005674 | 0.016956 | 0.006766 | 0.026934 | 11813.8818 | 13982.139
[35 empty] | 11813.8818 | 51 | 0.003417 | 0.004488 | 0.004488 | 0.017952 | 0.005607 | 0.016868 | 0.006678 | 0.026582 | 11920.7937 | 14064.4789
[35 empty] | 11920.7937 | 50 | 0.00335 | 0.0044 | 0.0044 | 0.0176 | 0.00554 | 0.01678 | 0.00659 | 0.02623 | 12029.6462 | 14147.7366
[35 empty] | 12029.6462 | 49 | 0.003283 | 0.004312 | 0.004312 | 0.017248 | 0.005473 | 0.016692 | 0.006502 | 0.025878 | 12140.4924 | 14231.9263
[35 empty] | 12140.4924 | 48 | 0.003216 | 0.004224 | 0.004224 | 0.016896 | 0.005406 | 0.016604 | 0.006414 | 0.025526 | 12253.3871 | 14317.0627
[35 empty] | 12253.3871 | 47 | 0.003149 | 0.004136 | 0.004136 | 0.016544 | 0.005339 | 0.016516 | 0.006326 | 0.025174 | 12368.3873 | 14403.1607
[35 empty] | 12368.3873 | 46 | 0.003082 | 0.004048 | 0.004048 | 0.016192 | 0.005272 | 0.016428 | 0.006238 | 0.024822 | 12485.5521 | 14490.2353
[35 empty] | 12485.5521 | 45 | 0.003015 | 0.00396 | 0.00396 | 0.01584 | 0.005205 | 0.01634 | 0.00615 | 0.02447 | 12604.9427 | 14578.302
[35 empty] | 12604.9427 | 44 | 0.002948 | 0.003872 | 0.003872 | 0.015488 | 0.005138 | 0.016252 | 0.006062 | 0.024118 | 12726.6226 | 14667.3765
[35 empty] | 12726.6226 | 43 | 0.002881 | 0.003784 | 0.003784 | 0.015136 | 0.005071 | 0.016164 | 0.005974 | 0.023766 | 12850.658 | 14757.475
[35 empty] | 12850.658 | 42 | 0.002814 | 0.003696 | 0.003696 | 0.014784 | 0.005004 | 0.016076 | 0.005886 | 0.023414 | 12977.1174 | 14848.6136
[35 empty] | 12977.1174 | 41 | 0.002747 | 0.003608 | 0.003608 | 0.014432 | 0.004937 | 0.015988 | 0.005798 | 0.023062 | 13106.0719 | 14940.8091
[35 empty] | 13106.0719 | 40 | 0.00268 | 0.00352 | 0.00352 | 0.01408 | 0.00487 | 0.0159 | 0.00571 | 0.02271 | 13237.5956 | 15034.0784
[35 empty] | 13237.5956 | 39 | 0.002613 | 0.003432 | 0.003432 | 0.013728 | 0.004803 | 0.015812 | 0.005622 | 0.022358 | 13371.7655 | 15128.4387
[35 empty] | 13371.7655 | 38 | 0.002546 | 0.003344 | 0.003344 | 0.013376 | 0.004736 | 0.015724 | 0.005534 | 0.022006 | 13508.6615 | 15223.9078
[35 empty] | 13508.6615 | 37 | 0.002479 | 0.003256 | 0.003256 | 0.013024 | 0.004669 | 0.015636 | 0.005446 | 0.021654 | 13648.3669 | 15320.5034
[35 empty] | 13648.3669 | 36 | 0.002412 | 0.003168 | 0.003168 | 0.012672 | 0.004602 | 0.015548 | 0.005358 | 0.021302 | 13790.9685 | 15418.244
[35 empty] | 13790.9685 | 35 | 0.002345 | 0.00308 | 0.00308 | 0.01232 | 0.004535 | 0.01546 | 0.00527 | 0.02095 | 13936.5563 | 15517.1481
[35 empty] | 13936.5563 | 34 | 0.002278 | 0.002992 | 0.002992 | 0.011968 | 0.004468 | 0.015372 | 0.005182 | 0.020598 | 14085.2243 | 15617.2347
[35 empty] | 14085.2243 | 33 | 0.002211 | 0.002904 | 0.002904 | 0.011616 | 0.004401 | 0.015284 | 0.005094 | 0.020246 | 14237.0706 | 15718.5231
[35 empty] | 14237.0706 | 32 | 0.002144 | 0.002816 | 0.002816 | 0.011264 | 0.004334 | 0.015196 | 0.005006 | 0.019894 | 14392.1971 | 15821.033
[35 empty] | 14392.1971 | 31 | 0.002077 | 0.002728 | 0.002728 | 0.010912 | 0.004267 | 0.015108 | 0.004918 | 0.019542 | 14550.7104 | 15924.7846
[35 empty] | 14550.7104 | 30 | 0.00201 | 0.00264 | 0.00264 | 0.01056 | 0.0042 | 0.01502 | 0.00483 | 0.01919 | 14712.7214 | 16029.7982
[35 empty] | 14712.7214 | 29 | 0.001943 | 0.002552 | 0.002552 | 0.010208 | 0.004133 | 0.014932 | 0.004742 | 0.018838 | 14878.3461 | 16136.0946
[35 empty] | 14878.3461 | 28 | 0.001876 | 0.002464 | 0.002464 | 0.009856 | 0.004066 | 0.014844 | 0.004654 | 0.018486 | 15047.7056 | 16243.6952
[35 empty] | 15047.7056 | 27 | 0.001809 | 0.002376 | 0.002376 | 0.009504 | 0.003999 | 0.014756 | 0.004566 | 0.018134 | 15220.9263 | 16352.6214
[35 empty] | 15220.9263 | 26 | 0.001742 | 0.002288 | 0.002288 | 0.009152 | 0.003932 | 0.014668 | 0.004478 | 0.017782 | 15398.1403 | 16462.8954
[35 empty] | 15398.1403 | 25 | 0.001675 | 0.0022 | 0.0022 | 0.0088 | 0.003865 | 0.01458 | 0.00439 | 0.01743 | 15579.486 | 16574.5395
[35 empty] | 15579.486 | 24 | 0.001608 | 0.002112 | 0.002112 | 0.008448 | 0.003798 | 0.014492 | 0.004302 | 0.017078 | 15765.1078 | 16687.5766
[35 empty] | 15765.1078 | 23 | 0.001541 | 0.002024 | 0.002024 | 0.008096 | 0.003731 | 0.014404 | 0.004214 | 0.016726 | 15955.1571 | 16802.03
[35 empty] | 15955.1571 | 22 | 0.001474 | 0.001936 | 0.001936 | 0.007744 | 0.003664 | 0.014316 | 0.004126 | 0.016374 | 16149.7924 | 16917.9232
[35 empty] | 16149.7924 | 21 | 0.001407 | 0.001848 | 0.001848 | 0.007392 | 0.003597 | 0.014228 | 0.004038 | 0.016022 | 16349.1796 | 17035.2804
[35 empty] | 16349.1796 | 20 | 0.00134 | 0.00176 | 0.00176 | 0.00704 | 0.00353 | 0.01414 | 0.00395 | 0.01567 | 16553.4928 | 17154.1262
[35 empty] | 16553.4928 | 19 | 0.001273 | 0.001672 | 0.001672 | 0.006688 | 0.003463 | 0.014052 | 0.003862 | 0.015318 | 16762.9145 | 17274.4856
[35 empty] | 16762.9145 | 18 | 0.001206 | 0.001584 | 0.001584 | 0.006336 | 0.003396 | 0.013964 | 0.003774 | 0.014966 | 16977.6363 | 17396.3839
[35 empty] | 16977.6363 | 17 | 0.001139 | 0.001496 | 0.001496 | 0.005984 | 0.003329 | 0.013876 | 0.003686 | 0.014614 | 17197.8591 | 17519.8472
[35 empty] | 17197.8591 | 16 | 0.001072 | 0.001408 | 0.001408 | 0.005632 | 0.003262 | 0.013788 | 0.003598 | 0.014262 | 17423.7944 | 17644.9016
[35 empty] | 17423.7944 | 15 | 0.001005 | 0.00132 | 0.00132 | 0.00528 | 0.003195 | 0.0137 | 0.00351 | 0.01391 | 17655.6639 | 17771.5739
[35 empty] | 17655.6639 | 14 | 0.000938 | 0.001232 | 0.001232 | 0.004928 | 0.003128 | 0.013612 | 0.003422 | 0.013558 | 17893.7014 | 17899.8916
[35 empty] | 17893.7014 | 13 | 0.000871 | 0.001144 | 0.001144 | 0.004576 | 0.003061 | 0.013524 | 0.003334 | 0.013206 | 18138.1525 | 18029.8822
[35 empty] | 18138.1525 | 12 | 0.000804 | 0.001056 | 0.001056 | 0.004224 | 0.002994 | 0.013436 | 0.003246 | 0.012854 | 18389.2759 | 18161.574
[35 empty] | 18389.2759 | 11 | 0.000737 | 0.000968 | 0.000968 | 0.003872 | 0.002927 | 0.013348 | 0.003158 | 0.012502 | 18647.3442 | 18294.9956
[35 empty] | 18647.3442 | 10 | 0.00067 | 0.00088 | 0.00088 | 0.00352 | 0.00286 | 0.01326 | 0.00307 | 0.01215 | 18912.645 | 18430.1761
[35 empty] | 18912.645 | 9 | 0.000603 | 0.000792 | 0.000792 | 0.003168 | 0.002793 | 0.013172 | 0.002982 | 0.011798 | 19185.4812 | 18567.1452
[35 empty] | 19185.4812 | 8 | 0.000536 | 0.000704 | 0.000704 | 0.002816 | 0.002726 | 0.013084 | 0.002894 | 0.011446 | 19466.1731 | 18705.9329
[35 empty] | 19466.1731 | 7 | 0.000469 | 0.000616 | 0.000616 | 0.002464 | 0.002659 | 0.012996 | 0.002806 | 0.011094 | 19755.0587 | 18846.5698
[35 empty] | 19755.0587 | 6 | 0.000402 | 0.000528 | 0.000528 | 0.002112 | 0.002592 | 0.012908 | 0.002718 | 0.010742 | 20052.4954 | 18989.0869
[35 empty] | 20052.4954 | 5 | 0.000335 | 0.00044 | 0.00044 | 0.00176 | 0.002525 | 0.01282 | 0.00263 | 0.01039 | 20358.8613 | 19133.5156
[35 empty] | 20358.8613 | 4 | 0.000268 | 0.000352 | 0.000352 | 0.001408 | 0.002458 | 0.012732 | 0.002542 | 0.010038 | 20674.5565 | 19279.8879
[35 empty] | 20674.5565 | 3 | 0.000201 | 0.000264 | 0.000264 | 0.001056 | 0.002391 | 0.012644 | 0.002454 | 0.009686 | 21000.005 | 19428.2363
[35 empty] | 21000.005 | 2 | 0.000134 | 0.000176 | 0.000176 | 0.000704 | 0.002324 | 0.012556 | 0.002366 | 0.009334 | 21335.6562 | 19578.5935
[35 empty] | 21335.6562 | 1 | 6.7e-05 | 8.8e-05 | 8.8e-05 | 0.000352 | 0.002257 | 0.012468 | 0.002278 | 0.008982 | 21681.987 | 19730.9928
[35 empty] | 21681.987 | 0 | 0 | 0 | 0 | 0 | 0.00219 | 0.01238 | 0.00219 | 0.00863 | 22039.5034 | 19885.468

## C_Calculations (hidden)
Arrangement C
Import
Phase Current |  |  |  | Neutral Current
Ipz1 | Ipr1 | Ipx1 | qph1 | Inz1 | Inr1 | Inx1 | qn1
724.6377 | 710.1449 | 144.2011 | 11.4783 | 362.3188 | 355.0725 | 72.1005 | 11.4783
Export
Phase Current |  |  |  | Neutral Current
Ipz1 | Ipr1 | Ipx1 | qph1 | Inz1 | Inr1 | Inx1 | qn1
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer
[8 empty] | T/F Resistance: | 0.00509 | Ω
[8 empty] | T/F Reactance: | 0.0171 | Ω
[8 empty] | T/F Voltage Drop: | 6.0805 | V
[8 empty] | T/F Voltage Rise: | 0 | V
Source Impedance
[11 empty] | Source Resistance: | 0 | Ω
[11 empty] | Source Reactance: | 0.0037498 | Ω
Voltage Drop calculation
[14 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[14 empty] | 0.02379 | 0.0063448 | 0.02379 | 0.0064169 | 204.1633
Voltage Rise Calculation
[14 empty] | Ipr.Rp | Ipx.Xp | Inr.Rn | Inx.Xn | Max. Cable Length (m)
[14 empty] | 0 | 0 | 0 | 0 | 10000
Fault Calculation
[21 empty] | Cable Impedance (Ω) |  |  |  | T/F + Cable Impedance (Ω) | [5 empty] | Maximum Cable Length: | 151
[19 empty] | FL Lookup | Cable Length (m) | RC1 | XC1 | RC0 | XC0 | R1 | X1 | R0 | X0 | Earth Fault level (A) | 3 Phase Fault level (A)
[19 empty] | 0 | 151 | 0.0050585 | 0.006644 | 0.03541 | 0.046961 | 0.010149 | 0.027494 | 0.0405 | 0.064061 | 5610.6591 | 8530.3865
[19 empty] | 5610.6591 | 150 | 0.005025 | 0.0066 | 0.035175 | 0.04665 | 0.010115 | 0.02745 | 0.040265 | 0.06375 | 5631.4046 | 8545.8043
[19 empty] | 5631.4046 | 149 | 0.0049915 | 0.006556 | 0.03494 | 0.046339 | 0.010082 | 0.027406 | 0.04003 | 0.063439 | 5652.3017 | 8561.2752
[19 empty] | 5652.3017 | 148 | 0.004958 | 0.006512 | 0.034706 | 0.046028 | 0.010048 | 0.027362 | 0.039796 | 0.063128 | 5673.3519 | 8576.7997
[19 empty] | 5673.3519 | 147 | 0.0049245 | 0.006468 | 0.034472 | 0.045717 | 0.010014 | 0.027318 | 0.039561 | 0.062817 | 5694.557 | 8592.3778
[19 empty] | 5694.557 | 146 | 0.004891 | 0.006424 | 0.034237 | 0.045406 | 0.009981 | 0.027274 | 0.039327 | 0.062506 | 5715.9186 | 8608.0099
[19 empty] | 5715.9186 | 145 | 0.0048575 | 0.00638 | 0.034003 | 0.045095 | 0.0099475 | 0.02723 | 0.039093 | 0.062195 | 5737.4385 | 8623.6963
[19 empty] | 5737.4385 | 144 | 0.004824 | 0.006336 | 0.033768 | 0.044784 | 0.009914 | 0.027186 | 0.038858 | 0.061884 | 5759.1183 | 8639.4372
[19 empty] | 5759.1183 | 143 | 0.0047905 | 0.006292 | 0.033534 | 0.044473 | 0.0098805 | 0.027142 | 0.038623 | 0.061573 | 5780.9598 | 8655.2329
[19 empty] | 5780.9598 | 142 | 0.004757 | 0.006248 | 0.033299 | 0.044162 | 0.009847 | 0.027098 | 0.038389 | 0.061262 | 5802.9649 | 8671.0836
[19 empty] | 5802.9649 | 141 | 0.0047235 | 0.006204 | 0.033065 | 0.043851 | 0.0098135 | 0.027054 | 0.038155 | 0.060951 | 5825.1353 | 8686.9896
[19 empty] | 5825.1353 | 140 | 0.00469 | 0.00616 | 0.03283 | 0.04354 | 0.00978 | 0.02701 | 0.03792 | 0.06064 | 5847.4728 | 8702.9513
[19 empty] | 5847.4728 | 139 | 0.0046565 | 0.006116 | 0.032595 | 0.043229 | 0.0097465 | 0.026966 | 0.037685 | 0.060329 | 5869.9794 | 8718.9688
[19 empty] | 5869.9794 | 138 | 0.004623 | 0.006072 | 0.032361 | 0.042918 | 0.009713 | 0.026922 | 0.037451 | 0.060018 | 5892.6569 | 8735.0425
[19 empty] | 5892.6569 | 137 | 0.0045895 | 0.006028 | 0.032127 | 0.042607 | 0.0096795 | 0.026878 | 0.037216 | 0.059707 | 5915.5072 | 8751.1726
[19 empty] | 5915.5072 | 136 | 0.004556 | 0.005984 | 0.031892 | 0.042296 | 0.009646 | 0.026834 | 0.036982 | 0.059396 | 5938.5324 | 8767.3594
[19 empty] | 5938.5324 | 135 | 0.0045225 | 0.00594 | 0.031658 | 0.041985 | 0.0096125 | 0.02679 | 0.036748 | 0.059085 | 5961.7342 | 8783.6033
[19 empty] | 5961.7342 | 134 | 0.004489 | 0.005896 | 0.031423 | 0.041674 | 0.009579 | 0.026746 | 0.036513 | 0.058774 | 5985.1149 | 8799.9044
[19 empty] | 5985.1149 | 133 | 0.0044555 | 0.005852 | 0.031189 | 0.041363 | 0.0095455 | 0.026702 | 0.036278 | 0.058463 | 6008.6763 | 8816.263
[19 empty] | 6008.6763 | 132 | 0.004422 | 0.005808 | 0.030954 | 0.041052 | 0.009512 | 0.026658 | 0.036044 | 0.058152 | 6032.4206 | 8832.6795
[19 empty] | 6032.4206 | 131 | 0.0043885 | 0.005764 | 0.03072 | 0.040741 | 0.0094785 | 0.026614 | 0.03581 | 0.057841 | 6056.3498 | 8849.1542
[19 empty] | 6056.3498 | 130 | 0.004355 | 0.00572 | 0.030485 | 0.04043 | 0.009445 | 0.02657 | 0.035575 | 0.05753 | 6080.4662 | 8865.6873
[19 empty] | 6080.4662 | 129 | 0.0043215 | 0.005676 | 0.030251 | 0.040119 | 0.0094115 | 0.026526 | 0.035341 | 0.057219 | 6104.7718 | 8882.2791
[19 empty] | 6104.7718 | 128 | 0.004288 | 0.005632 | 0.030016 | 0.039808 | 0.009378 | 0.026482 | 0.035106 | 0.056908 | 6129.2688 | 8898.9299
[19 empty] | 6129.2688 | 127 | 0.0042545 | 0.005588 | 0.029782 | 0.039497 | 0.0093445 | 0.026438 | 0.034871 | 0.056597 | 6153.9595 | 8915.6401
[19 empty] | 6153.9595 | 126 | 0.004221 | 0.005544 | 0.029547 | 0.039186 | 0.009311 | 0.026394 | 0.034637 | 0.056286 | 6178.8461 | 8932.4099
[19 empty] | 6178.8461 | 125 | 0.0041875 | 0.0055 | 0.029312 | 0.038875 | 0.0092775 | 0.02635 | 0.034402 | 0.055975 | 6203.9309 | 8949.2395
[19 empty] | 6203.9309 | 124 | 0.004154 | 0.005456 | 0.029078 | 0.038564 | 0.009244 | 0.026306 | 0.034168 | 0.055664 | 6229.2163 | 8966.1294
[19 empty] | 6229.2163 | 123 | 0.0041205 | 0.005412 | 0.028844 | 0.038253 | 0.0092105 | 0.026262 | 0.033933 | 0.055353 | 6254.7046 | 8983.0799
[19 empty] | 6254.7046 | 122 | 0.004087 | 0.005368 | 0.028609 | 0.037942 | 0.009177 | 0.026218 | 0.033699 | 0.055042 | 6280.3981 | 9000.0911
[19 empty] | 6280.3981 | 121 | 0.0040535 | 0.005324 | 0.028375 | 0.037631 | 0.0091435 | 0.026174 | 0.033465 | 0.054731 | 6306.2995 | 9017.1635
[19 empty] | 6306.2995 | 120 | 0.00402 | 0.00528 | 0.02814 | 0.03732 | 0.00911 | 0.02613 | 0.03323 | 0.05442 | 6332.411 | 9034.2973
[19 empty] | 6332.411 | 119 | 0.0039865 | 0.005236 | 0.027905 | 0.037009 | 0.0090765 | 0.026086 | 0.032995 | 0.054109 | 6358.7353 | 9051.4929
[19 empty] | 6358.7353 | 118 | 0.003953 | 0.005192 | 0.027671 | 0.036698 | 0.009043 | 0.026042 | 0.032761 | 0.053798 | 6385.2749 | 9068.7505
[19 empty] | 6385.2749 | 117 | 0.0039195 | 0.005148 | 0.027437 | 0.036387 | 0.0090095 | 0.025998 | 0.032526 | 0.053487 | 6412.0324 | 9086.0706
[19 empty] | 6412.0324 | 116 | 0.003886 | 0.005104 | 0.027202 | 0.036076 | 0.008976 | 0.025954 | 0.032292 | 0.053176 | 6439.0104 | 9103.4533
[19 empty] | 6439.0104 | 115 | 0.0038525 | 0.00506 | 0.026968 | 0.035765 | 0.0089425 | 0.02591 | 0.032058 | 0.052865 | 6466.2116 | 9120.899
[19 empty] | 6466.2116 | 114 | 0.003819 | 0.005016 | 0.026733 | 0.035454 | 0.008909 | 0.025866 | 0.031823 | 0.052554 | 6493.6387 | 9138.4081
[19 empty] | 6493.6387 | 113 | 0.0037855 | 0.004972 | 0.026499 | 0.035143 | 0.0088755 | 0.025822 | 0.031588 | 0.052243 | 6521.2945 | 9155.9809
[19 empty] | 6521.2945 | 112 | 0.003752 | 0.004928 | 0.026264 | 0.034832 | 0.008842 | 0.025778 | 0.031354 | 0.051932 | 6549.1817 | 9173.6176
[19 empty] | 6549.1817 | 111 | 0.0037185 | 0.004884 | 0.02603 | 0.034521 | 0.0088085 | 0.025734 | 0.03112 | 0.051621 | 6577.3033 | 9191.3187
[19 empty] | 6577.3033 | 110 | 0.003685 | 0.00484 | 0.025795 | 0.03421 | 0.008775 | 0.02569 | 0.030885 | 0.05131 | 6605.6622 | 9209.0844
[19 empty] | 6605.6622 | 109 | 0.0036515 | 0.004796 | 0.02556 | 0.033899 | 0.0087415 | 0.025646 | 0.030651 | 0.050999 | 6634.2612 | 9226.9151
[19 empty] | 6634.2612 | 108 | 0.003618 | 0.004752 | 0.025326 | 0.033588 | 0.008708 | 0.025602 | 0.030416 | 0.050688 | 6663.1034 | 9244.8111
[19 empty] | 6663.1034 | 107 | 0.0035845 | 0.004708 | 0.025091 | 0.033277 | 0.0086745 | 0.025558 | 0.030181 | 0.050377 | 6692.1918 | 9262.7727
[19 empty] | 6692.1918 | 106 | 0.003551 | 0.004664 | 0.024857 | 0.032966 | 0.008641 | 0.025514 | 0.029947 | 0.050066 | 6721.5294 | 9280.8004
[19 empty] | 6721.5294 | 105 | 0.0035175 | 0.00462 | 0.024623 | 0.032655 | 0.0086075 | 0.02547 | 0.029713 | 0.049755 | 6751.1196 | 9298.8943
[19 empty] | 6751.1196 | 104 | 0.003484 | 0.004576 | 0.024388 | 0.032344 | 0.008574 | 0.025426 | 0.029478 | 0.049444 | 6780.9653 | 9317.055
[19 empty] | 6780.9653 | 103 | 0.0034505 | 0.004532 | 0.024154 | 0.032033 | 0.0085405 | 0.025382 | 0.029244 | 0.049133 | 6811.0699 | 9335.2826
[19 empty] | 6811.0699 | 102 | 0.003417 | 0.004488 | 0.023919 | 0.031722 | 0.008507 | 0.025338 | 0.029009 | 0.048822 | 6841.4367 | 9353.5776
[19 empty] | 6841.4367 | 101 | 0.0033835 | 0.004444 | 0.023685 | 0.031411 | 0.0084735 | 0.025294 | 0.028775 | 0.048511 | 6872.069 | 9371.9403
[19 empty] | 6872.069 | 100 | 0.00335 | 0.0044 | 0.02345 | 0.0311 | 0.00844 | 0.02525 | 0.02854 | 0.0482 | 6902.9703 | 9390.371
[19 empty] | 6902.9703 | 99 | 0.0033165 | 0.004356 | 0.023216 | 0.030789 | 0.0084065 | 0.025206 | 0.028306 | 0.047889 | 6934.1439 | 9408.8702
[19 empty] | 6934.1439 | 98 | 0.003283 | 0.004312 | 0.022981 | 0.030478 | 0.008373 | 0.025162 | 0.028071 | 0.047578 | 6965.5934 | 9427.4381
[19 empty] | 6965.5934 | 97 | 0.0032495 | 0.004268 | 0.022746 | 0.030167 | 0.0083395 | 0.025118 | 0.027837 | 0.047267 | 6997.3224 | 9446.0752
[19 empty] | 6997.3224 | 96 | 0.003216 | 0.004224 | 0.022512 | 0.029856 | 0.008306 | 0.025074 | 0.027602 | 0.046956 | 7029.3346 | 9464.7817
[19 empty] | 7029.3346 | 95 | 0.0031825 | 0.00418 | 0.022277 | 0.029545 | 0.0082725 | 0.02503 | 0.027367 | 0.046645 | 7061.6336 | 9483.5581
[19 empty] | 7061.6336 | 94 | 0.003149 | 0.004136 | 0.022043 | 0.029234 | 0.008239 | 0.024986 | 0.027133 | 0.046334 | 7094.2232 | 9502.4047
[19 empty] | 7094.2232 | 93 | 0.0031155 | 0.004092 | 0.021809 | 0.028923 | 0.0082055 | 0.024942 | 0.026899 | 0.046023 | 7127.1073 | 9521.3218
[19 empty] | 7127.1073 | 92 | 0.003082 | 0.004048 | 0.021574 | 0.028612 | 0.008172 | 0.024898 | 0.026664 | 0.045712 | 7160.2897 | 9540.3099
[19 empty] | 7160.2897 | 91 | 0.0030485 | 0.004004 | 0.02134 | 0.028301 | 0.0081385 | 0.024854 | 0.02643 | 0.045401 | 7193.7744 | 9559.3693
[19 empty] | 7193.7744 | 90 | 0.003015 | 0.00396 | 0.021105 | 0.02799 | 0.008105 | 0.02481 | 0.026195 | 0.04509 | 7227.5654 | 9578.5004
[19 empty] | 7227.5654 | 89 | 0.0029815 | 0.003916 | 0.020871 | 0.027679 | 0.0080715 | 0.024766 | 0.025961 | 0.044779 | 7261.6669 | 9597.7036
[19 empty] | 7261.6669 | 88 | 0.002948 | 0.003872 | 0.020636 | 0.027368 | 0.008038 | 0.024722 | 0.025726 | 0.044468 | 7296.0829 | 9616.9792
[19 empty] | 7296.0829 | 87 | 0.0029145 | 0.003828 | 0.020402 | 0.027057 | 0.0080045 | 0.024678 | 0.025492 | 0.044157 | 7330.8178 | 9636.3276
[19 empty] | 7330.8178 | 86 | 0.002881 | 0.003784 | 0.020167 | 0.026746 | 0.007971 | 0.024634 | 0.025257 | 0.043846 | 7365.8759 | 9655.7492
[19 empty] | 7365.8759 | 85 | 0.0028475 | 0.00374 | 0.019933 | 0.026435 | 0.0079375 | 0.02459 | 0.025023 | 0.043535 | 7401.2615 | 9675.2444
[19 empty] | 7401.2615 | 84 | 0.002814 | 0.003696 | 0.019698 | 0.026124 | 0.007904 | 0.024546 | 0.024788 | 0.043224 | 7436.9791 | 9694.8136
[19 empty] | 7436.9791 | 83 | 0.0027805 | 0.003652 | 0.019463 | 0.025813 | 0.0078705 | 0.024502 | 0.024553 | 0.042913 | 7473.0334 | 9714.4571
[19 empty] | 7473.0334 | 82 | 0.002747 | 0.003608 | 0.019229 | 0.025502 | 0.007837 | 0.024458 | 0.024319 | 0.042602 | 7509.4288 | 9734.1754
[19 empty] | 7509.4288 | 81 | 0.0027135 | 0.003564 | 0.018995 | 0.025191 | 0.0078035 | 0.024414 | 0.024085 | 0.042291 | 7546.1702 | 9753.9689
[19 empty] | 7546.1702 | 80 | 0.00268 | 0.00352 | 0.01876 | 0.02488 | 0.00777 | 0.02437 | 0.02385 | 0.04198 | 7583.2623 | 9773.8379
[19 empty] | 7583.2623 | 79 | 0.0026465 | 0.003476 | 0.018526 | 0.024569 | 0.0077365 | 0.024326 | 0.023616 | 0.041669 | 7620.71 | 9793.7828
[19 empty] | 7620.71 | 78 | 0.002613 | 0.003432 | 0.018291 | 0.024258 | 0.007703 | 0.024282 | 0.023381 | 0.041358 | 7658.5183 | 9813.8041
[19 empty] | 7658.5183 | 77 | 0.0025795 | 0.003388 | 0.018056 | 0.023947 | 0.0076695 | 0.024238 | 0.023147 | 0.041047 | 7696.6922 | 9833.9022
[19 empty] | 7696.6922 | 76 | 0.002546 | 0.003344 | 0.017822 | 0.023636 | 0.007636 | 0.024194 | 0.022912 | 0.040736 | 7735.2369 | 9854.0774
[19 empty] | 7735.2369 | 75 | 0.0025125 | 0.0033 | 0.017588 | 0.023325 | 0.0076025 | 0.02415 | 0.022678 | 0.040425 | 7774.1576 | 9874.3302
[19 empty] | 7774.1576 | 74 | 0.002479 | 0.003256 | 0.017353 | 0.023014 | 0.007569 | 0.024106 | 0.022443 | 0.040114 | 7813.4597 | 9894.661
[19 empty] | 7813.4597 | 73 | 0.0024455 | 0.003212 | 0.017119 | 0.022703 | 0.0075355 | 0.024062 | 0.022209 | 0.039803 | 7853.1487 | 9915.0702
[19 empty] | 7853.1487 | 72 | 0.002412 | 0.003168 | 0.016884 | 0.022392 | 0.007502 | 0.024018 | 0.021974 | 0.039492 | 7893.23 | 9935.5582
[19 empty] | 7893.23 | 71 | 0.0023785 | 0.003124 | 0.01665 | 0.022081 | 0.0074685 | 0.023974 | 0.02174 | 0.039181 | 7933.7092 | 9956.1255
[19 empty] | 7933.7092 | 70 | 0.002345 | 0.00308 | 0.016415 | 0.02177 | 0.007435 | 0.02393 | 0.021505 | 0.03887 | 7974.5922 | 9976.7724
[19 empty] | 7974.5922 | 69 | 0.0023115 | 0.003036 | 0.016181 | 0.021459 | 0.0074015 | 0.023886 | 0.021271 | 0.038559 | 8015.8848 | 9997.4994
[19 empty] | 8015.8848 | 68 | 0.002278 | 0.002992 | 0.015946 | 0.021148 | 0.007368 | 0.023842 | 0.021036 | 0.038248 | 8057.593 | 10018.307
[19 empty] | 8057.593 | 67 | 0.0022445 | 0.002948 | 0.015711 | 0.020837 | 0.0073345 | 0.023798 | 0.020802 | 0.037937 | 8099.7227 | 10039.1955
[19 empty] | 8099.7227 | 66 | 0.002211 | 0.002904 | 0.015477 | 0.020526 | 0.007301 | 0.023754 | 0.020567 | 0.037626 | 8142.2803 | 10060.1653
[19 empty] | 8142.2803 | 65 | 0.0021775 | 0.00286 | 0.015243 | 0.020215 | 0.0072675 | 0.02371 | 0.020332 | 0.037315 | 8185.2719 | 10081.217
[19 empty] | 8185.2719 | 64 | 0.002144 | 0.002816 | 0.015008 | 0.019904 | 0.007234 | 0.023666 | 0.020098 | 0.037004 | 8228.7041 | 10102.351
[19 empty] | 8228.7041 | 63 | 0.0021105 | 0.002772 | 0.014774 | 0.019593 | 0.0072005 | 0.023622 | 0.019863 | 0.036693 | 8272.5833 | 10123.5677
[19 empty] | 8272.5833 | 62 | 0.002077 | 0.002728 | 0.014539 | 0.019282 | 0.007167 | 0.023578 | 0.019629 | 0.036382 | 8316.9163 | 10144.8675
[19 empty] | 8316.9163 | 61 | 0.0020435 | 0.002684 | 0.014305 | 0.018971 | 0.0071335 | 0.023534 | 0.019395 | 0.036071 | 8361.7097 | 10166.2509
[19 empty] | 8361.7097 | 60 | 0.00201 | 0.00264 | 0.01407 | 0.01866 | 0.0071 | 0.02349 | 0.01916 | 0.03576 | 8406.9706 | 10187.7184
[19 empty] | 8406.9706 | 59 | 0.0019765 | 0.002596 | 0.013836 | 0.018349 | 0.0070665 | 0.023446 | 0.018926 | 0.035449 | 8452.706 | 10209.2703
[19 empty] | 8452.706 | 58 | 0.001943 | 0.002552 | 0.013601 | 0.018038 | 0.007033 | 0.023402 | 0.018691 | 0.035138 | 8498.9231 | 10230.9072
[19 empty] | 8498.9231 | 57 | 0.0019095 | 0.002508 | 0.013366 | 0.017727 | 0.0069995 | 0.023358 | 0.018457 | 0.034827 | 8545.6291 | 10252.6296
[19 empty] | 8545.6291 | 56 | 0.001876 | 0.002464 | 0.013132 | 0.017416 | 0.006966 | 0.023314 | 0.018222 | 0.034516 | 8592.8316 | 10274.4378
[19 empty] | 8592.8316 | 55 | 0.0018425 | 0.00242 | 0.012898 | 0.017105 | 0.0069325 | 0.02327 | 0.017988 | 0.034205 | 8640.5382 | 10296.3324
[19 empty] | 8640.5382 | 54 | 0.001809 | 0.002376 | 0.012663 | 0.016794 | 0.006899 | 0.023226 | 0.017753 | 0.033894 | 8688.7567 | 10318.3138
[19 empty] | 8688.7567 | 53 | 0.0017755 | 0.002332 | 0.012429 | 0.016483 | 0.0068655 | 0.023182 | 0.017519 | 0.033583 | 8737.4949 | 10340.3824
[19 empty] | 8737.4949 | 52 | 0.001742 | 0.002288 | 0.012194 | 0.016172 | 0.006832 | 0.023138 | 0.017284 | 0.033272 | 8786.7609 | 10362.5388
[19 empty] | 8786.7609 | 51 | 0.0017085 | 0.002244 | 0.011959 | 0.015861 | 0.0067985 | 0.023094 | 0.017049 | 0.032961 | 8836.563 | 10384.7835
[19 empty] | 8836.563 | 50 | 0.001675 | 0.0022 | 0.011725 | 0.01555 | 0.006765 | 0.02305 | 0.016815 | 0.03265 | 8886.9095 | 10407.1169
[19 empty] | 8886.9095 | 49 | 0.0016415 | 0.002156 | 0.011491 | 0.015239 | 0.0067315 | 0.023006 | 0.016581 | 0.032339 | 8937.8091 | 10429.5395
[19 empty] | 8937.8091 | 48 | 0.001608 | 0.002112 | 0.011256 | 0.014928 | 0.006698 | 0.022962 | 0.016346 | 0.032028 | 8989.2703 | 10452.0517
[19 empty] | 8989.2703 | 47 | 0.0015745 | 0.002068 | 0.011022 | 0.014617 | 0.0066645 | 0.022918 | 0.016112 | 0.031717 | 9041.3022 | 10474.6542
[19 empty] | 9041.3022 | 46 | 0.001541 | 0.002024 | 0.010787 | 0.014306 | 0.006631 | 0.022874 | 0.015877 | 0.031406 | 9093.9137 | 10497.3473
[19 empty] | 9093.9137 | 45 | 0.0015075 | 0.00198 | 0.010552 | 0.013995 | 0.0065975 | 0.02283 | 0.015643 | 0.031095 | 9147.1143 | 10520.1315
[19 empty] | 9147.1143 | 44 | 0.001474 | 0.001936 | 0.010318 | 0.013684 | 0.006564 | 0.022786 | 0.015408 | 0.030784 | 9200.9132 | 10543.0075
[19 empty] | 9200.9132 | 43 | 0.0014405 | 0.001892 | 0.010084 | 0.013373 | 0.0065305 | 0.022742 | 0.015173 | 0.030473 | 9255.3201 | 10565.9756
[19 empty] | 9255.3201 | 42 | 0.001407 | 0.001848 | 0.009849 | 0.013062 | 0.006497 | 0.022698 | 0.014939 | 0.030162 | 9310.3449 | 10589.0363
[19 empty] | 9310.3449 | 41 | 0.0013735 | 0.001804 | 0.0096145 | 0.012751 | 0.0064635 | 0.022654 | 0.014705 | 0.029851 | 9365.9977 | 10612.1903
[19 empty] | 9365.9977 | 40 | 0.00134 | 0.00176 | 0.00938 | 0.01244 | 0.00643 | 0.02261 | 0.01447 | 0.02954 | 9422.2885 | 10635.4379
[19 empty] | 9422.2885 | 39 | 0.0013065 | 0.001716 | 0.0091455 | 0.012129 | 0.0063965 | 0.022566 | 0.014236 | 0.029229 | 9479.2279 | 10658.7797
[19 empty] | 9479.2279 | 38 | 0.001273 | 0.001672 | 0.008911 | 0.011818 | 0.006363 | 0.022522 | 0.014001 | 0.028918 | 9536.8264 | 10682.2163
[19 empty] | 9536.8264 | 37 | 0.0012395 | 0.001628 | 0.0086765 | 0.011507 | 0.0063295 | 0.022478 | 0.013767 | 0.028607 | 9595.0951 | 10705.748
[19 empty] | 9595.0951 | 36 | 0.001206 | 0.001584 | 0.008442 | 0.011196 | 0.006296 | 0.022434 | 0.013532 | 0.028296 | 9654.045 | 10729.3756
[19 empty] | 9654.045 | 35 | 0.0011725 | 0.00154 | 0.0082075 | 0.010885 | 0.0062625 | 0.02239 | 0.013298 | 0.027985 | 9713.6873 | 10753.0994
[19 empty] | 9713.6873 | 34 | 0.001139 | 0.001496 | 0.007973 | 0.010574 | 0.006229 | 0.022346 | 0.013063 | 0.027674 | 9774.0337 | 10776.9201
[19 empty] | 9774.0337 | 33 | 0.0011055 | 0.001452 | 0.0077385 | 0.010263 | 0.0061955 | 0.022302 | 0.012828 | 0.027363 | 9835.096 | 10800.8381
[19 empty] | 9835.096 | 32 | 0.001072 | 0.001408 | 0.007504 | 0.009952 | 0.006162 | 0.022258 | 0.012594 | 0.027052 | 9896.8861 | 10824.854
[19 empty] | 9896.8861 | 31 | 0.0010385 | 0.001364 | 0.0072695 | 0.009641 | 0.0061285 | 0.022214 | 0.01236 | 0.026741 | 9959.4164 | 10848.9683
[19 empty] | 9959.4164 | 30 | 0.001005 | 0.00132 | 0.007035 | 0.00933 | 0.006095 | 0.02217 | 0.012125 | 0.02643 | 10022.6994 | 10873.1816
[19 empty] | 10022.6994 | 29 | 0.0009715 | 0.001276 | 0.0068005 | 0.009019 | 0.0060615 | 0.022126 | 0.011891 | 0.026119 | 10086.748 | 10897.4944
[19 empty] | 10086.748 | 28 | 0.000938 | 0.001232 | 0.006566 | 0.008708 | 0.006028 | 0.022082 | 0.011656 | 0.025808 | 10151.5751 | 10921.9073
[19 empty] | 10151.5751 | 27 | 0.0009045 | 0.001188 | 0.0063315 | 0.008397 | 0.0059945 | 0.022038 | 0.011422 | 0.025497 | 10217.1942 | 10946.4209
[19 empty] | 10217.1942 | 26 | 0.000871 | 0.001144 | 0.006097 | 0.008086 | 0.005961 | 0.021994 | 0.011187 | 0.025186 | 10283.6188 | 10971.0356
[19 empty] | 10283.6188 | 25 | 0.0008375 | 0.0011 | 0.0058625 | 0.007775 | 0.0059275 | 0.02195 | 0.010953 | 0.024875 | 10350.863 | 10995.7521
[19 empty] | 10350.863 | 24 | 0.000804 | 0.001056 | 0.005628 | 0.007464 | 0.005894 | 0.021906 | 0.010718 | 0.024564 | 10418.9408 | 11020.5708
[19 empty] | 10418.9408 | 23 | 0.0007705 | 0.001012 | 0.0053935 | 0.007153 | 0.0058605 | 0.021862 | 0.010483 | 0.024253 | 10487.8668 | 11045.4925
[19 empty] | 10487.8668 | 22 | 0.000737 | 0.000968 | 0.005159 | 0.006842 | 0.005827 | 0.021818 | 0.010249 | 0.023942 | 10557.6558 | 11070.5176
[19 empty] | 10557.6558 | 21 | 0.0007035 | 0.000924 | 0.0049245 | 0.006531 | 0.0057935 | 0.021774 | 0.010014 | 0.023631 | 10628.323 | 11095.6467
[19 empty] | 10628.323 | 20 | 0.00067 | 0.00088 | 0.00469 | 0.00622 | 0.00576 | 0.02173 | 0.00978 | 0.02332 | 10699.8837 | 11120.8805
[19 empty] | 10699.8837 | 19 | 0.0006365 | 0.000836 | 0.0044555 | 0.005909 | 0.0057265 | 0.021686 | 0.0095455 | 0.023009 | 10772.3538 | 11146.2194
[19 empty] | 10772.3538 | 18 | 0.000603 | 0.000792 | 0.004221 | 0.005598 | 0.005693 | 0.021642 | 0.009311 | 0.022698 | 10845.7493 | 11171.6641
[19 empty] | 10845.7493 | 17 | 0.0005695 | 0.000748 | 0.0039865 | 0.005287 | 0.0056595 | 0.021598 | 0.0090765 | 0.022387 | 10920.0867 | 11197.2151
[19 empty] | 10920.0867 | 16 | 0.000536 | 0.000704 | 0.003752 | 0.004976 | 0.005626 | 0.021554 | 0.008842 | 0.022076 | 10995.3829 | 11222.8732
[19 empty] | 10995.3829 | 15 | 0.0005025 | 0.00066 | 0.0035175 | 0.004665 | 0.0055925 | 0.02151 | 0.0086075 | 0.021765 | 11071.6548 | 11248.6387
[19 empty] | 11071.6548 | 14 | 0.000469 | 0.000616 | 0.003283 | 0.004354 | 0.005559 | 0.021466 | 0.008373 | 0.021454 | 11148.9202 | 11274.5124
[19 empty] | 11148.9202 | 13 | 0.0004355 | 0.000572 | 0.0030485 | 0.004043 | 0.0055255 | 0.021422 | 0.0081385 | 0.021143 | 11227.1967 | 11300.4949
[19 empty] | 11227.1967 | 12 | 0.000402 | 0.000528 | 0.002814 | 0.003732 | 0.005492 | 0.021378 | 0.007904 | 0.020832 | 11306.5028 | 11326.5867
[19 empty] | 11306.5028 | 11 | 0.0003685 | 0.000484 | 0.0025795 | 0.003421 | 0.0054585 | 0.021334 | 0.0076695 | 0.020521 | 11386.8571 | 11352.7885
[19 empty] | 11386.8571 | 10 | 0.000335 | 0.00044 | 0.002345 | 0.00311 | 0.005425 | 0.02129 | 0.007435 | 0.02021 | 11468.2786 | 11379.1008
[19 empty] | 11468.2786 | 9 | 0.0003015 | 0.000396 | 0.0021105 | 0.002799 | 0.0053915 | 0.021246 | 0.0072005 | 0.019899 | 11550.7868 | 11405.5244
[19 empty] | 11550.7868 | 8 | 0.000268 | 0.000352 | 0.001876 | 0.002488 | 0.005358 | 0.021202 | 0.006966 | 0.019588 | 11634.4015 | 11432.0598
[19 empty] | 11634.4015 | 7 | 0.0002345 | 0.000308 | 0.0016415 | 0.002177 | 0.0053245 | 0.021158 | 0.0067315 | 0.019277 | 11719.1431 | 11458.7077
[19 empty] | 11719.1431 | 6 | 0.000201 | 0.000264 | 0.001407 | 0.001866 | 0.005291 | 0.021114 | 0.006497 | 0.018966 | 11805.0322 | 11485.4686
[19 empty] | 11805.0322 | 5 | 0.0001675 | 0.00022 | 0.0011725 | 0.001555 | 0.0052575 | 0.02107 | 0.0062625 | 0.018655 | 11892.09 | 11512.3433
[19 empty] | 11892.09 | 4 | 0.000134 | 0.000176 | 0.000938 | 0.001244 | 0.005224 | 0.021026 | 0.006028 | 0.018344 | 11980.3381 | 11539.3323
[19 empty] | 11980.3381 | 3 | 0.0001005 | 0.000132 | 0.0007035 | 0.000933 | 0.0051905 | 0.020982 | 0.0057935 | 0.018033 | 12069.7985 | 11566.4363
[19 empty] | 12069.7985 | 2 | 6.7e-05 | 8.8e-05 | 0.000469 | 0.000622 | 0.005157 | 0.020938 | 0.005559 | 0.017722 | 12160.4938 | 11593.6559
[19 empty] | 12160.4938 | 1 | 3.35e-05 | 4.4e-05 | 0.0002345 | 0.000311 | 0.0051235 | 0.020894 | 0.0053245 | 0.017411 | 12252.4469 | 11620.9918
[19 empty] | 12252.4469 | 0 | 0 | 0 | 0 | 0 | 0.00509 | 0.02085 | 0.00509 | 0.0171 | 12345.6813 | 11648.4447

## Data (hidden)
Cable Data
| Spring | [7 empty] | Summer | [7 empty] | Autumn | [7 empty] | Winter | [7 empty] | Resistance Ω/km |  |  |  | Reactance Ω/km |  | RC1 | XC1 | RC0 | XC0
| Sustained |  |  |  | Cyclic |  |  |  | Sustained |  |  |  | Cyclic |  |  |  | Sustained |  |  |  | Cyclic |  |  |  | Sustained |  |  |  | Cyclic |  |  |  | Load |  | Fault
| Ground | PVC Duct | Rigiduct | PVC Duct | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Ground | PVC Duct | Rigiduct | Air | Phase | Neutral | Phase | Neutral | Phase | Neutral
4 x 600 sqmm (SOLIDAL) | 726 | 601 | 557 | 912 | 840 | 671 | 611 | 912 | 673 | 572 | 533 | 838 | 784 | 646 | 590 | 838 | 712 | 595 | 552 | 912 | 826 | 667 | 608 | 912 | 785 | 628 | 579 | 947 | 900 | 692 | 628 | 947 | 0.067 | 0.067 | 0.067 | 0.067 | 0.088 | 0.088 | 0.067 | 0.088 | 0.268 | 0.352
4 x 740 sqmm (SOLIDAL) | 792 | 657 | 607 | 1021 | 922 | 738 | 669 | 1021 | 733 | 625 | 580 | 938 | 860 | 710 | 646 | 939 | 777 | 650 | 602 | 1021 | 906 | 733 | 665 | 1021 | 856 | 688 | 633 | 1060 | 988 | 763 | 689 | 1060 | 0.053 | 0.053 | 0.053 | 0.053 | 0.0886 | 0.0886 | 0.053 | 0.0886 | 0.212 | 0.3544
7 x 600 sqmm (SOLIDAL) | 1288 | 1122 | 1052 | 1824 | 1544 | 1282 | 1178 | 1824 | 1190 | 1062 | 1034 | 1676 | 1438 | 1230 | 1134 | 1676 | 1234 | 1088 | 1020 | 1824 | 1488 | 1250 | 1148 | 1824 | 1396 | 1180 | 1098 | 1894 | 1662 | 1332 | 1216 | 1894 | 0.0335 | 0.067 | 0.0335 | 0.067 | 0.044 | 0.089 | 0.0335 | 0.044 | 0.2345 | 0.311
7 x 740 sqmm (SOLIDAL) | 1394 | 1222 | 1144 | 2042 | 1684 | 1406 | 1286 | 2042 | 1288 | 1156 | 1084 | 1878 | 1568 | 1346 | 1236 | 1878 | 1338 | 1184 | 1108 | 2042 | 1624 | 1368 | 1254 | 2042 | 1512 | 1284 | 1196 | 2120 | 1814 | 1460 | 1330 | 2120 | 0.0265 | 0.053 | 0.0265 | 0.053 | 0.0443 | 0.0886 | 0.0265 | 0.0443 | 0.1855 | 0.3101
7 x 630 sqmm (CU) | 1590 | 1396 | 1304 | 2358 | 1920 | 1608 | 1470 | 2358 | 1468 | 1320 | 1240 | 2168 | 1784 | 1538 | 1414 | 2168 | 1524 | 1352 | 1266 | 2385 | 1856 | 1566 | 1432 | 2358 | 1724 | 1470 | 1366 | 2450 | 2076 | 1668 | 1520 | 2450 | 0.021 | 0.042 | 0.021 | 0.042 | 0.048 | 0.096 | 0.021 | 0.048 | 0.147 | 0.336
8 x 600 sqmm (SOLIDAL) | 1288 | 1122 | 1052 | 1824 | 1544 | 1282 | 1178 | 1824 | 1190 | 1062 | 1034 | 1676 | 1438 | 1230 | 1134 | 1676 | 1234 | 1088 | 1020 | 1824 | 1488 | 1250 | 1148 | 1824 | 1396 | 1180 | 1098 | 1894 | 1662 | 1332 | 1216 | 1894 | 0.034 | 0.034 | 0.034 | 0.034 | 0.044 | 0.044 | 0.034 | 0.044 | 0.136 | 0.176
8 x 740 sqmm (SOLIDAL) | 1394 | 1222 | 1144 | 2042 | 1684 | 1406 | 1286 | 2042 | 1288 | 1156 | 1084 | 1878 | 1568 | 1346 | 1236 | 1878 | 1338 | 1184 | 1108 | 2042 | 1624 | 1368 | 1254 | 2042 | 1512 | 1284 | 1196 | 2120 | 1814 | 1460 | 1330 | 2120 | 0.027 | 0.027 | 0.027 | 0.027 | 0.044 | 0.044 | 0.027 | 0.044 | 0.108 | 0.176
8 x 630 sqmm (CU) | 1590 | 1396 | 1304 | 2358 | 1920 | 1608 | 1470 | 2358 | 1468 | 1320 | 1240 | 2168 | 1784 | 1538 | 1414 | 2168 | 1524 | 1352 | 1266 | 2385 | 1856 | 1566 | 1432 | 2358 | 1724 | 1470 | 1366 | 2450 | 2076 | 1668 | 1520 | 2450 | 0.021 | 0.021 | 0.021 | 0.021 | 0.048 | 0.048 | 0.021 | 0.048 | 0.084 | 0.192
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43
Transformer Data
[43 empty] | kVA Rating | R | X | Max. Isd | Max TLF (1s)
[43 empty] | 300 | 0.00948 | 0.0281 | 1680 | 2800
[43 empty] | 315 | 0.00901 | 0.0268 | 1680 | 2800
[43 empty] | 500 | 0.00509 | 0.0171 | 2400 | 4400
[43 empty] | 750 | 0.00313 | 0.0115 | 3675 | 5700
[43 empty] | 800 | 0.00291 | 0.0107 | 3675 | 5700
[43 empty] | 1000 | 0.00219 | 0.00863 | 4000 | 7000
0.8
0.81
0.82
0.83
0.84
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
0.95
0.96
0.97
0.98
0.99
1

## MCCB_B_800x1 (hidden)
2 x MCCB Options
|  | T/F MCCB | [9 empty] | Metering MCCB
Transformer | Load (A) | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg
300 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
300 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1600A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1280A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1200A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 1680A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 435 | MCCB load is above T/F rating | [9 empty] | MCCB load is above T/F rating
315 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
315 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1600A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1280A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1200A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 1680A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 457 | MCCB load is above T/F rating | [9 empty] | MCCB load is above T/F rating
500 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
500 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2400A (i.e. 6xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1920A (i.e. 6xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1280A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 1680A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 1920A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 1800A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 2400A (i.e 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 1900A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 725 | MCCB load is above T/F rating | [9 empty] | MCCB load is above T/F rating
750 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
750 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2880A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2000A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3136A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
800 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
800 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2880A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2000A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.1s, I2t on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3136A (i.e. 4xIr) | 0.1s, I2t on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
1000 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
1000 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 3840A (i.e. 8xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2400A (i.e. 6xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3920A (i.e. 5xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
[22 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [9 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg |  |  |  | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg
[23 empty] | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000
[22 empty] | 0 | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
[22 empty] | 160 | [6 empty] | 160 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 160 | 800A | 800A | 800A | 800A | 800A | 800A | 160 | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 160 | 8s | 8s | 8s | 8s | 8s | 8s | 160 | 1600A (i.e. 4xIr) | 1600A (i.e. 4xIr) | 2400A (i.e. 6xIr) | 3200A (i.e. 8xIr) | 3200A (i.e. 8xIr) | 3200A (i.e. 8xIr) | 160 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 160 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 160 | N/A | N/A | N/A | N/A | N/A | N/A | 160 | N/A | N/A | N/A | N/A | N/A | N/A | 160 | [6 empty] | 160 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 160 | 800A | 800A | 800A | 800A | 800A | 800A | 160 | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 160 | 8s | 8s | 8s | 8s | 8s | 8s | 160 | 1280A (i.e. 4xIr) | 1280A (i.e. 4xIr) | 1920A (i.e. 6xIr) | 2560A (i.e. 8xIr) | 2560A (i.e. 8xIr) | 2560A (i.e. 8xIr) | 160 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 160 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 160 | N/A | N/A | N/A | N/A | N/A | N/A | 160 | N/A | N/A | N/A | N/A | N/A | N/A
[22 empty] | 320.1 | [6 empty] | 320.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 320.1 | 800A | 800A | 800A | 800A | 800A | 800A | 320.1 | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 320.1 | 8s | 8s | 8s | 8s | 8s | 8s | 320.1 | 1440A (i.e. 3xIr) | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2880A (i.e. 6xIr) | 2880A (i.e. 6xIr) | 3840A (i.e. 8xIr) | 320.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 320.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 320.1 | N/A | N/A | N/A | N/A | N/A | N/A | 320.1 | N/A | N/A | N/A | N/A | N/A | N/A | 320.1 | [6 empty] | 320.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 320.1 | 800A | 800A | 800A | 800A | 800A | 800A | 320.1 | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 320.1 | 8s | 8s | 8s | 8s | 8s | 8s | 320.1 | 1200A (i.e. 3xIr) | 1200A (i.e. 3xIr) | 1280A (i.e. 4xIr) | 2000A (i.e. 5xIr) | 2000A (i.e. 5xIr) | 2400A (i.e. 6xIr) | 320.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 320.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 320.1 | N/A | N/A | N/A | N/A | N/A | N/A | 320.1 | N/A | N/A | N/A | N/A | N/A | N/A
[22 empty] | 400.1 | [6 empty] | 400.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 400.1 | 800A | 800A | 800A | 800A | 800A | 800A | 400.1 | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 400.1 | 8s | 8s | 8s | 8s | 8s | 8s | 400.1 | 1680A (i.e. 3xIr) | 1680A (i.e. 3xIr) | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 400.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 400.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 400.1 | N/A | N/A | N/A | N/A | N/A | N/A | 400.1 | N/A | N/A | N/A | N/A | N/A | N/A | 400.1 | [6 empty] | 400.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 400.1 | 800A | 800A | 800A | 800A | 800A | 800A | 400.1 | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 400.1 | 8s | 8s | 8s | 8s | 8s | 8s | 400.1 | 1440A (i.e. 3xIr) | 1440A (i.e. 3xIr) | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 400.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 400.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 400.1 | N/A | N/A | N/A | N/A | N/A | N/A | 400.1 | N/A | N/A | N/A | N/A | N/A | N/A
[22 empty] | 435 | MCCB load is above T/F rating | [5 empty] | 435 |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  | 800A | 800A | 800A | 800A | 800A | 435 |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 435 |  | 8s | 8s | 8s | 8s | 8s | 435 |  | 1680A (i.e. 3xIr) | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 435 |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 435 |  | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 435 |  | N/A | N/A | N/A | N/A | N/A | 435 |  | N/A | N/A | N/A | N/A | N/A | 435 | MCCB load is above T/F rating | [5 empty] | 435 |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  | 800A | 800A | 800A | 800A | 800A | 435 |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 435 |  | 8s | 8s | 8s | 8s | 8s | 435 |  | 1440A (i.e. 3xIr) | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 435 |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 435 |  | 3200A (i.e. 4xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 435 |  | N/A | N/A | N/A | N/A | N/A | 435 |  | N/A | N/A | N/A | N/A | N/A
[22 empty] | 457 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 457 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  | 800A | 800A | 800A | 800A | 457 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 457 |  |  | 8s | 8s | 8s | 8s | 457 |  |  | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 457 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 457 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 457 |  |  | N/A | N/A | N/A | N/A | 457 |  |  | N/A | N/A | N/A | N/A | 457 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 457 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  | 800A | 800A | 800A | 800A | 457 |  |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 457 |  |  | 8s | 8s | 8s | 8s | 457 |  |  | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 457 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 457 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 457 |  |  | N/A | N/A | N/A | N/A | 457 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 480.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 480.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 480.1 |  |  | 800A | 800A | 800A | 800A | 480.1 |  |  | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 480.1 |  |  | 8s | 8s | 8s | 8s | 480.1 |  |  | 2160A (i.e. 3xIr) | 3600A (i.e. 5xIr) | 3600A (i.e. 5xIr) | 3600A (i.e. 5xIr) | 480.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, I2t on | 0.2s, IxIxt on | 480.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 480.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 480.1 |  |  | 800A | 800A | 800A | 800A | 480.1 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 480.1 |  |  | 8s | 8s | 8s | 8s | 480.1 |  |  | 1680A (i.e. 3xIr) | 2240A (i.e. 4xIr) | 2240A (i.e. 4xIr) | 2240A (i.e. 4xIr) | 480.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 480.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 560.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 560.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 560.1 |  |  | 800A | 800A | 800A | 800A | 560.1 |  |  | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 560.1 |  |  | 8s | 8s | 8s | 8s | 560.1 |  |  | 2352A (i.e. 3xIr) | 3136A (i.e. 4xIr) | 3136A (i.e. 4xIr) | 3920A (i.e. 5xIr) | 560.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, I2t on | 0.2s, IxIxt on | 560.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 560.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 560.1 |  |  | 800A | 800A | 800A | 800A | 560.1 |  |  | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 560.1 |  |  | 8s | 8s | 8s | 8s | 560.1 |  |  | 1920A (i.e. 3xIr) | 2560A (i.e. 4xIr) | 2560A (i.e. 4xIr) | 2560A (i.e. 4xIr) | 560.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 560.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 640.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 640.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 640.1 |  |  | 800A | 800A | 800A | 800A | 640.1 |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 640.1 |  |  | 8s | 12s | 12s | 12s | 640.1 |  |  | 2352A (i.e. 3xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 640.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 640.1 |  |  | 6400A (i.e. 8xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 640.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 640.1 |  |  | 800A | 800A | 800A | 800A | 640.1 |  |  | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 640.1 |  |  | 8s | 8s | 8s | 8s | 640.1 |  |  | 1800A (i.e. 2.5xIr) | 2160A (i.e. 3xIr) | 2160A (i.e. 3xIr) | 2160A (i.e. 3xIr) | 640.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 640.1 |  |  | 4800A (i.e. 6xIn) | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 720.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 720.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 720.1 |  |  | 800A | 800A | 800A | 800A | 720.1 |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 720.1 |  |  | 12s | 12s | 12s | 12s | 720.1 |  |  | 2400A (i.e 3xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 720.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 720.1 |  |  | 6400A (i.e. 8xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  |  | 720.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 720.1 |  |  | 800A | 800A | 800A | 800A | 720.1 |  |  | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 720.1 |  |  | 8s | 8s | 8s | 8s | 720.1 |  |  | 1900A (i.e. 2.5xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 720.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 720.1 |  |  | 4800A (i.e. 6xIn) | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 725 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 800A | 800A | 800A | 725 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 725 |  |  |  | 12s | 12s | 12s | 725 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 725 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 725 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A | 725 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 800A | 800A | 800A | 725 |  |  |  | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 725 |  |  |  | 8s | 8s | 8s | 725 |  |  |  | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 725 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 725 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A
[22 empty] | 760.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 760.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 760.1 |  |  |  | 800A | 800A | 800A | 760.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 760.1 |  |  |  | 12s | 12s | 12s | 760.1 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 760.1 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 760.1 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 760.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 760.1 |  |  |  | 800A | 800A | 800A | 760.1 |  |  |  | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 760.1 |  |  |  | 8s | 8s | 8s | 760.1 |  |  |  | 2352A (i.e. 3xIr) | 2352A (i.e. 3xIr) | 2352A (i.e. 3xIr) | 760.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 760.1 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 784.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 784.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 784.1 |  |  |  | 800A | 800A | 800A | 784.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 784.1 |  |  |  | 12s | 12s | 12s | 784.1 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 784.1 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 784.1 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating |  |  |  | 784.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 784.1 |  |  |  | 800A | 800A | 800A | 784.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 784.1 |  |  |  | 8s | 8s | 8s | 784.1 |  |  |  | 2400A (i.e. 3xIr) | 2400A (i.e. 3xIr) | 2400A (i.e. 3xIr) | 784.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 784.1 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 800.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating | Load is above MCCB rating | Load is above MCCB rating | Load is above MCCB rating | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | MCCB load is above T/F rating | MCCB load is above T/F rating | MCCB load is above T/F rating | Load is above MCCB rating | Load is above MCCB rating | Load is above MCCB rating | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1
[22 empty] | 2 | [6 empty] | 3 | [6 empty] | 4 | [6 empty] | 5 | [6 empty] | 6 | [6 empty] | 7 | [6 empty] | 8 | [6 empty] | 9 | [6 empty] | 10 | [6 empty] | 11 | [6 empty] | 12 | [6 empty] | 13 | [6 empty] | 14 | [6 empty] | 15 | [6 empty] | 16 | [6 empty] | 17 | [6 empty] | 18 | [6 empty] | 19 | [6 empty] | 20 | [6 empty] | 21

## MCCB_B_800x2 (hidden)
MCCB Settings
|  | T/F MCCB | [10 empty] | Metering MCCB
Transformer | Load (A) | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg
300 | 0 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
300 | 160 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
300 | 320.1 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
300 | 400.1 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
300 | 435 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 0 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 160 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 320.1 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 400.1 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 457 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
500 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
500 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2400A (i.e. 6xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1920A (i.e. 6xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1280A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 1680A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 1920A (i.e. 3xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 1800A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 2400A (i.e 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 1900A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
500 | 725 | MCCB load is above T/F rating | [9 empty] | MCCB load is above T/F rating
750 | 0 | Load is too low for potection | [9 empty] | Load is too low for potection
750 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2880A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2000A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3136A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
750 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
750 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
800 | 0 | Load is too low for potection | [9 empty] | Load is too low for potection
800 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2880A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2000A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3136A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A
800 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 4800A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
800 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
1000 | 0 | Load is too low for potection | [9 empty] | Load is too low for potection
1000 | 160 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 3200A (i.e. 8xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 320.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 3840A (i.e. 8xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2400A (i.e. 6xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 400.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 3360A (i.e. 6xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 480.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 3600A (i.e. 5xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 560.1 |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 3920A (i.e. 5xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 640.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 720.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 760.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 784A (i.e. 0.98xIn) | 8s | 2352A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 784.1 |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 12s | 3200A (i.e. 4xIr) | 0.2s, IxIxt on | 8000A (i.e. 10xIn) | N/A | N/A |  | Micrologic 5.0 | 800A | 800A (i.e. 1.0xIn) | 8s | 2400A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
1000 | 800.1 | Load is above MCCB rating | [9 empty] | Load is above MCCB rating
[22 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg | [6 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg
[23 empty] | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000
[22 empty] | 0 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is too low for protection | Load is too low for potection | Load is too low for potection | Load is too low for potection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is too low for protection | Load is too low for potection | Load is too low for potection | Load is too low for potection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
[22 empty] | 160 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 160 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 160 |  |  | 800A | 800A | 800A | 800A | 160 |  |  | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 160 |  |  | 8s | 8s | 8s | 8s | 160 |  |  | 2400A (i.e. 6xIr) | 3200A (i.e. 8xIr) | 3200A (i.e. 8xIr) | 3200A (i.e. 8xIr) | 160 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 160 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 160 |  |  | N/A | N/A | N/A | N/A | 160 |  |  | N/A | N/A | N/A | N/A | 160 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 160 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 160 |  |  | 800A | 800A | 800A | 800A | 160 |  |  | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 160 |  |  | 8s | 8s | 8s | 8s | 160 |  |  | 1920A (i.e. 6xIr) | 2560A (i.e. 8xIr) | 2560A (i.e. 8xIr) | 2560A (i.e. 8xIr) | 160 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 160 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 160 |  |  | N/A | N/A | N/A | N/A | 160 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 320.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 320.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 320.1 |  |  | 800A | 800A | 800A | 800A | 320.1 |  |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 320.1 |  |  | 8s | 8s | 8s | 8s | 320.1 |  |  | 2400A (i.e. 5xIr) | 2880A (i.e. 6xIr) | 2880A (i.e. 6xIr) | 3840A (i.e. 8xIr) | 320.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 320.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 320.1 |  |  | N/A | N/A | N/A | N/A | 320.1 |  |  | N/A | N/A | N/A | N/A | 320.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 320.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 320.1 |  |  | 800A | 800A | 800A | 800A | 320.1 |  |  | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 320.1 |  |  | 8s | 8s | 8s | 8s | 320.1 |  |  | 1280A (i.e. 4xIr) | 2000A (i.e. 5xIr) | 2000A (i.e. 5xIr) | 2400A (i.e. 6xIr) | 320.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 320.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 320.1 |  |  | N/A | N/A | N/A | N/A | 320.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 400.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 400.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 400.1 |  |  | 800A | 800A | 800A | 800A | 400.1 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 400.1 |  |  | 8s | 8s | 8s | 8s | 400.1 |  |  | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 400.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 400.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 400.1 |  |  | N/A | N/A | N/A | N/A | 400.1 |  |  | N/A | N/A | N/A | N/A | 400.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 400.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 400.1 |  |  | 800A | 800A | 800A | 800A | 400.1 |  |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 400.1 |  |  | 8s | 8s | 8s | 8s | 400.1 |  |  | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 400.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 400.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 400.1 |  |  | N/A | N/A | N/A | N/A | 400.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 435 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 435 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  |  | 800A | 800A | 800A | 800A | 435 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 435 |  |  | 8s | 8s | 8s | 8s | 435 |  |  | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 435 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 435 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 435 |  |  | N/A | N/A | N/A | N/A | 435 |  |  | N/A | N/A | N/A | N/A | 435 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 435 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  |  | 800A | 800A | 800A | 800A | 435 |  |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 435 |  |  | 8s | 8s | 8s | 8s | 435 |  |  | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 435 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 435 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 435 |  |  | N/A | N/A | N/A | N/A | 435 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 457 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 457 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  | 800A | 800A | 800A | 800A | 457 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 457 |  |  | 8s | 8s | 8s | 8s | 457 |  |  | 2240A (i.e. 4xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 3360A (i.e. 6xIr) | 457 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 457 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 457 |  |  | N/A | N/A | N/A | N/A | 457 |  |  | N/A | N/A | N/A | N/A | 457 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 457 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  | 800A | 800A | 800A | 800A | 457 |  |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 457 |  |  | 8s | 8s | 8s | 8s | 457 |  |  | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 2400A (i.e. 5xIr) | 457 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 457 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 457 |  |  | N/A | N/A | N/A | N/A | 457 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 480.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 480.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 480.1 |  |  | 800A | 800A | 800A | 800A | 480.1 |  |  | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 480.1 |  |  | 8s | 8s | 8s | 8s | 480.1 |  |  | 2160A (i.e. 3xIr) | 3600A (i.e. 5xIr) | 3600A (i.e. 5xIr) | 3600A (i.e. 5xIr) | 480.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 480.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 480.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 480.1 |  |  | 800A | 800A | 800A | 800A | 480.1 |  |  | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 560A (i.e. 0.7xIn) | 480.1 |  |  | 8s | 8s | 8s | 8s | 480.1 |  |  | 1680A (i.e. 3xIr) | 2240A (i.e. 4xIr) | 2240A (i.e. 4xIr) | 2240A (i.e. 4xIr) | 480.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 480.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 480.1 |  |  | N/A | N/A | N/A | N/A | 480.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 560.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 560.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 560.1 |  |  | 800A | 800A | 800A | 800A | 560.1 |  |  | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 560.1 |  |  | 8s | 8s | 8s | 8s | 560.1 |  |  | 2352A (i.e. 3xIr) | 3136A (i.e. 4xIr) | 3136A (i.e. 4xIr) | 3920A (i.e. 5xIr) | 560.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 560.1 |  |  | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 6400A (i.e. 8xIn) | 8000A (i.e. 10xIn) | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 560.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 560.1 |  |  | 800A | 800A | 800A | 800A | 560.1 |  |  | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 640A (i.e. 0.8xIn) | 560.1 |  |  | 8s | 8s | 8s | 8s | 560.1 |  |  | 1920A (i.e. 3xIr) | 2560A (i.e. 4xIr) | 2560A (i.e. 4xIr) | 2560A (i.e. 4xIr) | 560.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 560.1 |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 6400A (i.e. 8xIn) | 560.1 |  |  | N/A | N/A | N/A | N/A | 560.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 640.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 640.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 640.1 |  |  | 800A | 800A | 800A | 800A | 640.1 |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 640.1 |  |  | 8s | 12s | 12s | 12s | 640.1 |  |  | 2352A (i.e. 3xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 640.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 640.1 |  |  | 6400A (i.e. 8xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 640.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 640.1 |  |  | 800A | 800A | 800A | 800A | 640.1 |  |  | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 720A (i.e. 0.9xIn) | 640.1 |  |  | 8s | 8s | 8s | 8s | 640.1 |  |  | 1800A (i.e. 2.5xIr) | 2160A (i.e. 3xIr) | 2160A (i.e. 3xIr) | 2160A (i.e. 3xIr) | 640.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 640.1 |  |  | 4800A (i.e. 6xIn) | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 640.1 |  |  | N/A | N/A | N/A | N/A | 640.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 720.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 720.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 720.1 |  |  | 800A | 800A | 800A | 800A | 720.1 |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 720.1 |  |  | 12s | 12s | 12s | 12s | 720.1 |  |  | 2400A (i.e 3xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 720.1 |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 720.1 |  |  | 6400A (i.e. 8xIn) | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  |  | 720.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 720.1 |  |  | 800A | 800A | 800A | 800A | 720.1 |  |  | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 720.1 |  |  | 8s | 8s | 8s | 8s | 720.1 |  |  | 1900A (i.e. 2.5xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 720.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 720.1 |  |  | 4800A (i.e. 6xIn) | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 720.1 |  |  | N/A | N/A | N/A | N/A | 720.1 |  |  | N/A | N/A | N/A | N/A
[22 empty] | 725 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 800A | 800A | 800A | 725 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 725 |  |  |  | 12s | 12s | 12s | 725 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 725 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 725 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A | 725 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 800A | 800A | 800A | 725 |  |  |  | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 760A (i.e. 0.95xIn) | 725 |  |  |  | 8s | 8s | 8s | 725 |  |  |  | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 2280A (i.e. 3xIr) | 725 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 725 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A
[22 empty] | 760.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 760.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 760.1 |  |  |  | 800A | 800A | 800A | 760.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 760.1 |  |  |  | 12s | 12s | 12s | 760.1 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 760.1 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 760.1 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 760.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 760.1 |  |  |  | 800A | 800A | 800A | 760.1 |  |  |  | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 784A (i.e. 0.98xIn) | 760.1 |  |  |  | 8s | 8s | 8s | 760.1 |  |  |  | 2352A (i.e. 3xIr) | 2352A (i.e. 3xIr) | 2352A (i.e. 3xIr) | 760.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 760.1 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 760.1 |  |  |  | N/A | N/A | N/A | 760.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 784.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 784.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 784.1 |  |  |  | 800A | 800A | 800A | 784.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 784.1 |  |  |  | 12s | 12s | 12s | 784.1 |  |  |  | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 3200A (i.e. 4xIr) | 784.1 |  |  |  | 0.2s, IxIxt on | 0.2s, IxIxt on | 0.2s, IxIxt on | 784.1 |  |  |  | 4800A (i.e. 6xIn) | 4800A (i.e. 6xIn) | 8000A (i.e. 10xIn) | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating |  |  |  | 784.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 784.1 |  |  |  | 800A | 800A | 800A | 784.1 |  |  |  | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 800A (i.e. 1.0xIn) | 784.1 |  |  |  | 8s | 8s | 8s | 784.1 |  |  |  | 2400A (i.e. 3xIr) | 2400A (i.e. 3xIr) | 2400A (i.e. 3xIr) | 784.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 784.1 |  |  |  | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 784.1 |  |  |  | N/A | N/A | N/A | 784.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 800.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating | Load is above MCCB rating | Load is above MCCB rating | Load is above MCCB rating | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | MCCB load is above T/F rating | Load is above MCCB rating | Load is above MCCB rating | Load is above MCCB rating | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1 | [6 empty] | 800.1
[22 empty] | 2 | [6 empty] | 3 | [6 empty] | 4 | [6 empty] | 5 | [6 empty] | 6 | [6 empty] | 7 | [6 empty] | 8 | [6 empty] | 9 | [6 empty] | 10 | [6 empty] | 11 | [6 empty] | 12 | [6 empty] | 13 | [6 empty] | 14 | [6 empty] | 15 | [6 empty] | 16 | [6 empty] | 17 | [6 empty] | 18 | [6 empty] | 19 | [6 empty] | 20 | [6 empty] | 21

## MCCB_B_1250A (hidden)
1 x MCCB Options
|  | T/F MCCB | [9 empty] | Metering MCCB
Transformer | Load (A) | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg
300 | 0 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
300 | 435 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 0 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
315 | 457 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
500 | 0 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
500 | 725 | LV cabinet is not suitable for T/F | [9 empty] | LV cabinet is not suitable for T/F
750 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
750 | 250 |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 3125A (i.e. 5xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 500A (i.e. 0.4xIn) | 8s | 2000A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
750 | 500.1 |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 3500A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 2500A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
750 | 625.1 |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 2250A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
750 | 750.1 |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 3375A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 2625A (i.e. 3xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
750 | 875.1 |  | Micrologic 5.0 | 1250A | 1225A (i.e. 0.98xIn) | 8s | 3675A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
750 | 1000.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 8s | 3125A (i.e. 2.5xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 2250A (i.e. 2xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
750 | 1087 | Load is above T/F rating | Load is above T/F rating | [8 empty] | Load is above T/F rating
800 | 0 | Load is too low for protection | Load is too low for protection | [8 empty] | Load is too low for protection
800 | 250 |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 3125A (i.e. 5xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 500A (i.e. 0.4xIn) | 8s | 2000A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
800 | 500.1 |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 3500A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 2500A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
800 | 625.1 |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 2250A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
800 | 750.1 |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 3375A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 2625A (i.e. 3xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
800 | 875.1 |  | Micrologic 5.0 | 1250A | 1225A (i.e. 0.98xIn) | 8s | 3675A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
800 | 1000.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 8s | 3125A (i.e. 2.5xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 2250A (i.e. 2xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
800 | 1125.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 12s | 3125A (i.e. 2.5xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1187.5A (i.e. 0.95xIn) | 8s | 2375A (i.e. 2xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
800 | 1160 | Load is above T/F rating | Load is above T/F rating | [8 empty] | Load is above T/F rating
1000 | 0 | Load is too low for protection | Load is too low for protection | [8 empty] | Load is too low for protection
1000 | 250 |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 3750A (i.e. 6xIr) | 0.2s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 500A (i.e. 0.4xIn) | 8s | 3000A (i.e. 6xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
1000 | 500.1 |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 3750A (i.e. 5xIr) | 0.2s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 2500A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
1000 | 625.1 |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 3500A (i.e. 5xIr) | 0.2s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 2250A (i.e. 4xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
1000 | 750.1 |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 3375A (i.e. 3xIr) | 0.2s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 2625A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
1000 | 875.1 |  | Micrologic 5.0 | 1250A | 1187.5A (i.e. 0.95xIn) | 8s | 3562.5A (i.e. 3xIr) | 0.2s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 2500A (i.e. 2.5xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
1000 | 1000.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 12s | 3750A (i.e. 3xIr) | 0.2s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 2812.5A (i.e. 2.5xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
1000 | 1125.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 12s | 3750A (i.e. 3xIr) | 0.2s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1187.5A (i.e. 0.95xIn) | 8s | 2968.75A (i.e. 2.5xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
1000 | 1187.6 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 12s | 3750A (i.e. 3xIr) | 0.2s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1225A (i.e. 0.95xIn) | 8s | 2450A (i.e. 2xIr) | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
1000 | 1225.1 |  | Micrologic 5.0 | 1250A | 1250A (i.e. 1.0xIn) | 12s | 3750A (i.e. 3xIr) | 0.2s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A |  | Micrologic 5.0 | 1250A | 1250A (i.e. 0.95xIn) | 8s | 2500A | 0.1s, IxIxt on | 3750A (i.e. 3xIn) | N/A | N/A
1000 | 1250.1 | Load is above MCCB Rating | Load is above MCCB Rating | [8 empty] | Load is above MCCB Rating
[22 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg | [6 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg
[23 empty] | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000
[22 empty] | 0 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is too low for protection | Load is too low for protection | Load is too low for protection | 0 |  |  |  |  | Load is too low for protection | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is too low for protection | Load is too low for protection | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
[22 empty] | 250 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 250 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 250 |  |  |  | 1250A | 1250A | 1250A | 250 |  |  |  | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 250 |  |  |  | 8s | 8s | 8s | 250 |  |  |  | 3125A (i.e. 5xIr) | 3125A (i.e. 5xIr) | 3750A (i.e. 6xIr) | 250 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 250 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 250 |  |  |  | N/A | N/A | N/A | 250 |  |  |  | N/A | N/A | N/A | 250 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 250 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 250 |  |  |  | 1250A | 1250A | 1250A | 250 |  |  |  | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 250 |  |  |  | 8s | 8s | 8s | 250 |  |  |  | 2000A (i.e. 4xIr) | 2000A (i.e. 4xIr) | 3000A (i.e. 6xIr) | 250 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 250 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 250 |  |  |  | N/A | N/A | N/A | 250 |  |  |  | N/A | N/A | N/A
[22 empty] | 435 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 435 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  |  |  | 1250A | 1250A | 1250A | 435 |  |  |  | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 435 |  |  |  | 8s | 8s | 8s | 435 |  |  |  | 3125A (i.e. 5xIr) | 3125A (i.e. 5xIr) | 3750A (i.e. 6xIr) | 435 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 435 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 435 |  |  |  | N/A | N/A | N/A | 435 |  |  |  | N/A | N/A | N/A | 435 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 435 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 435 |  |  |  | 1250A | 1250A | 1250A | 435 |  |  |  | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 435 |  |  |  | 8s | 8s | 8s | 435 |  |  |  | 2000A (i.e. 4xIr) | 2000A (i.e. 4xIr) | 3000A (i.e. 6xIr) | 435 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 435 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 435 |  |  |  | N/A | N/A | N/A | 435 |  |  |  | N/A | N/A | N/A
[22 empty] | 457 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 457 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  |  | 1250A | 1250A | 1250A | 457 |  |  |  | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 457 |  |  |  | 8s | 8s | 8s | 457 |  |  |  | 3125A (i.e. 5xIr) | 3125A (i.e. 5xIr) | 3750A (i.e. 6xIr) | 457 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 457 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 457 |  |  |  | N/A | N/A | N/A | 457 |  |  |  | N/A | N/A | N/A | 457 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 457 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 457 |  |  |  | 1250A | 1250A | 1250A | 457 |  |  |  | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 457 |  |  |  | 8s | 8s | 8s | 457 |  |  |  | 2000A (i.e. 4xIr) | 2000A (i.e. 4xIr) | 3000A (i.e. 6xIr) | 457 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 457 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 457 |  |  |  | N/A | N/A | N/A | 457 |  |  |  | N/A | N/A | N/A
[22 empty] | 500.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 500.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 500.1 |  |  |  | 1250A | 1250A | 1250A | 500.1 |  |  |  | 875A (i.e. 0.7xIn) | 875A (i.e. 0.7xIn) | 750A (i.e. 0.6xIn) | 500.1 |  |  |  | 8s | 8s | 8s | 500.1 |  |  |  | 3500A (i.e. 4xIr) | 3500A (i.e. 4xIr) | 3750A (i.e. 5xIr) | 500.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 500.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 500.1 |  |  |  | N/A | N/A | N/A | 500.1 |  |  |  | N/A | N/A | N/A | 500.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 500.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 500.1 |  |  |  | 1250A | 1250A | 1250A | 500.1 |  |  |  | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 500.1 |  |  |  | 8s | 8s | 8s | 500.1 |  |  |  | 2500A (i.e. 4xIr) | 2500A (i.e. 4xIr) | 2500A (i.e. 4xIr) | 500.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 500.1 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 500.1 |  |  |  | N/A | N/A | N/A | 500.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 625.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 625.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 625.1 |  |  |  | 1250A | 1250A | 1250A | 625.1 |  |  |  | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 875A (i.e. 0.7xIn) | 625.1 |  |  |  | 8s | 8s | 8s | 625.1 |  |  |  | 3000A (i.e. 3xIr) | 3000A (i.e. 3xIr) | 3500A (i.e. 5xIr) | 625.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 625.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 625.1 |  |  |  | N/A | N/A | N/A | 625.1 |  |  |  | N/A | N/A | N/A | 625.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 625.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 625.1 |  |  |  | 1250A | 1250A | 1250A | 625.1 |  |  |  | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 625.1 |  |  |  | 8s | 8s | 8s | 625.1 |  |  |  | 2250A (i.e. 3xIr) | 2250A (i.e. 3xIr) | 2250A (i.e. 4xIr) | 625.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 625.1 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 625.1 |  |  |  | N/A | N/A | N/A | 625.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 725 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 1250A | 1250A | 1250A | 725 |  |  |  | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 875A (i.e. 0.7xIn) | 725 |  |  |  | 8s | 8s | 8s | 725 |  |  |  | 3000A (i.e. 3xIr) | 3000A (i.e. 3xIr) | 3500A (i.e. 5xIr) | 725 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 725 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A | 725 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 725 |  |  |  | 1250A | 1250A | 1250A | 725 |  |  |  | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 725 |  |  |  | 8s | 8s | 8s | 725 |  |  |  | 2250A (i.e. 3xIr) | 2250A (i.e. 3xIr) | 2250A (i.e. 4xIr) | 725 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 725 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 725 |  |  |  | N/A | N/A | N/A | 725 |  |  |  | N/A | N/A | N/A
[22 empty] | 750.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 750.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 750.1 |  |  |  | 1250A | 1250A | 1250A | 750.1 |  |  |  | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 750.1 |  |  |  | 8s | 8s | 8s | 750.1 |  |  |  | 3375A (i.e. 3xIr) | 3375A (i.e. 3xIr) | 3375A (i.e. 3xIr) | 750.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 750.1 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 7500A (i.e. 6xIn) | 750.1 |  |  |  | N/A | N/A | N/A | 750.1 |  |  |  | N/A | N/A | N/A | 750.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 750.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 750.1 |  |  |  | 1250A | 1250A | 1250A | 750.1 |  |  |  | 875A (i.e. 0.7xIn) | 875A (i.e. 0.7xIn) | 875A (i.e. 0.7xIn) | 750.1 |  |  |  | 8s | 8s | 8s | 750.1 |  |  |  | 2625A (i.e. 3xIr) | 2625A (i.e. 3xIr) | 2625A (i.e. 3xIr) | 750.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 750.1 |  |  |  | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 5000A (i.e. 4xIn) | 750.1 |  |  |  | N/A | N/A | N/A | 750.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 875.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 875.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 875.1 |  |  |  | 1250A | 1250A | 1250A | 875.1 |  |  |  | 1225A (i.e. 0.98xIn) | 1225A (i.e. 0.98xIn) | 1187.5A (i.e. 0.95xIn) | 875.1 |  |  |  | 8s | 8s | 8s | 875.1 |  |  |  | 3675A (i.e. 3xIr) | 3675A (i.e. 3xIr) | 3562.5A (i.e. 3xIr) | 875.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 875.1 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 875.1 |  |  |  | N/A | N/A | N/A | 875.1 |  |  |  | N/A | N/A | N/A | 875.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 875.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 875.1 |  |  |  | 1250A | 1250A | 1250A | 875.1 |  |  |  | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 875.1 |  |  |  | 8s | 8s | 8s | 875.1 |  |  |  | 3000A (i.e. 3xIr) | 3000A (i.e. 3xIr) | 2500A (i.e. 2.5xIr) | 875.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 875.1 |  |  |  | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 875.1 |  |  |  | N/A | N/A | N/A | 875.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 1000.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 1000.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 1000.1 |  |  |  | 1250A | 1250A | 1250A | 1000.1 |  |  |  | 1250A (i.e. 1.0xIn) | 1250A (i.e. 1.0xIn) | 1250A (i.e. 1.0xIn) | 1000.1 |  |  |  | 8s | 8s | 12s | 1000.1 |  |  |  | 3125A (i.e. 2.5xIr) | 3125A (i.e. 2.5xIr) | 3750A (i.e. 3xIr) | 1000.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.2s, IxIxt on | 1000.1 |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 1000.1 |  |  |  | N/A | N/A | N/A | 1000.1 |  |  |  | N/A | N/A | N/A | 1000.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F |  |  |  | 1000.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | 1000.1 |  |  |  | 1250A | 1250A | 1250A | 1000.1 |  |  |  | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 1000.1 |  |  |  | 8s | 8s | 8s | 1000.1 |  |  |  | 2250A (i.e. 2xIr) | 2250A (i.e. 2xIr) | 2812.5A (i.e. 2.5xIr) | 1000.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 1000.1 |  |  |  | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 1000.1 |  |  |  | N/A | N/A | N/A | 1000.1 |  |  |  | N/A | N/A | N/A
[22 empty] | 1087 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating |  |  | 1087 |  |  |  | Load is above T/F rating | Micrologic 5.0 | Micrologic 5.0 | 1087 |  |  |  |  | 1250A | 1250A | 1087 |  |  |  |  | 1250A (i.e. 1.0xIn) | 1250A (i.e. 1.0xIn) | 1087 |  |  |  |  | 8s | 12s | 1087 |  |  |  |  | 3125A (i.e. 2.5xIr) | 3750A (i.e. 3xIr) | 1087 |  |  |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 1087 |  |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 1087 |  |  |  |  | N/A | N/A | 1087 |  |  |  |  | N/A | N/A | 1087 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating |  |  | 1087 |  |  |  |  | Micrologic 5.0 | Micrologic 5.0 | 1087 |  |  |  |  | 1250A | 1250A | 1087 |  |  |  |  | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 1087 |  |  |  |  | 8s | 8s | 1087 |  |  |  |  | 2250A (i.e. 2xIr) | 2812.5A (i.e. 2.5xIr) | 1087 |  |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 1087 |  |  |  |  | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 1087 |  |  |  |  | N/A | N/A | 1087 |  |  |  |  | N/A | N/A
[22 empty] | 1125.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating |  |  | 1125.1 |  |  |  | Load is above T/F rating | Micrologic 5.0 | Micrologic 5.0 | 1125.1 |  |  |  |  | 1250A | 1250A | 1125.1 |  |  |  |  | 1250A (i.e. 1.0xIn) | 1250A (i.e. 1.0xIn) | 1125.1 |  |  |  |  | 12s | 12s | 1125.1 |  |  |  |  | 3125A (i.e. 2.5xIr) | 3750A (i.e. 3xIr) | 1125.1 |  |  |  |  | 0.1s, IxIxt on | 0.2s, IxIxt on | 1125.1 |  |  |  |  | 5000A (i.e. 4xIn) | 5000A (i.e. 4xIn) | 1125.1 |  |  |  |  | N/A | N/A | 1125.1 |  |  |  |  | N/A | N/A | 1125.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating |  |  | 1125.1 |  |  |  |  | Micrologic 5.0 | Micrologic 5.0 | 1125.1 |  |  |  |  | 1250A | 1250A | 1125.1 |  |  |  |  | 1187.5A (i.e. 0.95xIn) | 1187.5A (i.e. 0.95xIn) | 1125.1 |  |  |  |  | 8s | 8s | 1125.1 |  |  |  |  | 2375A (i.e. 2xIr) | 2968.75A (i.e. 2.5xIr) | 1125.1 |  |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 1125.1 |  |  |  |  | 3750A (i.e. 3xIn) | 3750A (i.e. 3xIn) | 1125.1 |  |  |  |  | N/A | N/A | 1125.1 |  |  |  |  | N/A | N/A
[22 empty] | 1160 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1160 |  |  |  | Load is above T/F rating | Load is above T/F rating | Micrologic 5.0 | 1160 | [5 empty] | 1250A | 1160 | [5 empty] | 1250A (i.e. 1.0xIn) | 1160 | [5 empty] | 12s | 1160 | [5 empty] | 3750A (i.e. 3xIr) | 1160 | [5 empty] | 0.2s, IxIxt on | 1160 | [5 empty] | 5000A (i.e. 4xIn) | 1160 | [5 empty] | N/A | 1160 | [5 empty] | N/A | 1160 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1160 | [5 empty] | Micrologic 5.0 | 1160 | [5 empty] | 1250A | 1160 | [5 empty] | 1187.5A (i.e. 0.95xIn) | 1160 | [5 empty] | 8s | 1160 | [5 empty] | 2968.75A (i.e. 2.5xIr) | 1160 | [5 empty] | 0.1s, IxIxt on | 1160 | [5 empty] | 3750A (i.e. 3xIn) | 1160 | [5 empty] | N/A | 1160 | [5 empty] | N/A
[22 empty] | 1187.6 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1187.6 |  |  |  | Load is above T/F rating | Load is above T/F rating | Micrologic 5.0 | 1187.6 | [5 empty] | 1250A | 1187.6 | [5 empty] | 1250A (i.e. 1.0xIn) | 1187.6 | [5 empty] | 12s | 1187.6 | [5 empty] | 3750A (i.e. 3xIr) | 1187.6 | [5 empty] | 0.2s, IxIxt on | 1187.6 | [5 empty] | 5000A (i.e. 4xIn) | 1187.6 | [5 empty] | N/A | 1187.6 | [5 empty] | N/A | 1187.6 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1187.6 | [5 empty] | Micrologic 5.0 | 1187.6 | [5 empty] | 1250A | 1187.6 | [5 empty] | 1225A (i.e. 0.95xIn) | 1187.6 | [5 empty] | 8s | 1187.6 | [5 empty] | 2450A (i.e. 2xIr) | 1187.6 | [5 empty] | 0.1s, IxIxt on | 1187.6 | [5 empty] | 3750A (i.e. 3xIn) | 1187.6 | [5 empty] | N/A | 1187.6 | [5 empty] | N/A
[22 empty] | 1225.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1225.1 |  |  |  | Load is above T/F rating | Load is above T/F rating | Micrologic 5.0 | 1225.1 | [5 empty] | 1250A | 1225.1 | [5 empty] | 1250A (i.e. 1.0xIn) | 1225.1 | [5 empty] | 12s | 1225.1 | [5 empty] | 3750A (i.e. 3xIr) | 1225.1 | [5 empty] | 0.2s, IxIxt on | 1225.1 | [5 empty] | 5000A (i.e. 4xIn) | 1225.1 | [5 empty] | N/A | 1225.1 | [5 empty] | N/A | 1225.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating |  | 1225.1 | [5 empty] | Micrologic 5.0 | 1225.1 | [5 empty] | 1250A | 1225.1 | [5 empty] | 1250A (i.e. 0.95xIn) | 1225.1 | [5 empty] | 8s | 1225.1 | [5 empty] | 2500A | 1225.1 | [5 empty] | 0.1s, IxIxt on | 1225.1 | [5 empty] | 3750A (i.e. 3xIn) | 1225.1 | [5 empty] | N/A | 1225.1 | [5 empty] | N/A
[22 empty] | 1250.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating | Load is above MCCB Rating | 1250.1 |  |  |  | Load is above T/F rating | Load is above T/F rating | Load is above MCCB Rating | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | LV cabinet is not suitable for T/F | Load is above T/F rating | Load is above T/F rating | Load is above MCCB Rating | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1 | [6 empty] | 1250.1
[22 empty] | 2 | [6 empty] | 3 | [6 empty] | 4 | [6 empty] | 5 | [6 empty] | 6 | [6 empty] | 7 | [6 empty] | 8 | [6 empty] | 9 | [6 empty] | 10 | [6 empty] | 11 | [6 empty] | 12 | [6 empty] | 13 | [6 empty] | 14 | [6 empty] | 15 | [6 empty] | 16 | [6 empty] | 17 | [6 empty] | 18 | [6 empty] | 19 | [6 empty] | 20 | [6 empty] | 21
1187.6
1225.1
1250.1

## MCCB_B_1600A (hidden)
1 x MCCB Options
|  | T/F MCCB | [9 empty] | Metering MCCB
Transformer | Load (A) | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg
300 | 0 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F
300 | 435 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F |  | Load is above T/F rating
315 | 0 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F
315 | 457 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F |  | Load is above T/F rating
500 | 0 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F
500 | 725 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F |  | Load is above T/F rating
750 | 0 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F
750 | 1087 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F |  | Load is above T/F rating
800 | 0 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F
800 | 1160 | LV cabinet not suitable for T/F | [9 empty] | LV cabinet not suitable for T/F |  | Load is above T/F rating
1000 | 0 | Load is too low for protection | [9 empty] | Load is too low for protection
1000 | 320 |  | Micrologic 6.0 | 1600A | 800A (i.e. 0.5xIn) | 8s | 4000A (i.e. 5xIr) | 0.1s, IxIxt on | 9600A (i.e.6xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 640A (i.e. 0.4xIn) | 8s | 3200A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 4xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 640.1 |  | Micrologic 6.0 | 1600A | 1120A (i.e. 0.7xIn) | 8s | 4480A (i.e. 4xIr) | 0.1s, IxIxt on | 9600A (i.e.6xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 800A (i.e. 0.5xIn) | 8s | 3200A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 4xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 800.1 |  | Micrologic 6.0 | 1600A | 1280A (i.e. 0.8xIn) | 8s | 4800A (i.e. 3xIr) | 0.1s, IxIxt on | 9600A (i.e.6xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 960A (i.e. 0.6xIn) | 8s | 2880A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 4xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 960.1 |  | Micrologic 6.0 | 1600A | 1440A (i.e. 0.9xIn) | 8s | 3840A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e.4xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 1120A (i.e. 0.7xIn) | 8s | 2800A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 3xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 1120.1 |  | Micrologic 6.0 | 1600A | 1600A (i.e. 1.0xIn) | 8s | 4000A (i.e. 2.5xIr) | 0.1s, IxIxt on | 6400A (i.e.4xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 1280A (i.e. 0.8xIn) | 8s | 3200A (i.e. 2.5xIr) | 0.1s, IxIxt on | 4800A (i.e. 3xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 1280.1 |  | Micrologic 6.0 | 1600A | 1600A (i.e. 1.0xIn) | 12s | 4000A (i.e. 2.5xIr) | 0.1s, IxIxt on | 6400A (i.e.4xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 1440A (i.e. 0.9xIn) | 8s | 2880A (i.e. 2xIr) | 0.1s, IxIxt on | 4800A (i.e. 3xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 1440.1 |  | Micrologic 6.0 | 1600A | 1600A (i.e. 1.0xIn) | 12s | 4000A (i.e. 2.5xIr) | 0.1s, IxIxt on | 6400A (i.e.4xIn) | 1200A (i.e. J) | 0.4s IxIxt off |  | Micrologic 6.0 | 1600A | 1520A (i.e. 0.95xIn) | 8s | 3040A (i.e. 2xIr) | 0.1s, IxIxt on | 4800A (i.e. 3xIn) | 960A (i.e. F) | 0.3s IxIxt off
1000 | 1450 | Load is above T/F rating | [9 empty] | Load is above T/F rating
[22 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg | [6 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg
[23 empty] | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000
[22 empty] | 0 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
[22 empty] | 320 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 320 | [5 empty] | Micrologic 6.0 | 320 | [5 empty] | 1600A | 320 | [5 empty] | 800A (i.e. 0.5xIn) | 320 | [5 empty] | 8s | 320 | [5 empty] | 4000A (i.e. 5xIr) | 320 | [5 empty] | 0.1s, IxIxt on | 320 | [5 empty] | 9600A (i.e.6xIn) | 320 | [5 empty] | 1200A (i.e. J) | 320 | [5 empty] | 0.4s IxIxt off | 320 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 320 | [5 empty] | Micrologic 6.0 | 320 | [5 empty] | 1600A | 320 | [5 empty] | 640A (i.e. 0.4xIn) | 320 | [5 empty] | 8s | 320 | [5 empty] | 3200A (i.e. 5xIr) | 320 | [5 empty] | 0.1s, IxIxt on | 320 | [5 empty] | 6400A (i.e. 4xIn) | 320 | [5 empty] | 960A (i.e. F) | 320 | [5 empty] | 0.3s IxIxt off
[22 empty] | 435 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 435 | [5 empty] | Micrologic 6.0 | 435 | [5 empty] | 1600A | 435 | [5 empty] | 800A (i.e. 0.5xIn) | 435 | [5 empty] | 8s | 435 | [5 empty] | 4000A (i.e. 5xIr) | 435 | [5 empty] | 0.1s, IxIxt on | 435 | [5 empty] | 9600A (i.e.6xIn) | 435 | [5 empty] | 1200A (i.e. J) | 435 | [5 empty] | 0.4s IxIxt off | 435 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 435 | [5 empty] | Micrologic 6.0 | 435 | Load is above T/F rating |  |  |  |  | 1600A | 435 | [5 empty] | 640A (i.e. 0.4xIn) | 435 | [5 empty] | 8s | 435 | [5 empty] | 3200A (i.e. 5xIr) | 435 | [5 empty] | 0.1s, IxIxt on | 435 | [5 empty] | 6400A (i.e. 4xIn) | 435 | [5 empty] | 960A (i.e. F) | 435 | [5 empty] | 0.3s IxIxt off
[22 empty] | 457 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 457 | [5 empty] | Micrologic 6.0 | 457 | [5 empty] | 1600A | 457 | [5 empty] | 800A (i.e. 0.5xIn) | 457 | [5 empty] | 8s | 457 | [5 empty] | 4000A (i.e. 5xIr) | 457 | [5 empty] | 0.1s, IxIxt on | 457 | [5 empty] | 9600A (i.e.6xIn) | 457 | [5 empty] | 1200A (i.e. J) | 457 | [5 empty] | 0.4s IxIxt off | 457 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 457 | [5 empty] | Micrologic 6.0 | 457 | Load is above T/F rating | Load is above T/F rating |  |  |  | 1600A | 457 | [5 empty] | 640A (i.e. 0.4xIn) | 457 | [5 empty] | 8s | 457 | [5 empty] | 3200A (i.e. 5xIr) | 457 | [5 empty] | 0.1s, IxIxt on | 457 | [5 empty] | 6400A (i.e. 4xIn) | 457 | [5 empty] | 960A (i.e. F) | 457 | [5 empty] | 0.3s IxIxt off
[22 empty] | 640.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 640.1 | [5 empty] | Micrologic 6.0 | 640.1 | [5 empty] | 1600A | 640.1 | [5 empty] | 1120A (i.e. 0.7xIn) | 640.1 | [5 empty] | 8s | 640.1 | [5 empty] | 4480A (i.e. 4xIr) | 640.1 | [5 empty] | 0.1s, IxIxt on | 640.1 | [5 empty] | 9600A (i.e.6xIn) | 640.1 | [5 empty] | 1200A (i.e. J) | 640.1 | [5 empty] | 0.4s IxIxt off | 640.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 640.1 | [5 empty] | Micrologic 6.0 | 640.1 | Load is above T/F rating | Load is above T/F rating |  |  |  | 1600A | 640.1 | [5 empty] | 800A (i.e. 0.5xIn) | 640.1 | [5 empty] | 8s | 640.1 | [5 empty] | 3200A (i.e. 4xIr) | 640.1 | [5 empty] | 0.1s, IxIxt on | 640.1 | [5 empty] | 6400A (i.e. 4xIn) | 640.1 | [5 empty] | 960A (i.e. F) | 640.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 725 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 725 | [5 empty] | Micrologic 6.0 | 725 | [5 empty] | 1600A | 725 | [5 empty] | 1120A (i.e. 0.7xIn) | 725 | [5 empty] | 8s | 725 | [5 empty] | 4480A (i.e. 4xIr) | 725 | [5 empty] | 0.1s, IxIxt on | 725 | [5 empty] | 9600A (i.e.6xIn) | 725 | [5 empty] | 1200A (i.e. J) | 725 | [5 empty] | 0.4s IxIxt off | 725 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 725 | [5 empty] | Micrologic 6.0 | 725 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  |  | 1600A | 725 | [5 empty] | 800A (i.e. 0.5xIn) | 725 | [5 empty] | 8s | 725 | [5 empty] | 3200A (i.e. 4xIr) | 725 | [5 empty] | 0.1s, IxIxt on | 725 | [5 empty] | 6400A (i.e. 4xIn) | 725 | [5 empty] | 960A (i.e. F) | 725 | [5 empty] | 0.3s IxIxt off
[22 empty] | 800.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 800.1 | [5 empty] | Micrologic 6.0 | 800.1 | [5 empty] | 1600A | 800.1 | [5 empty] | 1280A (i.e. 0.8xIn) | 800.1 | [5 empty] | 8s | 800.1 | [5 empty] | 4800A (i.e. 3xIr) | 800.1 | [5 empty] | 0.1s, IxIxt on | 800.1 | [5 empty] | 9600A (i.e.6xIn) | 800.1 | [5 empty] | 1200A (i.e. J) | 800.1 | [5 empty] | 0.4s IxIxt off | 800.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 800.1 | [5 empty] | Micrologic 6.0 | 800.1 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  |  | 1600A | 800.1 | [5 empty] | 960A (i.e. 0.6xIn) | 800.1 | [5 empty] | 8s | 800.1 | [5 empty] | 2880A (i.e. 3xIr) | 800.1 | [5 empty] | 0.1s, IxIxt on | 800.1 | [5 empty] | 6400A (i.e. 4xIn) | 800.1 | [5 empty] | 960A (i.e. F) | 800.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 960.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 960.1 | [5 empty] | Micrologic 6.0 | 960.1 | [5 empty] | 1600A | 960.1 | [5 empty] | 1440A (i.e. 0.9xIn) | 960.1 | [5 empty] | 8s | 960.1 | [5 empty] | 3840A (i.e. 4xIr) | 960.1 | [5 empty] | 0.1s, IxIxt on | 960.1 | [5 empty] | 6400A (i.e.4xIn) | 960.1 | [5 empty] | 1200A (i.e. J) | 960.1 | [5 empty] | 0.4s IxIxt off | 960.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 960.1 | [5 empty] | Micrologic 6.0 | 960.1 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  |  | 1600A | 960.1 | [5 empty] | 1120A (i.e. 0.7xIn) | 960.1 | [5 empty] | 8s | 960.1 | [5 empty] | 2800A (i.e. 2.5xIr) | 960.1 | [5 empty] | 0.1s, IxIxt on | 960.1 | [5 empty] | 4800A (i.e. 3xIn) | 960.1 | [5 empty] | 960A (i.e. F) | 960.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1087 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1087 | [5 empty] | Micrologic 6.0 | 1087 | [5 empty] | 1600A | 1087 | [5 empty] | 1440A (i.e. 0.9xIn) | 1087 | [5 empty] | 8s | 1087 | [5 empty] | 3840A (i.e. 4xIr) | 1087 | [5 empty] | 0.1s, IxIxt on | 1087 | [5 empty] | 6400A (i.e.4xIn) | 1087 | [5 empty] | 1200A (i.e. J) | 1087 | [5 empty] | 0.4s IxIxt off | 1087 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1087 | [5 empty] | Micrologic 6.0 | 1087 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  | 1600A | 1087 | [5 empty] | 1120A (i.e. 0.7xIn) | 1087 | [5 empty] | 8s | 1087 | [5 empty] | 2800A (i.e. 2.5xIr) | 1087 | [5 empty] | 0.1s, IxIxt on | 1087 | [5 empty] | 4800A (i.e. 3xIn) | 1087 | [5 empty] | 960A (i.e. F) | 1087 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1120.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1120.1 | [5 empty] | Micrologic 6.0 | 1120.1 | [5 empty] | 1600A | 1120.1 | [5 empty] | 1600A (i.e. 1.0xIn) | 1120.1 | [5 empty] | 8s | 1120.1 | [5 empty] | 4000A (i.e. 2.5xIr) | 1120.1 | [5 empty] | 0.1s, IxIxt on | 1120.1 | [5 empty] | 6400A (i.e.4xIn) | 1120.1 | [5 empty] | 1200A (i.e. J) | 1120.1 | [5 empty] | 0.4s IxIxt off | 1120.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1120.1 | [5 empty] | Micrologic 6.0 | 1120.1 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  | 1600A | 1120.1 | [5 empty] | 1280A (i.e. 0.8xIn) | 1120.1 | [5 empty] | 8s | 1120.1 | [5 empty] | 3200A (i.e. 2.5xIr) | 1120.1 | [5 empty] | 0.1s, IxIxt on | 1120.1 | [5 empty] | 4800A (i.e. 3xIn) | 1120.1 | [5 empty] | 960A (i.e. F) | 1120.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1160 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1160 | [5 empty] | Micrologic 6.0 | 1160 | [5 empty] | 1600A | 1160 | [5 empty] | 1600A (i.e. 1.0xIn) | 1160 | [5 empty] | 8s | 1160 | [5 empty] | 4000A (i.e. 2.5xIr) | 1160 | [5 empty] | 0.1s, IxIxt on | 1160 | [5 empty] | 6400A (i.e.4xIn) | 1160 | [5 empty] | 1200A (i.e. J) | 1160 | [5 empty] | 0.4s IxIxt off | 1160 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1160 | [5 empty] | Micrologic 6.0 | 1160 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | 1600A | 1160 | [5 empty] | 1280A (i.e. 0.8xIn) | 1160 | [5 empty] | 8s | 1160 | [5 empty] | 3200A (i.e. 2.5xIr) | 1160 | [5 empty] | 0.1s, IxIxt on | 1160 | [5 empty] | 4800A (i.e. 3xIn) | 1160 | [5 empty] | 960A (i.e. F) | 1160 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1280.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1280.1 | [5 empty] | Micrologic 6.0 | 1280.1 | [5 empty] | 1600A | 1280.1 | [5 empty] | 1600A (i.e. 1.0xIn) | 1280.1 | [5 empty] | 12s | 1280.1 | [5 empty] | 4000A (i.e. 2.5xIr) | 1280.1 | [5 empty] | 0.1s, IxIxt on | 1280.1 | [5 empty] | 6400A (i.e.4xIn) | 1280.1 | [5 empty] | 1200A (i.e. J) | 1280.1 | [5 empty] | 0.4s IxIxt off | 1280.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1280.1 | [5 empty] | Micrologic 6.0 | 1280.1 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | 1600A | 1280.1 | [5 empty] | 1440A (i.e. 0.9xIn) | 1280.1 | [5 empty] | 8s | 1280.1 | [5 empty] | 2880A (i.e. 2xIr) | 1280.1 | [5 empty] | 0.1s, IxIxt on | 1280.1 | [5 empty] | 4800A (i.e. 3xIn) | 1280.1 | [5 empty] | 960A (i.e. F) | 1280.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1440.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1440.1 | [5 empty] | Micrologic 6.0 | 1440.1 | [5 empty] | 1600A | 1440.1 | [5 empty] | 1600A (i.e. 1.0xIn) | 1440.1 | [5 empty] | 12s | 1440.1 | [5 empty] | 4000A (i.e. 2.5xIr) | 1440.1 | [5 empty] | 0.1s, IxIxt on | 1440.1 | [5 empty] | 6400A (i.e.4xIn) | 1440.1 | [5 empty] | 1200A (i.e. J) | 1440.1 | [5 empty] | 0.4s IxIxt off | 1440.1 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F |  | 1440.1 | [5 empty] | Micrologic 6.0 | 1440.1 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | 1600A | 1440.1 | [5 empty] | 1520A (i.e. 0.95xIn) | 1440.1 | [5 empty] | 8s | 1440.1 | [5 empty] | 3040A (i.e. 2xIr) | 1440.1 | [5 empty] | 0.1s, IxIxt on | 1440.1 | [5 empty] | 4800A (i.e. 3xIn) | 1440.1 | [5 empty] | 960A (i.e. F) | 1440.1 | [5 empty] | 0.3s IxIxt off
[22 empty] | 1450 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | Load is above T/F rating | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | LV cabinet not suitable for T/F | Load is above T/F rating | 1450 | [6 empty] | 1450 | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating | Load is above T/F rating |  | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450
[22 empty] | 2 | [6 empty] | 3 | [6 empty] | 4 | [6 empty] | 5 | [6 empty] | 6 | [6 empty] | 7 | [6 empty] | 8 | [6 empty] | 9 | [6 empty] | 10 | [6 empty] | 11 | [6 empty] | 12 | [6 empty] | 13 | [6 empty] | 14 | [6 empty] | 15 | [6 empty] | 16 | [6 empty] | 17 | [6 empty] | 18 | [6 empty] | 19 | [6 empty] | 20 | [6 empty] | 21

## MCCB C (hidden)
Metering MCCB
Transformer | Load (A) | Comments | Trip Unit | In | Ir | tr | Isd | tsd | Ii | Ig | tg
300 | 0 | Load is too low for protection
300 | 160 |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1600A (i.e. 5xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 320.1 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1600A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 400.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
300 | 435
315 | 0 | Load is too low for protection
315 | 160 |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 1600A (i.e. 5xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 320.1 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 1600A (i.e. 4xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 400.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 1440A (i.e. 3xIr) | 0.1s, IxIxt on | 3200A (i.e. 4xIn) | N/A | N/A
315 | 457
500 | 0 | Load is too low for protection
500 | 160 |  | Micrologic 5.0 | 800A | 320A (i.e. 0.4xIn) | 8s | 2560A (i.e. 8xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
500 | 320.1 |  | Micrologic 5.0 | 800A | 400A (i.e. 0.5xIn) | 8s | 2400A (i.e. 6xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
500 | 400.1 |  | Micrologic 5.0 | 800A | 480A (i.e. 0.6xIn) | 8s | 2400A (i.e. 5xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
500 | 480.1 |  | Micrologic 5.0 | 800A | 560A (i.e. 0.7xIn) | 8s | 2240A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
500 | 560.1 |  | Micrologic 5.0 | 800A | 640A (i.e. 0.8xIn) | 8s | 2560A (i.e. 4xIr) | 0.1s, IxIxt on | 6400A (i.e. 8xIn) | N/A | N/A
500 | 640.1 |  | Micrologic 5.0 | 800A | 720A (i.e. 0.9xIn) | 8s | 2160A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 6xIn) | N/A | N/A
500 | 720.1 |  | Micrologic 5.0 | 800A | 760A (i.e. 0.95xIn) | 8s | 2280A (i.e. 3xIr) | 0.1s, IxIxt on | 6400A (i.e. 6xIn) | N/A | N/A
500 | 725
750 | 0 | Load is too low for protection
750 | 250 |  | Micrologic 5.0 | 1250A | 500A (i.e. 0.4xIn) | 8s | 3000A (i.e. 6xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 500.1 |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 3125A (i.e. 5xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 625.1 |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 3000A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 750.1 |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 3500A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 875.1 |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 1000.1 |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 3375A (i.e. 3xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
750 | 1087
800 | 0 | Load is too low for protection
800 | 250 |  | Micrologic 5.0 | 1250A | 500A (i.e. 0.4xIn) | 8s | 3000A (i.e. 6xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
800 | 500.1 |  | Micrologic 5.0 | 1250A | 625A (i.e. 0.5xIn) | 8s | 3125A (i.e. 5xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
800 | 625.1 |  | Micrologic 5.0 | 1250A | 750A (i.e. 0.6xIn) | 8s | 3000A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
800 | 750.1 |  | Micrologic 5.0 | 1250A | 875A (i.e. 0.7xIn) | 8s | 3500A (i.e. 4xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
800 | 875.1 |  | Micrologic 5.0 | 1250A | 1000A (i.e. 0.8xIn) | 8s | 3000A (i.e. 3xIr) | 0.1s, IxIxt on | 7500A (i.e. 6xIn) | N/A | N/A
800 | 1000.1 |  | Micrologic 5.0 | 1250A | 1125A (i.e. 0.9xIn) | 8s | 3375A (i.e. 3xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
800 | 1125.1 |  | Micrologic 5.0 | 1250A | 1188A (i.e. 0.95xIn) | 8s | 2967A (i.e. 2.5xIr) | 0.1s, IxIxt on | 5000A (i.e. 4xIn) | N/A | N/A
800 | 1160
1000 | 0 | Load is too low for protection
1000 | 320 |  | Micrologic 6.0 | 1600A | 640A (i.e. 0.4xIn) | 8s | 3840A (i.e. 6xIr) | 0.1s, IxIxt on | 9600A (i.e. 6xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 640.1 |  | Micrologic 6.0 | 1600A | 800A (i.e. 0.5xIn) | 8s | 4000A (i.e. 5xIr) | 0.1s, IxIxt on | 9600A (i.e. 6xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 800.1 |  | Micrologic 6.0 | 1600A | 960A (i.e. 0.6xIn) | 8s | 3840A (i.e. 4xIr) | 0.1s, IxIxt on | 9600A (i.e. 6xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 960.1 |  | Micrologic 6.0 | 1600A | 1120A (i.e. 0.7xIn) | 8s | 3360A (i.e. 3xIr) | 0.1s, IxIxt on | 9600A (i.e. 6xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 1120.1 |  | Micrologic 6.0 | 1600A | 1280A (i.e. 0.8xIn) | 8s | 3840A (i.e. 3xIr) | 0.1s, IxIxt on | 9600A (i.e. 6xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 1280.1 |  | Micrologic 6.0 | 1600A | 1440A (i.e. 0.9xIn) | 8s | 3600A (i.e. 2.5xIr) | 0.1s, IxIxt on | 6400A (i.e. 4xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 1440.1 |  | Micrologic 6.0 | 1600A | 1520A (i.e. 0.95xIn) | 8s | 3800A (i.e. 2.5xIr) | 0.1s, IxIxt on | 6400A (i.e. 4xIn) | 1200A (i.e. J) | 0.4s, Ixixt off
1000 | 1450
[12 empty] | Comments | [6 empty] | Trip Unit | [6 empty] | In | [6 empty] | Ir | [6 empty] | tr | [6 empty] | Isd | [6 empty] | tsd | [6 empty] | Ii | [6 empty] | Ig | [6 empty] | tg
[13 empty] | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000 |  | 300 | 315 | 500 | 750 | 800 | 1000
[12 empty] | 0 | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | Load is too low for protection | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
[12 empty] | 160 |  |  |  | Load is too low for protection | Load is too low for protection | Load is too low for protection | 160 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 |  |  |  | 160 | 800A | 800A | 800A |  |  |  | 160 | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) |  |  |  | 160 | 8s | 8s | 8s |  |  |  | 160 | 1600A (i.e. 5xIr) | 1600A (i.e. 5xIr) | 2560A (i.e. 8xIr) |  |  |  | 160 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on |  |  |  | 160 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) |  |  |  | 160 | N/A | N/A | N/A |  |  |  | 160 | N/A | N/A | N/A
[12 empty] | 250 | [5 empty] | Load is too low for protection | 250 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 |  | 250 | 800A | 800A | 800A | 1250A | 1250A |  | 250 | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) |  | 250 | 8s | 8s | 8s | 8s | 8s |  | 250 | 1600A (i.e. 5xIr) | 1600A (i.e. 5xIr) | 2560A (i.e. 8xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) |  | 250 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on |  | 250 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) |  | 250 | N/A | N/A | N/A | N/A | N/A |  | 250 | N/A | N/A | N/A | N/A | N/A
[12 empty] | 320 | [6 empty] | 320 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 320 | 800A | 800A | 800A | 1250A | 1250A | 1600A | 320 | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 320A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 320 | 8s | 8s | 8s | 8s | 8s | 8s | 320 | 1600A (i.e. 5xIr) | 1600A (i.e. 5xIr) | 2560A (i.e. 8xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 320 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 320 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 320 | N/A | N/A | N/A | N/A | N/A | 1200A (i.e. J) | 320 | N/A | N/A | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 320.1 | [6 empty] | 320.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 320.1 | 800A | 800A | 800A | 1250A | 1250A | 1600A | 320.1 | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 400A (i.e. 0.5xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 320.1 | 8s | 8s | 8s | 8s | 8s | 8s | 320.1 | 1600A (i.e. 4xIr) | 1600A (i.e. 4xIr) | 2400A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 320.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 320.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 320.1 | N/A | N/A | N/A | N/A | N/A | 1200A (i.e. J) | 320.1 | N/A | N/A | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 400.1 | [6 empty] | 400.1 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 400.1 | 800A | 800A | 800A | 1250A | 1250A | 1600A | 400.1 | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 400.1 | 8s | 8s | 8s | 8s | 8s | 8s | 400.1 | 1440A (i.e. 3xIr) | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 400.1 | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 400.1 | 3200A (i.e. 4xIn) | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 400.1 | N/A | N/A | N/A | N/A | N/A | 1200A (i.e. J) | 400.1 | N/A | N/A | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 435 | [6 empty] | 435 |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 435 |  | 800A | 800A | 1250A | 1250A | 1600A | 435 |  | 480A (i.e. 0.6xIn) | 480A (i.e. 0.6xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 435 |  | 8s | 8s | 8s | 8s | 8s | 435 |  | 1440A (i.e. 3xIr) | 2400A (i.e. 5xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 435 |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 435 |  | 3200A (i.e. 4xIn) | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 435 |  | N/A | N/A | N/A | N/A | 1200A (i.e. J) | 435 |  | N/A | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 457 | [6 empty] | 457 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 457 |  |  | 800A | 1250A | 1250A | 1600A | 457 |  |  | 480A (i.e. 0.6xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 457 |  |  | 8s | 8s | 8s | 8s | 457 |  |  | 2400A (i.e. 5xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 457 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 457 |  |  | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 457 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 457 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 480.1 | [6 empty] | 480.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 480.1 |  |  | 800A | 1250A | 1250A | 1600A | 480.1 |  |  | 560A (i.e. 0.7xIn) | 500A (i.e. 0.4xIn) | 500A (i.e. 0.4xIn) | 640A (i.e. 0.4xIn) | 480.1 |  |  | 8s | 8s | 8s | 8s | 480.1 |  |  | 2240A (i.e. 4xIr) | 3000A (i.e. 6xIr) | 3000A (i.e. 6xIr) | 3840A (i.e. 6xIr) | 480.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 480.1 |  |  | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 480.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 480.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 500.1 | [6 empty] | 500.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 500.1 |  |  | 800A | 1250A | 1250A | 1600A | 500.1 |  |  | 560A (i.e. 0.7xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 640A (i.e. 0.4xIn) | 500.1 |  |  | 8s | 8s | 8s | 8s | 500.1 |  |  | 2240A (i.e. 4xIr) | 3125A (i.e. 5xIr) | 3125A (i.e. 5xIr) | 3840A (i.e. 6xIr) | 500.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 500.1 |  |  | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 500.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 500.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 560.1 | [6 empty] | 560.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 560.1 |  |  | 800A | 1250A | 1250A | 1600A | 560.1 |  |  | 640A (i.e. 0.8xIn) | 625A (i.e. 0.5xIn) | 625A (i.e. 0.5xIn) | 640A (i.e. 0.4xIn) | 560.1 |  |  | 8s | 8s | 8s | 8s | 560.1 |  |  | 2560A (i.e. 4xIr) | 3125A (i.e. 5xIr) | 3125A (i.e. 5xIr) | 3840A (i.e. 6xIr) | 560.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 560.1 |  |  | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 560.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 560.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 625.1 | [6 empty] | 625.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 625.1 |  |  | 800A | 1250A | 1250A | 1600A | 625.1 |  |  | 640A (i.e. 0.8xIn) | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 640A (i.e. 0.4xIn) | 625.1 |  |  | 8s | 8s | 8s | 8s | 625.1 |  |  | 2560A (i.e. 4xIr) | 3000A (i.e. 4xIr) | 3000A (i.e. 4xIr) | 3840A (i.e. 6xIr) | 625.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 625.1 |  |  | 6400A (i.e. 8xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 625.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 625.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 640.1 | [6 empty] | 640.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 640.1 |  |  | 800A | 1250A | 1250A | 1600A | 640.1 |  |  | 720A (i.e. 0.9xIn) | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 800A (i.e. 0.5xIn) | 640.1 |  |  | 8s | 8s | 8s | 8s | 640.1 |  |  | 2160A (i.e. 3xIr) | 3000A (i.e. 4xIr) | 3000A (i.e. 4xIr) | 4000A (i.e. 5xIr) | 640.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 640.1 |  |  | 6400A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 640.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 640.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 720.1 | [6 empty] | 720.1 |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 720.1 |  |  | 800A | 1250A | 1250A | 1600A | 720.1 |  |  | 760A (i.e. 0.95xIn) | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 800A (i.e. 0.5xIn) | 720.1 |  |  | 8s | 8s | 8s | 8s | 720.1 |  |  | 2280A (i.e. 3xIr) | 3000A (i.e. 4xIr) | 3000A (i.e. 4xIr) | 4000A (i.e. 5xIr) | 720.1 |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 720.1 |  |  | 6400A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 720.1 |  |  | N/A | N/A | N/A | 1200A (i.e. J) | 720.1 |  |  | N/A | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 725 | [6 empty] | 725 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 725 |  |  |  | 1250A | 1250A | 1600A | 725 |  |  |  | 750A (i.e. 0.6xIn) | 750A (i.e. 0.6xIn) | 800A (i.e. 0.5xIn) | 725 |  |  |  | 8s | 8s | 8s | 725 |  |  |  | 3000A (i.e. 4xIr) | 3000A (i.e. 4xIr) | 4000A (i.e. 5xIr) | 725 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 725 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 725 |  |  |  | N/A | N/A | 1200A (i.e. J) | 725 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 750.1 | [6 empty] | 750.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 750.1 |  |  |  | 1250A | 1250A | 1600A | 750.1 |  |  |  | 875A (i.e. 0.7xIn) | 875A (i.e. 0.7xIn) | 800A (i.e. 0.5xIn) | 750.1 |  |  |  | 8s | 8s | 8s | 750.1 |  |  |  | 3500A (i.e. 4xIr) | 3500A (i.e. 4xIr) | 4000A (i.e. 5xIr) | 750.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 750.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 750.1 |  |  |  | N/A | N/A | 1200A (i.e. J) | 750.1 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 800.1 | [6 empty] | 800.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 800.1 |  |  |  | 1250A | 1250A | 1600A | 800.1 |  |  |  | 875A (i.e. 0.7xIn) | 875A (i.e. 0.7xIn) | 960A (i.e. 0.6xIn) | 800.1 |  |  |  | 8s | 8s | 8s | 800.1 |  |  |  | 3500A (i.e. 4xIr) | 3500A (i.e. 4xIr) | 3840A (i.e. 4xIr) | 800.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 800.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 800.1 |  |  |  | N/A | N/A | 1200A (i.e. J) | 800.1 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 875.1 | [6 empty] | 875.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 875.1 |  |  |  | 1250A | 1250A | 1600A | 875.1 |  |  |  | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 960A (i.e. 0.6xIn) | 875.1 |  |  |  | 8s | 8s | 8s | 875.1 |  |  |  | 3000A (i.e. 3xIr) | 3000A (i.e. 3xIr) | 3840A (i.e. 4xIr) | 875.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 875.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 875.1 |  |  |  | N/A | N/A | 1200A (i.e. J) | 875.1 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 960.1 | [6 empty] | 960.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 960.1 |  |  |  | 1250A | 1250A | 1600A | 960.1 |  |  |  | 1000A (i.e. 0.8xIn) | 1000A (i.e. 0.8xIn) | 1120A (i.e. 0.7xIn) | 960.1 |  |  |  | 8s | 8s | 8s | 960.1 |  |  |  | 3000A (i.e. 3xIr) | 3000A (i.e. 3xIr) | 3360A (i.e. 3xIr) | 960.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 960.1 |  |  |  | 7500A (i.e. 6xIn) | 7500A (i.e. 6xIn) | 9600A (i.e. 6xIn) | 960.1 |  |  |  | N/A | N/A | 1200A (i.e. J) | 960.1 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 1000.1 | [6 empty] | 1000.1 |  |  |  | Micrologic 5.0 | Micrologic 5.0 | Micrologic 6.0 | 1000.1 |  |  |  | 1250A | 1250A | 1600A | 1000.1 |  |  |  | 1125A (i.e. 0.9xIn) | 1125A (i.e. 0.9xIn) | 1120A (i.e. 0.7xIn) | 1000.1 |  |  |  | 8s | 8s | 8s | 1000.1 |  |  |  | 3375A (i.e. 3xIr) | 3375A (i.e. 3xIr) | 3360A (i.e. 3xIr) | 1000.1 |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 0.1s, IxIxt on | 1000.1 |  |  |  | 7500A (i.e. 6xIn) | 5000A (i.e. 4xIn) | 9600A (i.e. 6xIn) | 1000.1 |  |  |  | N/A | N/A | 1200A (i.e. J) | 1000.1 |  |  |  | N/A | N/A | 0.4s, Ixixt off
[12 empty] | 1087 | [6 empty] | 1087 |  |  |  |  | Micrologic 5.0 | Micrologic 6.0 | 1087 |  |  |  |  | 1250A | 1600A | 1087 |  |  |  |  | 1125A (i.e. 0.9xIn) | 1120A (i.e. 0.7xIn) | 1087 |  |  |  |  | 8s | 8s | 1087 |  |  |  |  | 3375A (i.e. 3xIr) | 3360A (i.e. 3xIr) | 1087 |  |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 1087 |  |  |  |  | 5000A (i.e. 4xIn) | 9600A (i.e. 6xIn) | 1087 |  |  |  |  | N/A | 1200A (i.e. J) | 1087 |  |  |  |  | N/A | 0.4s, Ixixt off
[12 empty] | 1120.1 | [6 empty] | 1120.1 |  |  |  |  | Micrologic 5.0 | Micrologic 6.0 | 1120.1 |  |  |  |  | 1250A | 1600A | 1120.1 |  |  |  |  | 1125A (i.e. 0.9xIn) | 1280A (i.e. 0.8xIn) | 1120.1 |  |  |  |  | 8s | 8s | 1120.1 |  |  |  |  | 3375A (i.e. 3xIr) | 3840A (i.e. 3xIr) | 1120.1 |  |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 1120.1 |  |  |  |  | 5000A (i.e. 4xIn) | 9600A (i.e. 6xIn) | 1120.1 |  |  |  |  | N/A | 1200A (i.e. J) | 1120.1 |  |  |  |  | N/A | 0.4s, Ixixt off
[12 empty] | 1125.1 | [6 empty] | 1125.1 |  |  |  |  | Micrologic 5.0 | Micrologic 6.0 | 1125.1 |  |  |  |  | 1250A | 1600A | 1125.1 |  |  |  |  | 1188A (i.e. 0.95xIn) | 1280A (i.e. 0.8xIn) | 1125.1 |  |  |  |  | 8s | 8s | 1125.1 |  |  |  |  | 2967A (i.e. 2.5xIr) | 3840A (i.e. 3xIr) | 1125.1 |  |  |  |  | 0.1s, IxIxt on | 0.1s, IxIxt on | 1125.1 |  |  |  |  | 5000A (i.e. 4xIn) | 9600A (i.e. 6xIn) | 1125.1 |  |  |  |  | N/A | 1200A (i.e. J) | 1125.1 |  |  |  |  | N/A | 0.4s, Ixixt off
[12 empty] | 1160 | [6 empty] | 1160 | [5 empty] | Micrologic 6.0 | 1160 | [5 empty] | 1600A | 1160 | [5 empty] | 1280A (i.e. 0.8xIn) | 1160 | [5 empty] | 8s | 1160 | [5 empty] | 3840A (i.e. 3xIr) | 1160 | [5 empty] | 0.1s, IxIxt on | 1160 | [5 empty] | 9600A (i.e. 6xIn) | 1160 | [5 empty] | 1200A (i.e. J) | 1160 | [5 empty] | 0.4s, Ixixt off
[12 empty] | 1280.1 | [6 empty] | 1280.1 | [5 empty] | Micrologic 6.0 | 1280.1 | [5 empty] | 1600A | 1280.1 | [5 empty] | 1440A (i.e. 0.9xIn) | 1280.1 | [5 empty] | 8s | 1280.1 | [5 empty] | 3600A (i.e. 2.5xIr) | 1280.1 | [5 empty] | 0.1s, IxIxt on | 1280.1 | [5 empty] | 6400A (i.e. 4xIn) | 1280.1 | [5 empty] | 1200A (i.e. J) | 1280.1 | [5 empty] | 0.4s, Ixixt off
[12 empty] | 1440.1 | [6 empty] | 1440.1 | [5 empty] | Micrologic 6.0 | 1440.1 | [5 empty] | 1600A | 1440.1 | [5 empty] | 1520A (i.e. 0.95xIn) | 1440.1 | [5 empty] | 8s | 1440.1 | [5 empty] | 3800A (i.e. 2.5xIr) | 1440.1 | [5 empty] | 0.1s, IxIxt on | 1440.1 | [5 empty] | 6400A (i.e. 4xIn) | 1440.1 | [5 empty] | 1200A (i.e. J) | 1440.1 | [5 empty] | 0.4s, Ixixt off
[12 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450 | [6 empty] | 1450
[12 empty] | 2 | [6 empty] | 3 | [6 empty] | 4 | [6 empty] | 5 | [6 empty] | 6 | [6 empty] | 7 | [6 empty] | 8 | [6 empty] | 9 | [6 empty] | 10 | [6 empty] | 11