## Allocation Summary
WPD Method | [5 empty] | Index
Catergory | % by network tier
| LV | LV/HV | HV | EHV | Unallocated
Opex and transmission exit charges | 41.43% | 8.35% | 28.91% | 21.32%
Depriciation | 18.56% | 8.684% | 35.03% | 37.72%
Return | 18.56% | 8.684% | 35.03% | 37.72%
Weighted Average | 26.53% | 8.568% | 32.9% | 32%
Weighted Average (after incentive and pencsion deficit costs removed and weighted by units flowing) | 32.87% | 10.61% | 30.59% | 23.04% | 2.879%
Direct cost % | 50.22% | 74.76% | 73.86% | 71.94% | N/A
| LV | HV/LV | HV | EHV/HV | EHV | 132kV/EHV | 132kV
Weighted by units flowing | 32.87% | 10.61% | 30.59% | 3.765% | 4.822% | 4.451% | 10%
Direct cost % | 50.22% | 74.76% | 73.86% | 71.94% | 71.94% | 71.94% | 71.94%
| LV | HV | 33kV | 132kV
Network length split | 18.44% | 46% | 100% | 100%
Options | DCP071
TRUE
Discount matrix
| Discounts |  |  |  | Network levels provided or bypassed by the DNO |  |  |  | Network levels bypassed by the DNO
Boundary category | LV demand end user | LV Sub demand or LV generation end user | HV demand or LV Sub generation end user | HV generation end user | EHV/HV | EHV | 132kV/EHV | 132kV | EHV/HV | EHV | 132kV/EHV | 132kV
Boundary 0000 | 97.12% | 95.71% | 94.91% | 88.89% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boundary 132kV | 89.92% | 84.99% | 82.17% | 61.13% | 0 | 0 | 0 | 0.71937 | 0 | 0 | 0 | 0
Boundary 132kV/EHV | 82.67% | 74.18% | 69.33% | 33.13% | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
Boundary EHV | 79.2% | 69.01% | 63.19% | 19.75% | 0 | 0.71937 | 1 | 1 | 0 | 0 | 0 | 0
Boundary HVplus | 74.08% | 61.39% | 54.13% | 0% | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Not used
Input data reconciliation check
Compare results to current CDCM Method M with DCP096
| No discount | LDNO LV: LV user | LDNO HV: LV user | LDNO HV: LV sub user | LDNO HV: HV user
LDNO discount using data in this model |  | 29.83% | 63.68% | 45.9% | 35.74%

## WPD - Final Allocation
Step 1. Format price control allowed revenue data
Index
|  | I) DPCR3 type presentation | [9 empty] | ii) DPCR4 type presentation
|  |  |  | 2005/06 | 2006/07 |  | 2007/08 | 2008/09 | 2009/10 | [5 empty] | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
[12 empty] | Opening asset value |  |  | 573.6 | 577.8 | 579.3 | 578.4 | 575
|  | Allowed revenue |  | 140.7046 | 142.5337 |  | 144.3629 | 145.9107 | 147.7398 |  |  | Total capex |  |  | 49.9 | 49.7 | 49.7 | 49.7 | 49.7
[12 empty] | Depreciation |  |  | -45.7 | -48.2 | -50.6 | -53.1 | -55.6
|  | Opex (incl pensions after 57.7% capitalized) |  | 47.23 | 48.6877 |  | 49.4146 | 49.0992 | 48.7415 |  |  | Closing asset value |  |  | 577.8 | 579.3 | 578.4 | 575 | 569.1
|  | Quality Reward |  | 1.6 | 1.6 | 1.6 | 1.6 | 1.3 | 1.3 |  |  | Present value of opening/closing RAV |  |  | 0 |  |  |  | 434.5105
|  | DPCR3 costs |  | 0.9 | [7 empty] | 5 year movement in closing RAV | [6 empty] | 139.0895
|  | Total Opex |  | 49.73 | 50.2877 |  | 51.0146 | 50.3992 | 50.0415
[12 empty] | Operating costs (excl pensions) |  |  | 43 | 44.5 | 45.1 | 44.7 | 44.3
|  | Capital elements | [9 empty] | Capex (excl pensions) |  |  | 44.1 | 44 | 43.8 | 43.7 | 43.6
|  | Depreciation |  | 45.7 | 48.2 |  | 50.6 | 53.1 | 55.6 |  |  | Pensions |  |  | 10 | 9.9 | 10.2 | 10.4 | 10.5
|  | Tax allowance |  | 13.1 | 14.2 |  | 15 | 15.9 | 16.7 |  |  | Tax allowance |  |  | 13.1 | 14.2 | 15 | 15.9 | 16.7
|  | Capital incentive |  | -1.7 | -1.1 |  | -0.9 | -0.3 | -0.1 |  |  | Capex incentive |  |  | -1.7 | -1.1 | -0.9 | -0.3 | -0.1
|  | Sliding scale |  | 1.2 | 1.2 |  | 1.2 | 1.2 | 1.1 |  |  | Sliding scale addn income |  |  | 1.2 | 1.2 | 1.2 | 1.2 | 1.1
|  | Return |  | 32.6746 | 29.746 |  | 27.4483 | 25.6115 | 24.3983 |  |  | Quality reward/Opex incentive & Other Adjustments |  |  | 1.6 | 1.6 | 1.6 | 1.3 | 1.3
|  | Total capital |  | 90.9746 | 92.246 |  | 93.3483 | 95.5115 | 97.6983 |  |  | DPCR3 costs |  |  | 0.9 | 0 | 0 | 0 | 0
|  | Total capital ex depreciation |  | 45.2746 | 44.046 |  | 42.7483 | 42.4115 | 42.0983 |  |  | Total allowed items |  |  | 112.2 | 114.3 | 116 | 116.9 | 117.4
[12 empty] | PV of allowed items |  |  | 109.2129 | 105.4119 | 101.3594 | 96.7793 | 92.0871
|  | Allocation of allowed revenue to:- | [9 empty] | 5 year movement in closing RAV | [6 empty] | 139.0895
[12 empty] | TOTAL PV OVER 5 YEARS | [6 empty] | 643.9401
|  | Opex |  | 49.73 | 50.2877 |  | 51.0146 | 50.3992 | 50.0415
|  | Depreciation |  | 45.7 | 48.2 |  | 50.6 | 53.1 | 55.6 |  |  | 5.545% |  |  | 0.94746 | 0.89769 | 0.85052 | 0.80584 | 0.7635
|  | Return |  | 32.6746 | 29.746 |  | 27.4483 | 25.6115 | 24.3983 | [5 empty] | 1 | 0.94746 | 0.89769 | 0.85052 | 0.80584
[15 empty] | 0.97338 | 0.92224 | 0.87379 | 0.82788 | 0.78439
[12 empty] | Revenue index |  |  | 1 | 1.013 | 1.026 | 1.037 | 1.05
[12 empty] | Discounted revenue index |  |  | 0.97338 | 0.93423 | 0.89651 | 0.85851 | 0.82361
[12 empty] | Price control revenue |  |  | 140.7046 | 142.5337 | 144.3629 | 145.9107 | 147.7398
[12 empty] | Excluded services revenue |  |  | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
[12 empty] | Total revenue |  |  | 143.6046 | 145.4337 | 147.2629 | 148.8107 | 150.6398
[12 empty] | PV of total revenue |  |  | 139.7814 | 134.1247 | 128.6765 | 123.1976 | 118.1599
[12 empty] | TOTAL PV OVER 5 YEARS | [6 empty] | 643.9401
[12 empty] | PV of excluded service revenue |  | 12.7069 | 2.8228 | 2.6745 | 2.534 | 2.4009 | 2.2747
Step 2. Allocate price control revenues to network tiers
|  | Hence DPCR4 revenue made up of | Total DPCR4 | Basis of allocation | % used | [5 empty] | £m
[5 empty] | EHV |  | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV
|  | Return | 216.5787 | Net Capex | 37.72% |  | 35.03% | 8.684% | 18.56% |  | 81.6999 | 75.8767 | 18.8074 | 40.1947
|  | Depreciation | 253.2 | Net Capex | 37.72% |  | 35.03% | 8.684% | 18.56% |  | 95.5145 | 88.7067 | 21.9876 | 46.9912
|  | Operating costs | 251.473 | Overall Opex split | 21.32% |  | 28.91% | 8.35% | 41.43% |  | 53.6026 | 72.6888 | 20.9987 | 104.183
|  | Total | 721.2517 | [7 empty] | 230.817 | 237.2721 | 61.7936 | 191.3689
[11 empty] | 32% | 32.9% | 8.568% | 26.53%
[5 empty] | 5 |  | 4 | 3 | 2
NET CAPEX SPLIT FROM "CALC -NET CAPEX" SHEET
OVERALL OPEX SPLIT FROM "CALC WPD OPEX ALLOCATYION" SHEET
Step 3. Remove incentive reveune and pension deficit payment from allocations
2007/08 allowed revenue source from page "summary allowed revenue"
| Base revenue |  |  |  |  | 164.619 | 94.43% | [10 empty] | £m
| Allowed pass through items |  |  |  |  | -0.912 | -0.5231%
| Incentive revenue |  |  |  |  | 2.5029 | 1.436% |  |  | Total allowed income | [7 empty] | 174.3332 | From 2007/08 revenue summary
| Under/over revoery |  |  |  |  | 2.5333 | 1.453%
| Excluded |  |  |  |  | 5.59 | 3.207% |  |  | Less incentive revenue ? |  |  |  |  | y |  |  | -2.5029 | From 2007/08 revenue summary
| Total |  |  |  |  | 174.3332 | 100% |  |  | Less Pension deficit payment ? |  |  |  |  | n |  |  | 0 | From SEPD method A spreadsheet
[10 empty] | Less transmission exit charges ? |  |  |  |  | y |  |  | -4.2
| Input pension deficit payment |  |  |  |  | 0 | From SEPD method A spreadsheet
[10 empty] | Total revenue to share | [7 empty] | 167.6303
|  |  |  | Step 3.a. Split out pension deficit and incentive payments | [7 empty] | Step 2.b. Divide cost by units flowing - effectively adjust the cost because of electricity lost as it flows thorugh the network meaning that there is more cost in the lower tiers
HENCE SPLIT OF TARIFFS
|  |  |  | £m | [7 empty] | p/kWh
|  |  |  | Total |  | EHV | HV | HV/LV | LV | Not to be split |  | EHV | HV | HV/LV | LV | Not to be split |  | Total
| Income |  |  | 174.3332 |  | 53.6455 | 55.1458 | 14.3618 | 44.4772 | 6.7029 |  | 0.43204 | 0.57363 | 0.19902 | 0.61635 | 0.053983
| All LV Tariffs | [10 empty] | 0.43204 | 0.57363 | 0.19902 | 0.61635 | 0.053983 |  | 1.875
HV Tariffs
EHV Tariffs
| All LV Tariffs | [10 empty] | 23.04% | 30.59% | 10.61% | 32.87% | 2.879% |  | 100%
HV Tariffs
EHV Tariffs

## Calc - WPD Opex Allocation
Index
|  |  | Step 1 - extract total activity costs from cost report | [5 empty] | Step 2. Idnetify costs inlcuded in price control revenues to be allocated by MEAV | [5 empty] | Step 3. Allocate costs not directly atttibutable to network teirs to network tiers using MEAV |  |  |  |  | Step 4. Sum directly atttibuted and allocated costs | [5 empty] | Step 5. Divide cost by units flowing - effectively adjust the cost because of electricity lost as it flows thorugh the network meaning that there is more cost in the lower tiers |  |  |  | Step 6. Adjust costs so that they are aligned with the definition of opex in the allowed price control revenues
|  |  |  | Costs extracted from RRP Tables |  |  |  |  | Cost drivers - lookup from "Calc-Drivers" | [5 empty] | Allocation of "Unallocated" costs by cost driver to network tiers |  |  |  |  | Sum of allocated and "unallocted" costs | [5 empty] | Sum of allocated and "unallocted" costs expressed per unit throughput (p/kWh) |  |  |  | Propportion of costs allocated to Opex and Capex |  |  |  | Operating costs = sum of allocated and unallocated multplied by 1 minus capitalised proprtion |  |  |  |  | Opex only on p/kWh throughput
|  |  | Total activity cost - from RRP 1.3 | Costs allocated to netwrok tiers in RRP - from 2.2 amd 2.3 |  |  |  | Unallocated costs = Total - costs allocated to network tiers | Insert name of cost driver | Proportion of cost allocated to each network tier | [19 empty] | % Cost capitalised (from DCPR settlement - same for all DNOs) | Capex | Opex |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV
|  |  |  | EHV | HV | HV/LV | LV |  |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV |  | EHV | HV | HV/LV | LV |  |  | EHV | HV | HV/LV | LV
Cash typical costs (excluding disallowed related party margins) | Direct activities - From RRP 2.2 Detailed Cost Matrix | Load related new connections & reinforcement (net of contributions) | -0.5 | 4.7 | 3.8 | 0 | -9 | 0 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0 | 0 | 0 | 0 |  | 4.7 | 3.8 | 0 | -9 |  |  | 0.037852 | 0.039528 | 0 | -0.12472 | 100% | -0.5 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | Non-load new & replacement assets (net of contributions) | 32.3 | 8.5 | 14.3 | 4.2 | 5.2 | 0.1 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.022063 | 0.027826 | 0.0068103 | 0.0433 |  | 8.5221 | 14.3278 | 4.2068 | 5.2433 |  |  | 0.068634 | 0.14904 | 0.058297 | 0.07266 | 100% | 32.3 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | Non-operational capex | 3 | 0 | 0 | 0 | 0 | 3 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.6619 | 0.83479 | 0.20431 | 1.299 |  | 0.6619 | 0.83479 | 0.20431 | 1.299 |  |  | 0.0053308 | 0.0086835 | 0.0028312 | 0.018001 | 23.5% | 0.705 | 2.295 |  | 0.50635 | 0.63861 | 0.1563 | 0.99374 |  | 0.004078 | 0.0066429 | 0.0021659 | 0.013771
|  | Faults | 8.3 | 0.6 | 2.3 | 0.2 | 4.9 | 0.3 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.06619 | 0.083479 | 0.020431 | 0.1299 |  | 0.66619 | 2.3835 | 0.22043 | 5.0299 |  |  | 0.0053653 | 0.024793 | 0.0030547 | 0.069703 | 23.5% | 1.9505 | 6.3495 |  | 0.50964 | 1.8234 | 0.16863 | 3.8479 |  | 0.0041044 | 0.018967 | 0.0023368 | 0.053323
|  | Inspections, & Maintenance | 5.5 | 2.3 | 0.6 | 1.6 | 0.7 | 0.3 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.06619 | 0.083479 | 0.020431 | 0.1299 |  | 2.3662 | 0.68348 | 1.6204 | 0.8299 |  |  | 0.019057 | 0.0071096 | 0.022455 | 0.011501 | 23.5% | 1.2925 | 4.2075 |  | 1.8101 | 0.52286 | 1.2396 | 0.63487 |  | 0.014578 | 0.0054389 | 0.017178 | 0.0087979
|  | Tree Cutting | 4.1 | 0.62978 | 2.3631 | 0 | 1.1655 | -0.058365 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | -0.012877 | -0.016241 | -0.0039748 | -0.025272 |  | 0.6169 | 2.3468 | -0.0039748 | 1.1402 |  |  | 0.0049683 | 0.024412 | -5.5081e-05 | 0.015801 | 23.5% | 0.9635 | 3.1365 |  | 0.47193 | 1.7953 | -0.0030407 | 0.87229 |  | 0.0038008 | 0.018675 | -4.2137e-05 | 0.012088
| Indirect activities - From RRP 2.2 Detailed Cost Matrix | Network Policy | 0.6 | 0 | 0 | 0 | 0 | 0.6 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.13238 | 0.16696 | 0.040862 | 0.2598 |  | 0.13238 | 0.16696 | 0.040862 | 0.2598 |  |  | 0.0010662 | 0.0017367 | 0.00056625 | 0.0036002 | 52.57% | 0.31542 | 0.28458 |  | 0.062788 | 0.079188 | 0.019381 | 0.12322 |  | 0.00050568 | 0.00082372 | 0.00026857 | 0.0017076
|  | Network Design & Engineering | 3.5 | 0 | 0 | 0 | 0 | 3.5 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.77222 | 0.97392 | 0.23836 | 1.5155 |  | 0.77222 | 0.97392 | 0.23836 | 1.5155 |  |  | 0.0062192 | 0.010131 | 0.0033031 | 0.021001 | 52.57% | 1.8399 | 1.6601 |  | 0.36626 | 0.46193 | 0.11305 | 0.7188 |  | 0.0029498 | 0.004805 | 0.0015667 | 0.009961
|  | Project Management | 2.9 | 0 | 0 | 0 | 0 | 2.9 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.63984 | 0.80696 | 0.1975 | 1.2557 |  | 0.63984 | 0.80696 | 0.1975 | 1.2557 |  |  | 0.0051531 | 0.0083941 | 0.0027369 | 0.017401 | 52.57% | 1.5245 | 1.3755 |  | 0.30348 | 0.38274 | 0.093673 | 0.59558 |  | 0.0024441 | 0.0039813 | 0.0012981 | 0.0082534
|  | Engineering Mgt & Clerical Support | 7.2 | 0 | 0 | 0 | 0 | 7.2 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 1.5886 | 2.0035 | 0.49034 | 3.1176 |  | 1.5886 | 2.0035 | 0.49034 | 3.1176 |  |  | 0.012794 | 0.020841 | 0.006795 | 0.043203 | 52.57% | 3.785 | 3.415 |  | 0.75346 | 0.95025 | 0.23257 | 1.4787 |  | 0.0060681 | 0.0098847 | 0.0032229 | 0.020491
|  | Control Centre | 1.9 | 0 | 0 | 0 | 0 | 1.9 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.4192 | 0.5287 | 0.12939 | 0.8227 |  | 0.4192 | 0.5287 | 0.12939 | 0.8227 |  |  | 0.0033761 | 0.0054996 | 0.0017931 | 0.011401 | 52.57% | 0.99883 | 0.90117 |  | 0.19883 | 0.25076 | 0.061372 | 0.39021 |  | 0.0016013 | 0.0026084 | 0.00085047 | 0.0054074
|  | System Mapping - Cartographical | 1 | 0 | 0 | 0 | 0 | 1 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.22063 | 0.27826 | 0.068103 | 0.433 |  | 0.22063 | 0.27826 | 0.068103 | 0.433 |  |  | 0.0017769 | 0.0028945 | 0.00094374 | 0.0060004 | 52.57% | 0.5257 | 0.4743 |  | 0.10465 | 0.13198 | 0.032301 | 0.20537 |  | 0.00084279 | 0.0013729 | 0.00044762 | 0.002846
|  | Customer Call Centre | 0.7 | 0 | 0 | 0 | 0 | 0.7 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.15444 | 0.19478 | 0.047672 | 0.3031 |  | 0.15444 | 0.19478 | 0.047672 | 0.3031 |  |  | 0.0012438 | 0.0020262 | 0.00066062 | 0.0042003 | 52.57% | 0.36799 | 0.33201 |  | 0.073253 | 0.092386 | 0.022611 | 0.14376 |  | 0.00058995 | 0.00096101 | 0.00031333 | 0.0019922
|  | Stores | 0.9 | 0 | 0 | 0 | 0 | 0.9 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.19857 | 0.25044 | 0.061292 | 0.3897 |  | 0.19857 | 0.25044 | 0.061292 | 0.3897 |  |  | 0.0015992 | 0.0026051 | 0.00084937 | 0.0054004 | 52.57% | 0.47313 | 0.42687 |  | 0.094182 | 0.11878 | 0.029071 | 0.18484 |  | 0.00075851 | 0.0012356 | 0.00040286 | 0.0025614
|  | Vehicles & Transport | 2.7 | 0 | 0 | 0 | 0 | 2.7 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.59571 | 0.75131 | 0.18388 | 1.1691 |  | 0.59571 | 0.75131 | 0.18388 | 1.1691 |  |  | 0.0047977 | 0.0078152 | 0.0025481 | 0.016201 | 52.57% | 1.4194 | 1.2806 |  | 0.28255 | 0.35634 | 0.087213 | 0.55451 |  | 0.0022755 | 0.0037067 | 0.0012086 | 0.0076842
|  | IT & Telecoms | 6.8 | 0 | 0 | 0 | 0 | 6.8 | Do not allocate | [20 empty] | 52.57% | 3.5748 | 3.2252
|  | Property Mgt | 2.1 | 0 | 0 | 0 | 0 | 2.1 | Do not allocate | [20 empty] | 52.57% | 1.104 | 0.99603
|  | HR & Non-operational Training | 0.9 | 0 | 0 | 0 | 0 | 0.9 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.19857 | 0.25044 | 0.061292 | 0.3897 |  | 0.19857 | 0.25044 | 0.061292 | 0.3897 |  |  | 0.0015992 | 0.0026051 | 0.00084937 | 0.0054004 | 52.57% | 0.47313 | 0.42687 |  | 0.094182 | 0.11878 | 0.029071 | 0.18484 |  | 0.00075851 | 0.0012356 | 0.00040286 | 0.0025614
|  | Health & Safety & Operational Training | 1.1 | 0 | 0 | 0 | 0 | 1.1 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.2427 | 0.30609 | 0.074913 | 0.4763 |  | 0.2427 | 0.30609 | 0.074913 | 0.4763 |  |  | 0.0019546 | 0.003184 | 0.0010381 | 0.0066005 | 52.57% | 0.57827 | 0.52173 |  | 0.11511 | 0.14518 | 0.035531 | 0.22591 |  | 0.00092707 | 0.0015102 | 0.00049238 | 0.0031306
|  | Finance & Regulation | 5.8 | 0 | 0 | 0 | 0 | 5.8 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 1.2797 | 1.6139 | 0.39499 | 2.5114 |  | 1.2797 | 1.6139 | 0.39499 | 2.5114 |  |  | 0.010306 | 0.016788 | 0.0054737 | 0.034802 | 52.57% | 3.0491 | 2.7509 |  | 0.60695 | 0.76548 | 0.18735 | 1.1912 |  | 0.0048882 | 0.0079626 | 0.0025962 | 0.016507
|  | CEO etc | 1.8 | 0 | 0 | 0 | 0 | 1.8 | MEAV | 22.06% | 27.83% | 6.81% | 43.3% |  | 0.39714 | 0.50087 | 0.12258 | 0.7794 |  | 0.39714 | 0.50087 | 0.12258 | 0.7794 |  |  | 0.0031985 | 0.0052101 | 0.0016987 | 0.010801 | 52.57% | 0.94626 | 0.85374 |  | 0.18836 | 0.23756 | 0.058142 | 0.36967 |  | 0.001517 | 0.0024712 | 0.00080571 | 0.0051228
Other Costs from full activitty cost allocation |  | Atypical cash costs | 4.3 | 0 | 0 | 0 | 0 | 4.3 | Do not allocate | [20 empty] | 0% | 0 | 4.3
|  | Pension deficit payments | 13.4 | 0 | 0 | 0 | 0 | 13.4 | Do not allocate | [20 empty] | 57.7% | 7.7318 | 5.6682
|  | Metering | 1.8 | 0 | 0 | 0 | 0 | 1.8 | Do not allocate | [20 empty] | 0% | 0 | 1.8
|  | Excluded services & de minimis | 8.9 | 0 | 0 | 0 | 0 | 8.9 | Do not allocate | [20 empty] | 0% | 0 | 8.9
|  | Relevant distributed generation (less contributions) | -0.1 | 0 | 0 | 0 | 0 | -0.1 | Do not allocate | [20 empty] | 0% | 0 | -0.1
|  | IFI | 0.1 | 0 | 0 | 0 | 0 | 0.1 | Do not allocate | [20 empty] | 0% | 0 | 0.1
|  | Disallowed Related Party Margins | -2.7756e-17 | 0 | 0 | 0 | 0 | -2.7756e-17 | Do not allocate | [20 empty] | 0% | 0 | -2.7756e-17
|  | Statutory Depreciation | 25.3 | 0 | 0 | 0 | 0 | 25.3 | Do not allocate | [20 empty] | 0% | 0 | 25.3
|  | Network Rates | 15.1 | 0 | 0 | 0 | 0 | 15.1 | Do not allocate | [20 empty] | 0% | 0 | 15.1
|  | Transmission Exit Charges | 4.2 | 0 | 0 | 0 | 0 | 4.2 | Do not allocate | [20 empty] | 0% | 0 | 4.2
|  | Pension deficit repair payments by related parties (note 2) | 0 | 0 | 0 | 0 | 0 | 0 | Do not allocate | [20 empty] | 0% | 0 | 0
|  | Non activity costs and reconciling amounts (note 3) | -2.9 | 0 | 0 | 0 | 0 | -2.9 | Do not allocate | [20 empty] | 0% | 0 | -2.9
|  | Total Annual Operating & Capital Expenditure per Regulatory Accounts | 162.7 | 16.7298 | 23.3631 | 6 | 2.9655 | 113.6416 | [5 empty] | Total | 7.6431 | 9.6394 | 2.3592 | 14.9999 | Total all network tiers | 83.7 |  |  |  |  | Total all network tiers | 0.90439 |  |  |  | Total | 65.4187 | 97.2813 | Total all network tiers | 30.6918 |  |  |  | Total all network tiers | 0.35669
[19 empty] | Total by network tiers | 24.3729 | 33.0025 | 8.3592 | 17.9654 |  | Total by network tiers | 0.19629 | 0.3433 | 0.11584 | 0.24896 |  |  |  | Total by network tiers | 6.5421 | 8.8715 | 2.5628 | 12.7153 | Total by network tiers | 0.052688 | 0.092283 | 0.035515 | 0.17621
[19 empty] | % | 29.12% | 39.43% | 9.987% | 21.46% |  | % | 21.7% | 37.96% | 12.81% | 27.53% |  |  |  | % | 21.32% | 28.91% | 8.35% | 41.43% | % | 14.77% | 25.87% | 9.957% | 49.4%
[10 empty] | 5 | 4 | 3 | 2 | [20 empty] | THESE % ARE USED TO ALLOCATE PRICE CONTROL OPEX
Step 4.a. calculate proportion of cost classified as direct costs
[19 empty] | Total direct+other | 17.5332 | 24.3764 | 6.252 | 13.5424 | Max of zero or total from each catergory
[19 empty] | Total indirect | 6.8396 | 8.6261 | 2.1112 | 13.4231 | Max of zero or total from each catergory
[19 empty] | % direct+other | 71.94% | 73.86% | 74.76% | 50.22%
[19 empty] | % indirect | 28.06% | 26.14% | 25.24% | 49.78%

## Calc-Units
103. Units distributed (GWh) from RRP table 5.1 |  |  | Index
Units distributed (GWh) from RRP table 5.1
Units distributed at LV | 7216.2042
Units distributed at HV | 2482.1084
Units distributed at EHV+ | 2954.8379
Losses | 675.237
104. Estimated line loss adjustment factors relative to LV
| LV services | LV | HV | EHV | 132kV
Units distributed at LV | 1 | 1 | 1 | 1 | 1
Units distributed at HV | 0 | 0 | 0.9658 | 0.9658 | 0.9658
Units distributed at EHV+ | 0 | 0 | 0 | 0.9487 | 0.9487
| LV services | LV | HV | EHV | 132kV
Units (GWh) flowing through each level, loss-adjusted to LV | 7216.2042 | 7216.2042 | 9613.4186 | 12416.6629 | 12416.6629
Units (kWh) flowing through each level, loss-adjusted to LV | 7216204194.5 | 7216204194.5 | 9613418584.5808 | 12416662877.4644 | 12416662877.4644

## Calc-Drivers
Drivers - LV, HV, EHV split | [5 empty] | Index
| Catergory | LV | HV | EHV | Source
| Net Capex | 18.56% | 43.72% | 37.72% | FBPQ capex - see "Calc Net capex"
| Customers | 100% | 0% | 0% | Assumption
| Network Length | 40.07% | 50.56% | 9.364% | RRP table 5.1
| Substations | 0% | 99.31% | 0.687% | RRP table 5.1
| Tranmission Exit Charges | 0% | 0% | 100% | Assumption
| MEAV | 43.3% | 34.64% | 22.06% | FBPQ capex - see "Calc MEAV"
| EHV only | 0% | 0% | 100% | Assumption
| LV only | 100% | 0% | 0% | Assumption
| HV only | 0% | 100% | 0% | Assumption
Drivers - LV, LV/HV, HV, EHV split
| Catergory | LV | LV/HV | HV | EHV | Source
| Net Capex | 18.56% | 8.684% | 35.03% | 37.72% | FBPQ capex - see "Calc Net capex"
| No Cutomers | 100% | 0% | 0% | 0% | Assumption
| Network Length | 40.07% | 0% | 50.56% | 9.364% | RRP table 5.1
| No. Substations | 0% | 0% | 99.31% | 0.687% | RRP table 5.1
| Tranmission Exit Charges | 0% | 0% | 0% | 100% | Assumption
| MEAV | 43.3% | 6.81% | 27.83% | 22.06% | FBPQ capex - see "Calc MEAV"
| MEAV excl services | 32.45% | 10.53% | 30.74% | 26.29% | FBPQ capex - see "Calc MEAV"
| MEAV excl services and 50% LV network | 0% | 0% | % of Total | 31.93% | FBPQ capex - see "Calc MEAV"
| EHV only | 0% | 0% | 0% | 100% | Assumption
| LV only | 100% | 0% | 0% | 0% | Assumption
| HV only | 0% | 0% | 100% | 0% | Assumption

## Calc-MEAV
MEAV by Voltage Level |  |  |  |  | Index
| MEAV - LV, HV, EHV, 132kV split |  |  |  | MEAV - LV, LV/HV, HV, EHV, 132kV split |  |  |  | MEAV - LV (excl. services), LV/HV, HV, EHV, 132kV split |  |  |  |  | MEAV - LV (excl. services + 50%LV), LV/HV, HV, EHV, 132kV split
| Sum of MEAV of asset classified in voltage tier (as calculated below) |  |  |  | Sum of MEAV of asset classified in voltage tier |  |  |  | Sum of MEAV of asset classified in voltage tier (as calculated below) |  |  |  |  | Sum of MEAV of asset classified in voltage tier (as calculated below)
|  | £m | % of Total |  |  | £m | % of Total |  |  | £m | % of Total |  |  |  | £m | % of Total
| LV | 1763568.7248 | 43.3% |  | LV | 1763568.7248 | 43.3% |  | LV | 1109148.0648 | 32.45% |  |  | LV | 554574.0324 | 19.36%
| HV | 1410703.782 | 34.64% |  | LV/HV | 277374.22 | 6.81% |  | LV/HV | 359933.93 | 10.53% |  |  | LV/HV | 359933.93 | 12.57%
| EHV | 323753.8937 | 7.949% |  | HV | 1133329.562 | 27.83% |  | HV | 1050769.852 | 30.74% |  |  | HV | 1050769.852 | 36.69%
| 132 kV | 574863.35 | 14.11% | Check | EHV | 323753.8937 | 7.949% |  | EHV | 323753.8937 | 9.471% |  |  | EHV | 323753.8937 | 11.3%
| Total | 4072889.7505 | 100% | OK | 132 kV | 574863.35 | 14.11% | Check | 132 kV | 574863.35 | 16.82% | Check |  | 132 kV | 574863.35 | 20.07% | Check
[5 empty] | Total | 4072889.7505 | 100% | OK | Total | 3418469.0905 | 100% | OK |  | Total | 2863895.0581 | 100% | OK
MEAV Calculation = Replacement unit cost*FBPQ closing asset balance
|  | Asset categories | Units | DNO reported Unit Cost (£) |  | Unit cost used in MEAV calculation (£) | Closing DCPR asset Balance (units) | MEAV (£)
|  |  |  | Sum of direct and indriect replacement unit cost from FBPQ C2 | PB power numbers, if available | Is DNO Unit cost if avaliable, otherwise PB power unit cost | Closing asset balannce from FBPQ V4 | Unit cost used in MEAV calculation*Closing DCPR asset Balance (units) | Classification
LV Network | [10 empty] | LV | 1763568.7248 | 43.3%
| Overhead lines | [7 empty] | LV |  | HV/LV | 277374.22 | 6.81%
|  | LV Main (OHL) | km | 19.99 | DATA | 19.99 | 3192 | 63808.08 | LV |  | HV | 1051814.732 | 25.82%
|  | LV Service (OHL) | Each | 0.32 | DATA | 0.32 | 317000 | 101440 | LV |  | EHV/HV | 160146.74 | 3.932%
[6 empty] | 0 |  |  | LV |  | EHV | 205131.4537 | 5.037%
| Overhead lines - Support |  |  |  |  | 0 |  |  | LV |  | 132kV/EHV | 189323.98 | 4.648%
|  | LV Support | Each | 1.92 | DATA | 1.92 | 97546 | 187288.32 | LV |  | 132kV | 425529.9 | 10.45%
[6 empty] | 0 |  |  | LV |  | All | 4072889.7505 | 100%
| Underground cables |  |  |  |  | 0 |  |  | LV
|  | LV Main (UG Consac) | km |  | DATA |  | 0 |  | LV
|  | LV Main (UG Plastic) | km | 67.22 | DATA | 67.22 | 4772.09 | 320779.8898 | LV |  | EHV/HV | 160146.74 | 16.34%
|  | LV Main (UG Paper) | km | 75.91 | DATA | 75.91 | 6194.5 | 470224.495 | LV |  | EHV | 205131.4537 | 20.93%
|  | LV Service (UG) | Each | 0.71 | DATA | 0.71 | 778846 | 552980.66 | LV |  | 132kV/EHV | 189323.98 | 19.32%
[6 empty] | 0 |  |  | LV |  | 132kV | 425529.9 | 43.42%
| Switchgear |  |  |  |  | 0 |  |  | LV |  | All EHV | 980132.0737 | 100%
|  | LV Pillar (ID) | Each | 8.06 | DATA | 8.06 | 4081 | 32892.86 | LV
|  | LV Pillar (OD) | Each | 8.47 | DATA | 8.47 | 3785 | 32058.95 | LV
|  | LV Board (WM) | Each | 10.53 | DATA | 10.53 | 199 | 2095.47 | LV
|  | LV UGB | Each |  | DATA | DATA | 3645 |  | LV
|  | LV Fuses (PM) | Each |  | DATA | DATA | 31376 |  | LV
|  | LV Fuses (TM) | Each |  | DATA | DATA | 2653 |  | LV
[6 empty] | 0 |  |  | LV
HV network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV OHL (Open) | km | 20.82 | DATA | 20.82 | 12207 | 254149.74 | HV
|  | 6.6/11 kV OHL (Covered) | km |  | DATA |  | 0 |  | HV
|  | 20 kV OHL (Open) | km |  | DATA |  | 0 |  | HV
|  | 20 kV OHL (Covered) | km |  | DATA |  | 0 |  | HV
[6 empty] | 0 |  |  | HV
| Overhead lines - Support |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV Support | Each | 2.05 | DATA | 2.05 | 162533 | 333192.65 | HV
|  | 20 kV Support | Each |  | DATA |  | 0 |  | HV
[5 empty] | DATA | DATA |  |  | HV
| Underground cables (kms) |  |  |  |  | 0 |  |  | HV
|  | 6.6/11kV UG Cable | km | 84.36 | DATA | 84.36 | 5461.7 | 460749.012 | HV
|  | 20kV UG Cable | km |  | DATA |  | 0 |  | HV
[6 empty] | 0 |  |  | HV
| Submarine cables (kms) |  |  |  |  | 0 |  |  | HV
|  | HV Sub Cable | km | 535.69 | DATA | 535.69 | 5 | 2678.45 | HV
[5 empty] | DATA | DATA |  |  | HV
| Switchgear |  |  |  |  | 0 |  |  | HV
|  | 6.6/11 kV CB (PM) | Each | 8.31 | DATA | 8.31 | 913 | 7587.03 | EHV/HV
|  | 6.6/11 kV CB (GM) | Each | 24.52 | DATA | 24.52 | 3015 | 73927.8 | EHV/HV
|  | 6.6/11 kV Switch (PM) | Each | 7.06 | DATA | 7.06 | 148 | 1044.88 | HV
|  | 6.6/11 kV Switch (GM) | Each | 10.15 | DATA | 10.15 | 2330 | 23649.5 | HV/LV
|  | 6.6/11 kV RMU | Each | 12.28 | DATA | 12.28 | 7526 | 92419.28 | HV/LV
|  | 6.6/11 kV Switchgear - Other (PM) | Each |  | DATA | DATA | 5702 |  | HV
|  | 6.6/11 kV Switchgear - Other (GM) | Each |  | DATA | DATA | 1 |  | HV
|  | 20 kV CB (PM) | Each |  | DATA |  | 0 |  | EHV/HV
|  | 20 kV CB (GM) | Each |  | DATA |  | 0 |  | EHV/HV
|  | 20 kV Switch (PM) | Each |  | DATA |  | 0 |  | HV
|  | 20 kV Switch (GM) | Each |  | DATA |  | 0 |  | HV/LV
|  | 20 kV RMU | Each |  | DATA |  | 0 |  | HV/LV
|  | 20 kV Switchgear - Other (PM) | Each |  | DATA |  | 0 |  | HV
|  | 20 kV Switchgear - Other (GM) | Each |  | DATA |  | 0 |  | HV
0
| Transformers |  |  |  |  | 0
|  | 6.6/11 kV Transformer (PM) | Each | 1.78 | DATA | 1.78 | 31541 | 56142.98 | HV/LV
|  | 6.6/11 kV Transformer (GM) | Each | 12.82 | DATA | 12.82 | 8203 | 105162.46 | HV/LV
|  | 20 kV Transformer (PM) | Each |  | DATA |  | 0 |  | HV/LV
|  | 20 kV Transformer (GM) | Each |  | DATA |  | 0 |  | HV/LV
0
EHV Network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0
|  | 33kV OHL (Pole Line) | km | 26.88 | DATA | 26.88 | 1186 | 31879.68 | EHV
|  | 33kV OHL (Tower Line) | km | 33.67 | DATA | 33.67 | 41 | 1380.47 | EHV
|  | 66kV OHL (Pole Line) | km | 41.55 | DATA | 41.55 | 329 | 13669.95 | EHV
|  | 66kV OHL (Tower Line) | km | 52.49 | DATA | 52.49 | 28 | 1469.72 | EHV
0
| Overhead lines - Support |  |  |  |  | 0
|  | 33kV Pole | Each | 2.61 | DATA | 2.61 | 15324 | 39995.64 | EHV
|  | 33kV Tower | Each | 45.36 | DATA | 45.36 | 190 | 8618.4 | EHV
|  | 66kV Pole | Each | 3.61 | DATA | 3.61 | 4318 | 15587.98 | EHV
|  | 66kV Tower | Each | 74.53 | DATA | 74.53 | 251 | 18707.03 | EHV
0
| Underground cables (kms) |  |  |  |  | 0
|  | 33kV UG Cable (Non Pressurised) | km | 173.04 | DATA | 173.04 | 386.84 | 66938.7936 | EHV
|  | 33kV UG Cable (Oil) | km | 152.89 | DATA | 152.89 | 0 | 0 | EHV
|  | 33kV UG Cable (Gas) | km | 173.42 | DATA | 173.42 | 8.124 | 1408.8641 | EHV
|  | 66kV UG Cable (Non Pressurised) | km | 444.45 | DATA | 444.45 | 6 | 2666.7 | EHV
|  | 66kV UG Cable (Oil) | km | 444.45 | DATA | 444.45 | 2 | 888.9 | EHV
|  | 66kV UG Cable (Gas) | km | 444.45 | DATA | 444.45 | 1 | 444.45 | EHV
0
| Submarine cables (kms) |  |  |  |  | 0
|  | EHV Sub Cable | km | 1134.52 | DATA | 1134.52 | 1.3 | 1474.876 | EHV
0
| Switchgear |  |  |  |  | 0
|  | 33 KV CB (ID) | Each | 66.58 | DATA | 66.58 | 311 | 20706.38 | 132kV/EHV
|  | 33 kV CB (OD) | Each | 51.4 | DATA | 51.4 | 274 | 14083.6 | 132kV/EHV
|  | 33 kV Switch (GM) | Each | 33.17 | DATA | 33.17 | 16 | 530.72 | 132kV/EHV
|  | 33 kV Switch (PM) | Each |  | DATA |  | 0 |  | 132kV/EHV
|  | 33 kV RMU | Each |  | DATA |  | 0 |  | 132kV/EHV
|  | 33 kV Switchgear - Other | Each |  | DATA | DATA | 1074 |  | EHV/HV
|  | 66 KV CB (ID & OD) | Each | 88.11 | DATA | 88.11 | 53 | 4669.83 | 132kV/EHV
|  | 66 KV Switchgear - Other | Each |  | DATA | DATA | 233 |  | EHV/HV
0
| Transformers |  |  |  |  | 0
|  | 33 kV Transformer (PM) | Each |  | DATA |  | 0 |  | EHV/HV
|  | 33 kV Transformer (GM) | Each | 262.73 | DATA | 262.73 | 247 | 64894.31 | EHV/HV
|  | 33 kV AuxiliaryTransfomer | Each |  | DATA | DATA | 244 |  | EHV/HV
|  | 66 kV Transformer | Each | 457.92 | DATA | 457.92 | 30 | 13737.6 | EHV/HV
|  | 66 kV AuxiliaryTransfomer | Each |  | DATA |  | 0 |  | EHV/HV
0
132kV Network | [5 empty] | 0
| Overhead lines |  |  |  |  | 0
|  | 132kV OHL Conductor (Pole Line) | km | 52.85 | DATA | 52.85 | 91 | 4809.35 | 132kV
|  | 132kV OHL Conductor (Tower Line) | km | 53.51 | DATA | 53.51 | 1089 | 58272.39 | 132kV
0
| Overhead lines - Support |  |  |  |  | 0
|  | 132kV Pole | Each | 3.64 | DATA | 3.64 | 835 | 3039.4 | 132kV
|  | 132kV Tower | Each | 98.62 | DATA | 98.62 | 2354 | 232151.48 | 132kV
|  | 132kV Fittings (Tower Line) | Each | 3.8 | DATA | 3.8 | 4708 | 17890.4 | 132kV
0
| Underground cables (kms) |  |  |  |  | 0
|  | 132kV UG Cable (Non Pressurised) | km | 0 | DATA | 0 | 35.4 | 0 | 132kV
|  | 132kV UG Cable (Oil) | km | 1323.44 | DATA | 1323.44 | 58 | 76759.52 | 132kV
|  | 132kV UG Cable (Gas) | km |  | DATA |  | 0 |  | 132kV
0
| Submarine cables (kms) |  |  |  |  | 0
|  | 132 kV Sub Cable | km |  | DATA |  | 0 |  | 132kV
0
| Switchgear |  |  |  |  | 0
|  | 132 kV CB (ID & OD) | Each | 146.88 | DATA | 146.88 | 222 | 32607.36 | 132kV
|  | 132 kV Switchgear (other) | Each |  | DATA | DATA | 727 |  | 132kV
0
| Transformers |  |  |  |  | 0
|  | 132 kV Transformer | Each | 1139.95 | DATA | 1139.95 | 131 | 149333.45 | 132kV/EHV
|  | 132 kV AuxiliaryTransfomer | Each |  | DATA | DATA | 140 |  | 132kV/EHV
0
Tele-control / SCADA | [5 empty] | 0
| Primary substation |  |  |  |  | 0
|  | 132 kV/EHV RTU (PM) | Each |  | DATA | DATA | 1 |  | EHV/HV
|  | 132 kV/EHV RTU (GM) | Each |  | DATA | DATA | 272 |  | EHV/HV
0
| Secondary substation |  |  |  |  | 0
|  | HV RTU (PM) | Each |  | DATA | DATA | 1246 |  | HV/LV
|  | HV RTU (GM) | Each |  | DATA | DATA | 143 |  | HV/LV
0
0
HV network switchgear | [5 empty] | 0
|  | 6.6/11 kV CB (GM) |  |  |  | 0
|  | Primary | Each | 24.52 | DATA | 24.52
|  | Distribution | Each | 24.52 | DATA | 24.52
|  | 20 kV Switch (GM) |  |  | DATA | DATA
|  | Primary | Each |  | DATA | DATA
|  | Distribution | Each |  | DATA | DATA
[7 empty] | Total MEAV | 4072889.7505

## Calc-Net capex
Total Net Capex |  |  |  |  | Index
| Total Net Capex 2005/06 -2014/15 LV, HV, EHV, 132kV split |  |  |  | Total Net Capex 2005/06 -2014/15 LV, LV/HV, HV, EHV, 132kV split
| Sum connecions/reinforcement/replacement capex -see below |  |  |  | Sum connecions/reinforcement/replacement capex -see below
|  | £m | % of Total |  |  | £m | % of Total
| LV | 49.2999 | 18.56% |  | LV | 49.2999 | 18.56%
| HV | 116.1327 | 43.72% |  | LV/HV | 23.0678 | 8.684%
| EHV | 58.0496 | 21.85% |  | HV | 93.0649 | 35.03%
| 132 kV | 42.1576 | 15.87% |  | EHV | 58.0496 | 21.85%
[5 empty] | 132 kV | 42.1576 | 15.87%
Connection/Reinfircement/Replacement Capex LV, HV, EHV, 132kV split
| Connections Capex 2005/06 -2014/15 (£m) |  |  | General reniforcement Capex 2005/06 -2014/15 (£m) |  |  | Fault reniforcement Capex 2005/06 -2014/15 (£m)
| Connections spend minus customer contrbutions (from FBPQ LR1) |  |  | (from FBPQ LR4) |  |  | (from FBPQ LR6)
| LV | 3.1 |  | LV | 1.9 |  | LV | 0
| HV | 1.2 |  | HV | 12.6 |  | HV | 0
| EHV | 1.55 |  | EHV | 17.7 |  | EHV | 0.7
| 132 kV | 0 |  | 132 kV | 9.3 |  | 132 kV | 0
Replacement Capex 2005/06 -2014/15 (£m)
(from FBPQ NL1)
| LV | 44.2999
| HV | 102.3327
| EHV | 38.0996
| 132 kV | 32.8576
Connection/Reinfircement/Replacement Capex LV, LV/HV, HV, EHV, 132kV split
| Connections Capex 2005/06 -2014/15 (£m) |  |  | General reniforcement Capex 2005/06 -2014/15 (£m) |  |  | Fault reniforcement Capex 2005/06 -2014/15 (£m)
| Connections spend minus customer contrbutions (from FBPQ LR1) |  |  | (from FBPQ LR4) |  |  | (from FBPQ LR6)
| LV | 3.1 |  | LV | 1.9 |  | LV | 0
| LV/HV | 0.28725 | allocated in proportion to repex | LV/HV | 3.0161 | allocated in proportion to repex | LV/HV | 0 | allocated in proportion to repex
| HV | 0.91275 |  | HV | 9.5839 |  | HV | 0
| EHV | 1.55 |  | EHV | 17.7 |  | EHV | 0.7
| 132 kV | 0 |  | 132 kV | 9.3 |  | 132 kV | 0
Replacement Capex 2005/06 -2014/15 (£m)
(from FBPQ NL1)
| LV | 44.2999
| LV/HV | 19.7645 | HV/LV sub/trans costs |  | LV/HV/(LV/HV+HV) % | 23.94%
| HV | 82.5682
| EHV | 38.0996
| 132 kV | 32.8576

## Summary of revenue
|  | Summary of Revenue |  |  |  | Index
Allowed Demand Revenue (ADt) |  |  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
|  |  |  | 16 | 17 | 18 | 19 | 20
| Base Demand Revenue (BRt) |  | £m | 155.3 | 158.4622 | 164.619 | 7.5294 | #DIV/0!
| Pass through Items (PTt) |  | £m | 2.4393 | 0.36507 | -0.912 | -17.2673 | -17.2673
| Incentive Revenue (Ipt) |  | £m | 3.0814 | -1.9055 | 2.5029 | 0 | 0
| Correction Factor (KDt) |  | £m | 0.58791 | 1.209 | 4.7732 | 2.5713 | 12.4938
| Allowed Demand Revenue (Adt) |  | £m | 160.2328 | 155.7128 | 161.4367 | -12.3092 | #DIV/0!
| Regulated Demand Revenue (RDt) |  | £m | 161.37 | 160.11 | 163.97 | 0 | 0
| Net Movement on Revenue Provisions |  | £m | 0 | 0 | 0 | 0 | 0
| Over/Under Recovery |  | £m | 1.1372 | 4.3972 | 2.5333 | 12.3092 | #DIV/0!
Allowed Network Generation Revenue (AGt)
| Incentivised Generation (IGt) |  | £m | 0 | 0.015387 | 0.023939 | 0 | 0
| Registered Power Zones (RPZt) |  | £m | 0 | 0 | 0 | 0 | 0
| Correction Factor (KGt) |  | £m | 0 | 0 | -0.005848 | -0.080984 | -0.082199
| Allowed Network Generation Revenue (AGt) |  | £m | 0 | 0.015387 | 0.029787 | 0.080984 | 0.082199
| Network Generation Revenue (RGt) |  | £m | 0 | 0.01 | -0.05 | 0 | 0
| Over/Under Recovery |  | £m | 0 | -0.005387 | -0.079787 | -0.080984 | -0.082199
Metering Revenue
| Legacy Basic Meter Asset Provision Revenue |  | £m | 2.81 | 3.06 | 3.63 | 0 | 0
| Basic Meter Operation Revenue |  | £m | 3.6498 | 4.2581 | 0 | 0 | 0
|  |  |  | 6.4598 | 7.3181 | 3.63 | 0 | 0
Excluded Services and Revenue Outside of Price Control
| Excluded Services |  | £m | 25.34 | 34.46 | 36.6 | 0 | 0
| Revenue Outside of Price Control |  | £m | 4.01 | 4.32 | 4.31 | 0 | 0
| Di-Minimis Revenue |  | £m | 0.14 | 0.87 | 1.28 | 0 | 0
|  |  |  | 29.49 | 39.65 | 42.19 | 0 | 0

## Allowed revenue -DPCR4
|  | 2004/05 | 2005/6 | 2006/7 | 2007/8 | 2008/9 | 2009/10 | Index
|  | (£M) | (£M) | (£M) | (£M) | (£M) | (£M)
1 | Opening asset value |  | 573.6 | 577.8 | 579.3 | 578.4 | 575
2 | Total capex |  | 49.9 | 49.7 | 49.7 | 49.7 | 49.7
3 | Depreciation |  | -45.7 | -48.2 | -50.6 | -53.1 | -55.6
4 | Closing asset value |  | 577.8 | 579.3 | 578.4 | 575 | 569.1
5 | Present value of opening / closing RAV | [5 empty] | 434.5105
6 | 5 Year movement in closing RAV | [5 empty] | 139.0895
ALLOWED ITEMS
7 | Operating costs (excluding pensions) |  | 43 | 44.5 | 45.1 | 44.7 | 44.3
8 | Capital expenditure (excluding pensions) |  | 44.1 | 44 | 43.8 | 43.7 | 43.6
9 | Pensions allowance |  | 10 | 9.9 | 10.2 | 10.4 | 10.5
10 | Tax allowance |  | 13.1 | 14.2 | 15 | 15.9 | 16.7
11 | Capex incentive scheme |  | -1.7 | -1.1 | -0.9 | -0.3 | -0.1
12 | Sliding scale additional income |  | 1.2 | 1.2 | 1.2 | 1.2 | 1.1
13 | Opex incentive / Other adjustments
14 | Quality award |  | 1.6 | 1.6 | 1.6 | 1.3 | 1.3
15 | DPCR3 costs |  | 0.9
16 | Total allowed items |  | 112.2 | 114.3 | 116 | 116.9 | 117.4
17 | Present value of allowed items |  | 109.2129 | 105.4119 | 101.3594 | 96.7793 | 92.0871
18 | 5 year movement in closing RAV | [5 empty] | 139.0895
19 | TOTAL PRESENT VALUE OVER 5 YEARS | [5 empty] | 643.9401
REVENUE
20 | Revenue index |  | 1 | 1.013 | 1.026 | 1.037 | 1.05
21 | Discounted revenue index |  | 0.97338 | 0.93423 | 0.89651 | 0.85851 | 0.82361
22 | Price control revenue | DATA | 140.7046 | 142.5337 | 144.3629 | 145.9107 | 147.7398
23 | Excluded service revenue |  | 2.9 | 2.9 | 2.9 | 2.9 | 2.9
24 | Total revenue |  | 143.6046 | 145.4337 | 147.2629 | 148.8107 | 150.6398
25 | Present value of total revenue |  | 139.7814 | 134.1247 | 128.6765 | 123.1976 | 118.1599
26 | TOTAL PRESENT VALUE OVER 5 YEARS | [5 empty] | 643.9401
Take these data from the February 2005 Ofgem document (link below), not the November 2004 final proposals.
http://www.ofgem.gov.uk/Markets/RetMkts/Metrng/Metering/Documents1/9745-5405.pdf

## FBPQ T4
Main Forecast Business Plan DPCR5 | [5 empty] | Index
T4 - Volume Summary
Total Asset Register Movement
[6 empty] | 2005/06 |  |  |  |  | 2006/07 |  |  |  |  | 2007/08 |  |  |  |  | 2008/09 |  |  |  |  | 2009/10
|  |  |  | Asset categories | Opening Balance DCPR4 | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance | Assets removed |  | Assets Installed |  | Closing Balance DPCR4
[6 empty] | LRE | NLRE | LRE | NLRE | 2005/06 | LRE | NLRE | LRE | NLRE | 2006/07 | LRE | NLRE | LRE | NLRE | 2007/08 | LRE | NLRE | LRE | NLRE | 2008/09 | LRE | NLRE | LRE | NLRE | 2009/10
LV Network
Overhead lines - Conductor
|  |  |  | LV Main (OHL) | 3215 | 0 | 9 | 0 | 4 | 3210 | 0 | 61 | 0 | 56 | 3205 | 0 | 66 | 0 | 54 | 3193 | 0 | 39 | 0 | 39 | 3193 | 0 | 43 | 0 | 42 | 3192
|  |  |  | LV Service (OHL) | 317000 | 0 | 5256 | 0 | 5256 | 317000 | 0 | 5428 | 0 | 5428 | 317000 | 0 | 9048 | 0 | 9048 | 317000 | 0 | 5000 | 0 | 5000 | 317000 | 0 | 2500 | 0 | 2500 | 317000
Overhead lines - Support
|  |  |  | LV Support | 98008 | 0 | 1043 | 0 | 961 | 97926 | 0 | 1028 | 0 | 833 | 97731 | 0 | 900 | 0 | 734 | 97565 | 0 | 840 | 0 | 840 | 97565 | 0 | 845 | 0 | 826 | 97546
Underground cables
|  |  |  | LV Main (UG Consac) | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | LV Main (UG Plastic) | 3999 | 0 | 0 | 248 | 4 | 4251 | 0 | 2 | 134.79 | 9.4 | 4393.19 | 0 | 2 | 143.9 | 2 | 4537.09 | 0 | 0 | 117 | 2 | 4656.09 | 0 | 0 | 113 | 3 | 4772.09
|  |  |  | LV Main (UG Paper) | 6214.9 | 0 | 4 | - | 0 | 6210.9 | 0 | 7.4 | - | 0 | 6203.5 | 0 | 5 | - | 0 | 6198.5 | 0 | 2 | 0 | 0 | 6196.5 | 0 | 2 | 0 | 0 | 6194.5
|  |  |  | LV Service (UG) | 732157 | 0 | 0 | 10675 | 0 | 742832 | 0 | 0 | 11542 | 0 | 754374 | 0 | 0 | 8211 | 0 | 762585 | 0 | 1100 | 8288 | 1100 | 770873 | 0 | 750 | 7973 | 750 | 778846
Switchgear
|  |  |  | LV Pillar (ID) | 3736 | 0 | 0 | 40 | 65 | 3841 | 0 | 22 | 38 | 59 | 3916 | 0 | 53 | 54 | 88 | 4005 | 0 | 0 | 39 | 0 | 4044 | 0 | 0 | 37 | 0 | 4081
|  |  |  | LV Pillar (OD) | 3893 | 21 | 8 | 1 | 8 | 3873 | 23 | 14 | 1 | 13 | 3850 | 29 | 14 | 3 | 14 | 3824 | 22 | 30 | 2 | 30 | 3804 | 21 | 40 | 2 | 40 | 3785
|  |  |  | LV Board (WM) | 215 | 1 | 0 | 0 | 0 | 214 | 11 | 0 | 0 | 0 | 203 | 0 | 0 | 3 | 0 | 206 | 5 | 0 | 1 | 0 | 202 | 4 | 0 | 1 | 0 | 199
|  |  |  | LV UGB | 3635 | 6 | 10 | 14 | 10 | 3643 | 5 | 8 | 11 | 8 | 3649 | 18 | 8 | 13 | 8 | 3644 | 10 | 0 | 10 | 0 | 3644 | 9 | 0 | 10 | 0 | 3645
|  |  |  | LV Fuses (PM) | 31144 | 0 | 511 | 0 | 640 | 31273 | 0 | 0 | 0 | 0 | 31273 | 0 | 0 | 0 | 103 | 31376 | 0 | 0 | 0 | 0 | 31376 | 0 | 0 | 0 | 0 | 31376
|  |  |  | LV Fuses (TM) | 2813 | 20 | 0 | 0 | 0 | 2793 | 36 | 0 | 0 | 0 | 2757 | 41 | 0 | 0 | 0 | 2716 | 32 | 0 | 0 | 0 | 2684 | 31 | 0 | 0 | 0 | 2653
HV network
Overhead lines - Conductor
|  |  |  | 6.6/11 kV OHL (Open) | 12254 | 0 | 52 | 0 | 32 | 12234 | 0 | 89 | 0 | 77 | 12222 | 0 | 79 | 0 | 64 | 12207 | 0 | 55 | 0 | 55 | 12207 | 0 | 55 | 0 | 55 | 12207
|  |  |  | 6.6/11 kV OHL (Covered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV OHL (Open) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV OHL (Covered) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Overhead lines - Support
|  |  |  | 6.6/11 kV Support | 163307 | 0 | 1809 | 0 | 1678 | 163176 | 0 | 2035 | 0 | 1912 | 163053 | 0 | 2381 | 0 | 1861 | 162533 | 0 | 1582.5 | 0 | 1582.5 | 162533 | 0 | 1582.5 | 0 | 1582.5 | 162533
|  |  |  | 20 kV Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Underground cables (kms)
|  |  |  | 6.6/11kV UG Cable | 5119.7 | 0 | 0 | 120 | 0 | 5239.7 | 0 | 11 | 54.8 | 11 | 5294.5 | 0 | 4.7 | 66.9 | 5 | 5361.7 | 0 | 0 | 51 | 0 | 5412.7 | 0 | 0 | 49 | 0 | 5461.7
|  |  |  | 20kV UG Cable | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  |  | HV Sub Cable | 5 | 0 | 0 | - | 0 | 5 | 0 | 0 | - | 0 | 5 | 0 | 0 | - | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5
Switchgear
|  |  |  | 6.6/11 kV CB (PM) | 615 | 0 | 48 | 0 | 196 | 763 | 0 | 55 | 0 | 119 | 827 | 0 | 64 | 0 | 150 | 913 | 0 | 100 | 0 | 100 | 913 | 0 | 43 | 0 | 43 | 913
|  |  |  | 6.6/11 kV CB (GM) | 2940 | 0 | 24 | 15 | 36 | 2967 | 7 | 43 | 22 | 33 | 2972 | 0 | 43 | 13 | 50 | 2992 | 3 | 50 | 15 | 50 | 3004 | 3 | 50 | 14 | 50 | 3015
|  |  |  | 6.6/11 kV Switch (PM) | 138 | 0 | 3 | 0 | 15 | 150 | 0 | 2 | 0 | 14 | 162 | 8 | 3 | 0 | 3 | 154 | 3 | 100 | 0 | 100 | 151 | 3 | 43 | 0 | 43 | 148
|  |  |  | 6.6/11 kV Switch (GM) | 2496 | 14 | 18 | 4 | 18 | 2486 | 48 | 26 | 5 | 25 | 2442 | 50 | 26 | 8 | 26 | 2400 | 41 | 25 | 6 | 25 | 2365 | 40 | 50 | 5 | 50 | 2330
|  |  |  | 6.6/11 kV RMU | 7060 | 0 | 49 | 83 | 72 | 7166 | 0 | 72 | 87 | 73 | 7254 | 5 | 100 | 114 | 100 | 7363 | 2 | 225 | 85 | 225 | 7446 | 2 | 160 | 82 | 160 | 7526
|  |  |  | 6.6/11 kV Switchgear - Other (PM) | 5011 | 0 | 93 | 21 | 252 | 5191 | 0 | 36 | 24 | 305 | 5484 | 0 | 65 | 20 | 227 | 5666 | 0 | 0 | 18 | 0 | 5684 | 0 | 0 | 18 | 0 | 5702
|  |  |  | 6.6/11 kV Switchgear - Other (GM) | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
|  |  |  | 20 kV CB (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV CB (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switch (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switch (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV RMU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switchgear - Other (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Switchgear - Other (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformers
|  |  |  | 6.6/11 kV Transformer (PM) | 31144 | 0 | 511 | 127 | 513 | 31273 | 60 | 559 | 140 | 537 | 31331 | 51 | 559 | 130 | 559 | 31410 | 47 | 182 | 114 | 182 | 31477 | 45 | 343 | 109 | 343 | 31541
|  |  |  | 6.6/11 kV Transformer (GM) | 7770 | 0 | 46 | 95 | 69 | 7888 | 16 | 87 | 104 | 72 | 7961 | 21 | 87 | 114 | 87 | 8054 | 16 | 22 | 92 | 22 | 8130 | 15 | 42 | 88 | 42 | 8203
|  |  |  | 20 kV Transformer (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 20 kV Transformer (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EHV Network
Overhead lines - Conductor
|  |  |  | 33kV OHL (Pole Line) | 1196 | 0 | 5 | 0 | 5 | 1196 | 0 | 20 | 0 | 14 | 1190 | 0 | 25 | 0 | 21 | 1186 | 0 | 0 | 0 | 0 | 1186 | 0 | 0 | 0 | 0 | 1186
|  |  |  | 33kV OHL (Tower Line) | 41 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 41
|  |  |  | 66kV OHL (Pole Line) | 329 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 329
|  |  |  | 66kV OHL (Tower Line) | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28
Overhead lines - Support
|  |  |  | 33kV Pole | 15348 | 0 | 138 | 0 | 138 | 15348 | 0 | 285 | 0 | 261 | 15324 | 0 | 366 | 0 | 366 | 15324 | 0 | 350 | 0 | 350 | 15324 | 0 | 350 | 0 | 350 | 15324
|  |  |  | 33kV Tower | 190 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 190
|  |  |  | 66kV Pole | 4318 | 0 | 0 | 0 | 0 | 4318 | 0 | 0 | 0 | 0 | 4318 | 0 | 0 | 0 | 0 | 4318 | 0 | 0 | 0 | 0 | 4318 | 0 | 0 | 0 | 0 | 4318
|  |  |  | 66kV Tower | 251 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 251
Underground cables (kms)
|  |  |  | 33kV UG Cable (Non Pressurised) | 364.14 | 0 | 0 | 1 | 0 | 365.14 | 0 | 0 | 12.9 | 0 | 378.04 | 0 | 0 | 0.4 | 0.4 | 378.84 | 0 | 0 | 2 | 0 | 380.84 | 0 | 0 | 6 | 0 | 386.84
|  |  |  | 33kV UG Cable (Oil) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33kV UG Cable (Gas) | 8.124 | 0 | 0 | 0 | 0 | 8.124 | 0 | 0 | 0 | 0 | 8.124 | 0 | 0 | 0 | 0 | 8.124 | 0 | 0 | 0 | 0 | 8.124 | 0 | 0 | 0 | 0 | 8.124
|  |  |  | 66kV UG Cable (Non Pressurised) | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6
|  |  |  | 66kV UG Cable (Oil) | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2
|  |  |  | 66kV UG Cable (Gas) | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1
Submarine cables (kms)
|  |  |  | EHV Sub Cable | 1.3 | 0 | 0 | - | 0 | 1.3 | 0 | 0 | - | 0 | 1.3 | 0 | 0 | - | 0 | 1.3 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 1.3
Switchgear
|  |  |  | 33 KV CB (ID) | 295 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 7 | 302 | 0 | 0 | 1 | 6 | 309 | 0 | 6 | 1 | 6 | 310 | 0 | 6 | 1 | 6 | 311
|  |  |  | 33 kV CB (OD) | 294 | 10 | 5 | 0 | 5 | 284 | 2 | 2 | 0 | 2 | 282 | 6 | 30 | 0 | 30 | 276 | 2 | 4 | 1 | 4 | 275 | 2 | 4 | 1 | 4 | 274
|  |  |  | 33 kV Switch (GM) | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16
|  |  |  | 33 kV Switch (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV RMU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV Switchgear - Other | 1117 | 9 | 10 | 0 | 10 | 1108 | 26 | 1 | 0 | 1 | 1082 | 4 | 8 | 0 | 8 | 1078 | 4 | 0 | 2 | 0 | 1076 | 4 | 0 | 2 | 0 | 1074
|  |  |  | 66 KV CB (ID & OD) | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 1 | 0 | 1 | 53 | 0 | 1 | 0 | 1 | 53
|  |  |  | 66 KV Switchgear - Other | 233 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 233 | 2 | 0 | 0 | 0 | 231 | 0 | 0 | 2 | 0 | 233 | 0 | 0 | 0 | 0 | 233
Transformers
|  |  |  | 33 kV Transformer (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 33 kV Transformer (GM) | 247 | 2 | 0 | 3 | 0 | 248 | 0 | 0 | 3 | 0 | 251 | 5 | 0 | 1 | 0 | 247 | 2 | 2 | 2 | 2 | 247 | 2 | 2 | 2 | 2 | 247
|  |  |  | 33 kV AuxiliaryTransfomer | 242 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 2 | 0 | 244 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 244
|  |  |  | 66 kV Transformer | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 2 | 0 | 2 | 30 | 0 | 2 | 0 | 2 | 30
|  |  |  | 66 kV AuxiliaryTransfomer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132kV Network
Overhead lines - Conductor
|  |  |  | 132kV OHL Conductor (Pole Line) | 91 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 91
|  |  |  | 132kV OHL Conductor (Tower Line) | 1089 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 1089 | 0 | 0 | 0 | 0 | 1089
Overhead lines - Support
|  |  |  | 132kV Pole | 835 | 0 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 835 | 0 | 10 | 0 | 10 | 835 | 0 | 10 | 0 | 10 | 835
|  |  |  | 132kV Tower | 2354 | 0 | 0 | 0 | 0 | 2354 | 0 | 0 | 0 | 0 | 2354 | 0 | 0 | 0 | 0 | 2354 | 0 | 1 | 0 | 1 | 2354 | 0 | 1 | 0 | 1 | 2354
|  |  |  | 132kV Fittings (Tower Line) | 4708 | 0 | 0 | 0 | 0 | 4708 | 0 | 0 | 0 | 0 | 4708 | 0 | 0 | 0 | 0 | 4708 | 0 | 0 | 0 | 0 | 4708 | 0 | 0 | 0 | 0 | 4708
Underground cables (kms)
|  |  |  | 132kV UG Cable (Non Pressurised) | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0.4 | 0 | 35.4 | 0 | 0 | 0 | 0 | 35.4 | 0 | 0 | 0 | 0 | 35.4 | 0 | 0 | 0 | 0 | 35.4
|  |  |  | 132kV UG Cable (Oil) | 58 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 58 | 0 | 0.1 | 0 | 0.1 | 58 | 0 | 0.1 | 0 | 0.1 | 58
|  |  |  | 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Submarine cables (kms)
|  |  |  | 132 kV Sub Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Switchgear
|  |  |  | 132 kV CB (ID & OD) | 214 | 2 | 1 | 2 | 1 | 214 | 0 | 0 | 2 | 1 | 217 | 0 | 0 | 3 | 2 | 222 | 0 | 2 | 0 | 2 | 222 | 0 | 2 | 0 | 2 | 222
|  |  |  | 132 kV Switchgear (other) | 730 | 0 | 0 | 0 | 0 | 730 | 7 | 4 | 0 | 4 | 723 | 0 | 0 | 2 | 2 | 727 | 0 | 0 | 0 | 0 | 727 | 0 | 0 | 0 | 0 | 727
Transformers
|  |  |  | 132 kV Transformer | 128 | 0 | 0 | 0 | 0 | 128 | 1 | 0 | 2 | 0 | 129 | 3 | 4 | 2 | 4 | 128 | 1 | 2 | 1 | 2 | 128 | 0 | 2 | 3 | 2 | 131
|  |  |  | 132 kV AuxiliaryTransfomer | 133 | 0 | 0 | 0 | 0 | 133 | 1 | 0 | 2 | 0 | 134 | 0 | 0 | 0 | 4 | 138 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 2 | 0 | 140
Tele-control / SCADA
Primary substation
|  |  |  | 132 kV/EHV RTU (PM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
|  |  |  | 132 kV/EHV RTU (GM) | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 272
Secondary substation
|  |  |  | HV RTU (PM) | 1244 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 1 | 0 | 1245 | 0 | 0 | 1 | 0 | 1246
|  |  |  | HV RTU (GM) | 143 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 143

## FBPQ LR1
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
LR1 - Demand
Demand Totals
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
| Gross direct costs | £m | 17.6 | 18.1 | 20.7 | 15.3 | 14.6 | 13.4 | 14.1 | 13.1 | 13.1 | 13.8 | 56.4 | 29.9 | 86.3 | 67.5 | -21.78%
| Customer contributions directs | £m | 17 | 17.1 | 19 | 14.15 | 13.5 | 12.7 | 13.15 | 12.3 | 12.3 | 12.85 | 53.1 | 27.65 | 80.75 | 63.3 | -21.61%
| Net (gross directs - customer contributions directs) | £m | 0.6 | 1 | 1.7 | 1.15 | 1.1 | 0.7 | 0.95 | 0.8 | 0.8 | 0.95 | 3.3 | 2.25 | 5.55 | 4.2 | -24.32%
| Customer contributions indirects | £m | -0.7 | 3.8 | 5.8 | 5.4 | 5.1 | 4.8 | 5 | 4.7 | 4.7 | 4.9 | 8.9 | 10.5 | 19.4 | 24.1 | 24.23%
| Net (gross directs - customer contributions directs and indirects) | £m | 1.3 | -2.8 | -4.1 | -4.25 | -4 | -4.1 | -4.05 | -3.9 | -3.9 | -3.95 | -5.6 | -8.25 | -13.85 | -19.9 | 43.68%
Demand trends
|  |  | DPCR4 |  |  |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
| Estimated system maximum demand | MW | 2248.9503 | 2150.7975 | 2179.2926 | 2157.8561 | 2157.8561 | 2179.4346 | 2201.229 | 2223.2413 | 2245.4737 | 2267.9284
| Increase (reduction) in max demand | MW | 14.9925 | -98.1529 | 28.4951 | -21.4365 | 0 | 21.5786 | 21.7943 | 22.0123 | 22.2324 | 22.4547
| Incremental increase in max demand due to new connections | MW | 14.9925 | 13.3021 | 18.3856 | 14.915 | 14.75 | 15.8 | 17.1 | 18.1 | 18.1 | 18.1
| Incremental reduction in max demand due to disconnections | MW | 0 | -0.4282 | -0.8454 | -0.47 | -0.448 | -0.72 | -0.775 | -0.775 | -0.775 | -0.775
| Net change in max demand (not due to connections/disconnections) | MW | 0 | -111.0268 | 10.9549 | -35.8815 | -14.302 | 6.4986 | 5.4693 | 4.6873 | 4.9074 | 5.1297
| Estimated units distributed | GWh | 13175.3122 | 12752.5159 | 12653.1505 | 12355.3505 | 12355.3505 | 12478.9041 | 12603.6933 | 12729.7304 | 12857.0279 | 12985.5983
| Increase (reduction) in units distributed | GWh | 56.0175 | -422.7964 | -99.3654 | -297.8 | 0 | 123.5537 | 124.7892 | 126.0371 | 127.2975 | 128.5704
| Increase in units distributed due to generic background demand growth | GWh | 56.0175 | -422.7964 | -99.3654 | -171.3 | 123.6 | 123.5537 | 124.7892 | 126.0371 | 127.2975 | 128.5704
| Reduction in units distributed due to energy efficiency | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Units distributed offset by DG | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Units distributed offset by DSM | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Price impact on units distributed | GWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Economic downturn effect on units distributed | GWh | 0 | 0 | 0 | -126.5 | -123.6 | 0 | 0 | 0 | 0 | 0
Estimated units distributed
| LV | GWh | 7428.8729 | 7245.3085 | 7216.2042 | 7288.3662 | 7288.3662 | 7361.2499 | 7434.8624 | 7509.211 | 7584.3031 | 7660.1462
| HV | GWh | 2674.8897 | 2491.1796 | 2482.1084 | 2407.6451 | 2407.6451 | 2431.7216 | 2456.0388 | 2480.5992 | 2505.4051 | 2530.4592
| EHV (inc. 132kV) | GWh | 3071.5497 | 3016.0277 | 2954.8379 | 2659.3541 | 2659.3541 | 2685.9477 | 2712.8072 | 2739.9352 | 2767.3346 | 2795.0079
| Total units distributed | GWh | 13175.3122 | 12752.5159 | 12653.1505 | 12355.3655 | 12355.3655 | 12478.9191 | 12603.7083 | 12729.7454 | 12857.0429 | 12985.6133
Incremental increase in units distributed attributable to new connections
| LV | MWh | 37362.5 | 38496.5 | 42462 | 31500 | 30345 | 28000 | 27125 | 24675 | 24675 | 24675
| HV | MWh | 28470 | 5255 | 37230 | 30660 | 30660 | 32850 | 39420 | 48180 | 48180 | 48180
| EHV (inc. 132kV) | MWh | 0 | 0 | 30000 | 89000 | 0 | 0 | 20000 | 20000 | 0 | 20000
| Total increase in units distributed due to new connections | MWh | 65832.5 | 43751.5 | 109692 | 151160 | 61005 | 60850 | 86545 | 92855 | 72855 | 92855
Connections/disconnections volume
|  |  | DPCR4 |  |  |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15
Connections/Disconnections
Estimated number demand connections/disconnections at LV
| IDNO connections | # | 0 | 0 | 7 | 2 | 4 | 8 | 10 | 12 | 12 | 12
| Connections (excluding IDNOs) | # | 10675 | 11161 | 10696 | 9200 | 8850 | 8200 | 8000 | 7300 | 7300 | 7300
| Disconnections | # | N/A | 162 | 314 | 200 | 180 | 200 | 250 | 250 | 250 | 250
Estimated number demand connections/disconnections at HV
| IDNO connections | # | 0 | 1 | 4 | 3 | 3 | 6 | 8 | 10 | 10 | 10
| Connections (excluding IDNOs) | # | 13 | 3 | 19 | 15 | 15 | 17 | 20 | 24 | 24 | 24
| Disconnections | # | N/A | 1 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2
Estimated number demand connections/disconnections at EHV
| IDNO connections | # | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Connections (excluding IDNOs) | # | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1
| Disconnections | # | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Estimated number demand connections/disconnections at 132kV
| IDNO connections | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Connections (excluding IDNOs) | # | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Disconnections | # | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total number of demand connections | # | 10688 | 11165 | 10728 | 9221 | 8872 | 8231 | 8039 | 7346 | 7346 | 7347
| Total number of demand disconnections | # | 0 | 163 | 316 | 201 | 181 | 202 | 252 | 252 | 252 | 252
Customer specific demand investment
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
| Customer specific demand investment | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
New connections & customer specific reinforcement:
Connections provided at LV
| Sole use | £m | 14.1 | 12 | 13.8 | 11.3 | 10.9 | 10 | 9.8 | 9 | 9 | 9 | 39.9 | 22.2 | 62.1 | 46.9 | -24.48%
| Shared | £m | 0.7 | 1 | 1.7 | 1 | 0.9 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 3.4 | 1.9 | 5.3 | 4.1 | -22.64%
| LV total | £m | 14.8 | 13 | 15.5 | 12.3 | 11.8 | 11.3 | 11.1 | 10.1 | 10.1 | 10.1 | 43.3 | 24.1 | 67.4 | 51 | -24.33%
Connections provided at HV
| Sole use | £m | 2.2 | 3.2 | 2.5 | 1.7 | 1.9 | 1.1 | 1 | 1 | 1 | 1 | 7.9 | 3.6 | 11.5 | 11.9 | 3.478%
| Shared | £m | 0 | 0 | 0.5 | 0.6 | 0.7 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0.5 | 1.3 | 1.8 | 3.2 | 77.78%
| HV total | £m | 2.2 | 3.2 | 3 | 2.3 | 2.6 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 8.4 | 4.9 | 13.3 | 15.1 | 13.53%
Connections provided at EHV
| Sole use | £m | 0.6 | 1.2 | 0.5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0.4 | 2.7 | 0.8 | -70.37%
| Shared | £m | 0 | 0.7 | 1.7 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.5 | 2.9 | 0.6 | -79.31%
| EHV total | £m | 0.6 | 1.9 | 2.2 | 0.7 | 0.2 | 0 | 0.7 | 0 | 0 | 0.7 | 4.7 | 0.9 | 5.6 | 1.4 | -75%
Connections provided at 132kV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV total | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expenditure on DSM to avoid customer spec investment | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total inc. expenditure on DSM to avoid customer spec investment | £m | 17.6 | 18.1 | 20.7 | 15.3 | 14.6 | 13.7 | 13.4 | 12.4 | 12.4 | 12.4 | 56.4 | 29.9 | 86.3 | 67.5 | -21.78%
| Expenditure avoided due to DG | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Expenditure avoided due to DSM | £m |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Customer contributions - customer specific demand investment
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
| Customer contributions - customer specific demand investment | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
Customer contributions (directs) for connections at LV
| Sole use | £m | 14.1 | 12 | 13.8 | 11.3 | 10.9 | 10 | 9.8 | 9 | 9 | 9 | 39.9 | 22.2 | 62.1 | 46.9 | -24.48%
| Shared | £m | 0.1 | 0.4 | 0.9 | 0.4 | 0.4 | 1.3 | 1.3 | 1.1 | 1.1 | 1.1 | 1.4 | 0.8 | 2.2 | 1.6 | -27.27%
| LV total | £m | 14.2 | 12.4 | 14.7 | 11.7 | 11.3 | 11.3 | 11.1 | 10.1 | 10.1 | 10.1 | 41.3 | 23 | 64.3 | 48.5 | -24.57%
Customer contributions (directs) for connections at HV
| Sole use | £m | 2.2 | 3.2 | 2.5 | 1.7 | 1.9 | 1.1 | 1 | 1 | 1 | 1 | 7.9 | 3.6 | 11.5 | 11.9 | 3.478%
| Shared | £m | 0 | 0 | 0.2 | 0.2 | 0.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0.2 | 0.4 | 0.6 | 1.8 | 200%
| HV total | £m | 2.2 | 3.2 | 2.7 | 1.9 | 2.1 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 8.1 | 4 | 12.1 | 13.7 | 13.22%
Customer contributions (directs) for connections at EHV
| Sole use | £m | 0.6 | 1.2 | 0.5 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 0.4 | 2.7 | 0.8 | -70.37%
| Shared | £m | 0 | 0.3 | 1.1 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0.25 | 1.65 | 0.3 | -81.82%
| EHV total | £m | 0.6 | 1.5 | 1.6 | 0.55 | 0.1 | 0 | 0.55 | 0 | 0 | 0.55 | 3.7 | 0.65 | 4.35 | 1.1 | -74.71%
Customer contributions (directs) for connections at 132kV
| Sole use | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shared | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV total | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer contributions (directs) total | £m | 17 | 17.1 | 19 | 14.15 | 13.5 | 13.7 | 13.4 | 12.4 | 12.4 | 12.4 | 53.1 | 27.65 | 80.75 | 63.3 | -21.61%
| Customer contributions (indirects) | £m | -0.7 | 3.8 | 5.8 | 5.4 | 5.1 | 4.8 | 5 | 4.7 | 4.7 | 4.9 | 8.9 | 10.5 | 19.4 | 24.1 | 24.23%
| Customer contributions total | £m | 16.3 | 20.9 | 24.8 | 19.55 | 18.6 | 18.5 | 18.4 | 17.1 | 17.1 | 17.3 | 62 | 38.15 | 100.15 | 87.4 | -12.73%
| Total inc. exp on DSM to avoid customer spec investment (net of cust cont) | £m | 1.3 | -2.8 | -4.1 | -4.25 | -4 | -4.1 | -4.05 | -3.9 | -3.9 | -3.95 | -5.6 | -8.25 | -13.85 | -19.9 | 43.68%
|  |  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
| Unapportioned part of shared LV | £m | 0.6 | 0.6 | 0.8 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 2 | 1.1 | 3.1 | 2.5 | -19.35%
| Unapportioned part of shared HV | £m | 0 | 0 | 0.3 | 0.4 | 0.5 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.9 | 1.2 | 1.4 | 16.67%
| Unapportioned part of shared EHV | £m | 0 | 0.4 | 0.6 | 0.15 | 0.1 | 0 | 0.15 | 0 | 0 | 0.15 | 1 | 0.25 | 1.25 | 0.3 | -76%
| Unapportioned part of shared 132kV | £m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## FBPQ LR4
Main Forecast Business Plan DPCR5 | [5 empty] | Index
LR4 - General reinforcement
General reinforcement expenditure
|  |  | DPCR4 |  |  |  |  | DPCR5 | [5 empty] | DPCR4 |  |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 |  | Actuals | Forecast | Total |  | Forecast | % change
|  |  | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) |  | (£m) | (£m) | (£m) |  | (£m) | (£m)
General reinforcement:
|  | LV System | 0.1 | 0.1 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  | 0.5 | 0.4 | 0.9 |  | 1 | 11.11%
|  | HV System | 1.3 | 2 | 0.9 | 1 | 1.1 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 |  | 4.2 | 2.1 | 6.3 |  | 6.3 | -1.41e-14%
|  | EHV System | 2.2 | 1.6 | 1.4 | 2 | 2.7 | 2.6 | 1.8 | 1.5 | 1.1 | 0.8 |  | 5.2 | 4.7 | 9.9 |  | 14.9 | 50.51%
|  | 132kV System | 1.3 | 2 | 1.1 | 0.9 | 0.8 | 1.2 | 0.2 | 0.6 | 0.6 | 0.6 |  | 4.4 | 1.7 | 6.1 |  | 6.8 | 11.48%
|  | Expenditure on DSM to avoid gen reinf. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
|  | Total | 4.9 | 5.7 | 3.7 | 4.1 | 4.8 | 5.2 | 3.4 | 3.6 | 3.2 | 2.9 |  | 14.3 | 8.9 | 23.2 |  | 29 | 25%
|  | Expenditure avoided due to DG |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
|  | Expenditure avoided due to DSM |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
General reinforcement projects
|  | Scheme details | DPCR5 2011/12: DPCR4 |  | DPCR5 |  |  |  |  | Scheme description
|  | Named scheme | Voltage | Limiting Factor | Forecast year in which substation demand will reach substation firm capacity | MVA of additional firm capacity to be installed | Total cost of project | Total cost of project in DPCR5 period | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Brief description of work involved, substations affected, assets installed/replaced etc.
|  | (Unique name) | (kV) | (a-j) | (Year) | (MVA) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (Description)
| 1 |  | 33/11 | a | 2008/9 | 10 | 0.6 | 0.6 | DPCR5 2010/11: 0.6; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Change 33/11 transformer units to 12/24 and replace 11kV switchboard | 0 | 0 | 0 | 0 | 0 | 0
| 2 |  | 33 | c | 2008/9 | 4.6 | 1.4 | 1.4 | DPCR5 2010/11: 0; DPCR5 2011/12: 0.7; DPCR5 2012/13: 0.7; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Establish new 33kV circuit into Tregaron site. | 0 | 0 | 0 | 0 | 0 | 0
| 3 |  | 33 | a | 2011/12 | 3 | 0.45 | 0.45 | DPCR5 2010/11: 0; DPCR5 2011/12: 0.45; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | 11kV load transfer to Waterton 132/11 | 0 | 0 | 0 | 0 | 0 | 0
| 4 |  | 33 | d | 2014/15 | 23 | 0.8 | 0.8 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0.6; DPCR5 2014/15: 0.2 | Establish 3rd 33kV circuit (cable) to s/s and additional 12/24 transformer & 11kV Swbd Change | 0 | 0 | 0 | 0 | 0 | 0
| 5 |  | 33 | b | 2011/12 | 7.1 | 0.3 | 0.3 | DPCR5 2010/11: 0; DPCR5 2011/12: 0.3; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Establish 33kV switchboard and 2nd transformer unit. | 0 | 0 | 0 | 0 | 0 | 0
| 6 |  | 33 | c | 2009/10 | 7.1 | 0.8 | 0.8 | DPCR5 2010/11: 0.3; DPCR5 2011/12: 0.4; DPCR5 2012/13: 0.1; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Install 2nd transformer, and 33kV circuit (o/h) | 0 | 0 | 0 | 0 | 0 | 0
| 7 |  | 33 | a/b | 2013/14 | 6 | 1.2 | 1.2 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 1.2; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Increase 11kV Interconnection between 3 Tx Group | 0 | 0 | 0 | 0 | 0 | 0
| 8 |  | 33/11 | a | 2013/14 | 17.9 | 0.7 | 0.7 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0.7; DPCR5 2014/15: 0 | Overlay 33kV circuits and install 19/38 MVA 33/11 units | 0 | 0 | 0 | 0 | 0 | 0
| 9 |  | 33 | b | 2009 | 20 | 0.4 | 0.4 | DPCR5 2010/11: 0.4; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Establish new 33kV circuit to Gas Yard, to remove load from Gas Yard/Nelson 33kV ring. | 0 | 0 | 0 | 0 | 0 | 0
| 10 |  | 66 | j | 2009/10 | 6 | 0.2 | 0.2 | DPCR5 2010/11: 0.2; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Establish 66kV bar with bus-section breaker | 0 | 0 | 0 | 0 | 0 | 0
| 11 |  | 66 | j | 2008/9 | 12 | 0.3 | 0.3 | DPCR5 2010/11: 0.3; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Reconductor front end of 66kV circuits Abergavenny to Crickhowell or apply higher operating Temp/increasing height | 0 | 0 | 0 | 0 | 0 | 0
| 12 |  | 33 | b | 2008/9 | 6 | 0.9 | 0.9 | DPCR5 2010/11: 0; DPCR5 2011/12: 0.5; DPCR5 2012/13: 0.4; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Increase height to allow higher Op Temp, installation of 11kV Cap Bank Brawdy | 0 | 0 | 0 | 0 | 0 | 0
| 13 |  | 33/11 | a | 2013/14 | 14 | 1.7 | 1.7 | DPCR5 2010/11: 0.2; DPCR5 2011/12: 0; DPCR5 2012/13: 0.7; DPCR5 2013/14: 0.8; DPCR5 2014/15: 0 | Install addition 33/11 Tx capacity 11kV interconnection between sites | 0 | 0 | 0 | 0 | 0 | 0
| 14 |  | 33 | a | 2008/9 | 15 | 1.6 | 1.6 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0.4; DPCR5 2013/14: 0.6; DPCR5 2014/15: 0.6 | Additional Grid Tx at Rhos or 33 kV circuit uprating | 0 | 0 | 0 | 0 | 0 | 0
| 15 |  | 33/11 | f | 2008/9 | 6.2 | 0.8 | 0.8 | DPCR5 2010/11: 0.6; DPCR5 2011/12: 0.2; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | New 33kV tranformer circuit and 33/11kV transformer | 0 | 0 | 0 | 0 | 0 | 0
| 16 |  | 33/11 | a | 2008/9 | 15 | 0.45 | 0.45 | DPCR5 2010/11: 0; DPCR5 2011/12: 0.45; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Transformer change to 19/38 MVA units & 33/11kV Swbd Change | 0 | 0 | 0 | 0 | 0 | 0
| 17 |  | 33 |  |  |  | 2.3 | 2.3 | DPCR5 2010/11: 0.2; DPCR5 2011/12: 0.2; DPCR5 2012/13: 0.2; DPCR5 2013/14: 0.2; DPCR5 2014/15: 1.5 | Typically smaller schemes. Unidentified larger scheme(s) 2014/15. | 0 | 0 | 0 | 0 | 0 | 0
| 18 |  | 132/11 | a | 2010/11 | 11.3 | 2.5 | 0.5 |  |  |  | 1 | 1 | 0.5 | 0 | 0 | 0 | 0 | Establish 132/11kV susbstaion at Abergavenny | 0 | 0 | 0 | 0 | 0 | 0
| 19 |  | 132/11 | b | 2010/11 | 14.5 | 2 | 1.5 |  |  |  |  | 0.5 | 1.5 | 0 | 0 | 0 | 0 | Establish 132/11kV substation near Pentrebach to deload existing 33kV ccts | 0 | 0 | 0 | 0 | 0 | 0
| 20 |  | 132/33 | c | 2011/12 | 11 | 1 | 1 | DPCR5 2010/11: 0; DPCR5 2011/12: 1; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 0 | Establish a second 132/33 transformer | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 132/33 | a | 2013/14 | 40 | 1 | 1 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 1 | Establish second 132/33kv unit and break parallel. | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132/33 | c | 2014/15 | 40 | 1 | 1 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 1; DPCR5 2014/15: 0 | Establish second 132/33kv unit and break parallel. | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132/11 | a | 2014/15 | 30 | 1.2 | 1.2 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0; DPCR5 2013/14: 0; DPCR5 2014/15: 1.2 | Establish new 132/11kV site | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132 |  |  |  | 0.6 | 0.6 | DPCR5 2010/11: 0; DPCR5 2011/12: 0; DPCR5 2012/13: 0.6; DPCR5 2013/14: 0 | Unidentified | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 319.7 | 24.2 | 21.7 | 0 | 0 | 0 | 1 | 1.5 | 4.8 | 4.2 | 4.3 | 3.9 | 4.5

## FBPQ LR6
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
LR6 - Fault levels
Fault level system measures
|  |  | As at 31st March 2010 |  |  | As at 31st March 2015
|  |  | 132kV | EHV | HV | 132kV | EHV | HV
| No. of switchboards |  | 127 | 172 | 207 | 127 | 172 | 207
| No. of switchboards @ >95% of F.L. |  | 4 | 9 | 4 | 4 | 9 | 4
| No. of switchboards having fault level 'operational restrictions' |  | 0 | 0 | 0 | 0 | 0 | 0
Number of fault level schemes
| No. of schemes |  | DPCR4 |  |  | DPCR5
|  |  | 132kV | EHV | HV | 132kV | EHV | HV
| Switchboards |  | 0 | 0 | 0 | 0 | 1 | 0
| Transformers |  | 0 | 0 | 0 | 0 | 0 | 0
| Other |  | 0 | 0 | 0 | 0 | 0 | 0
Fault level reinforcement
|  | DPCR4 |  |  |  |  | DPCR5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m) | (£m)
Fault level reinforcement:
| LV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0
| 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0

## FBPQ NL1
Main Forecast Business Plan DPCR5 |  |  |  |  | Index
NL1 - Condition based expenditure
Total condition based replacement
| Asset Categories |  | DPCR 4 |  |  |  |  | DPCR 5 |  |  |  |  | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 1 | 0.9 | 1.5 | 0.97998 | 0.44857 | 0.82 | 0.89 | 1 | 1 | 1 | 3.4 | 1.4285 | 4.8285 | 4.71 | -2.455%
|  | Underground | 0.5 | 0.7 | 0.6 | 0.6795 | 0.39907 | 1.04 | 1.18 | 1.32 | 1.47 | 1.62 | 1.8 | 1.0786 | 2.8786 | 6.63 | 130.3%
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0.0094229 | 0.031592 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041015 | 0.041015 | 0 | -100%
|  | Underground | 0 | -0.10413 | -0.2 | -0.034053 | -0.053771 | -0.1 | -0.1 | -0.1 | -0.1 | -0.1 | -0.30413 | -0.087824 | -0.39195 | -0.5 | 27.57%
| LV System | Overhead mains | 1.7 | 1.7 | 2 | 1.4574 | 1.4107 | 1.61 | 1.76 | 1.94 | 1.94 | 1.94 | 5.4 | 2.8681 | 8.2681 | 9.19 | 11.15%
|  | Underground mains | 0.2 | 0.2 | 0.3 | 0.18008 | 0.22106 | 0.58 | 0.67 | 0.75 | 0.83 | 0.93 | 0.7 | 0.40114 | 1.1011 | 3.76 | 241.5%
|  | Switchgear (incl other plant & equipment) | 0.2 | 0.1 | 0.1 | 0.26593 | 0.30855 | 0.47 | 0.51 | 0.56 | 0.61 | 0.66 | 0.4 | 0.57449 | 0.97449 | 2.81 | 188.4%
| HV | Overhead lines | 1.9 | 5.2 | 5 | 3.4247 | 3.2169 | 5.15 | 7.1 | 9.07 | 9.07 | 9.07 | 12.1 | 6.6416 | 18.7416 | 39.46 | 110.5%
|  | Underground cables | 0.2 | 0.6 | 1.1 | 0.43136 | 0.24747 | 0.43 | 0.48 | 0.55 | 0.61 | 0.69 | 1.9 | 0.67883 | 2.5788 | 2.76 | 7.025%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0.25 | 0
|  | Switchgear (incl other plant & equipment) | 0.9 | 1.1 | 2.6 | 1.9861 | 2.5316 | 1.81 | 1.88 | 1.94 | 1.99 | 2.04 | 4.6 | 4.5177 | 9.1177 | 9.66 | 5.947%
|  | Transformers | 0.1 | 0.8 | 0.8 | 0.48476 | 0.91513 | 1.76 | 1.85 | 1.93 | 2.01 | 2.08 | 1.7 | 1.3999 | 3.0999 | 9.63 | 210.7%
|  | Substation | 0.6 | 1 | 0.8 | 0.64704 | 0.48758 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 2.4 | 1.1346 | 3.5346 | 3.5 | -0.9793%
| EHV | Overhead lines | 0.3 | 0.4 | 0.9 | 2.0772 | 1.2089 | 0.66 | 1.08 | 1.51 | 1.51 | 1.52 | 1.6 | 3.2862 | 4.8862 | 6.28 | 28.53%
|  | Underground cables | 0.8 | 0.9 | 0 | 0.047114 | 0.10847 | 0.14 | 0.17 | 0.2 | 0.23 | 0.26 | 1.7 | 0.15558 | 1.8556 | 1 | -46.11%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0.5 | 0
|  | Switchgear (incl other plant & equipment) | 0.5 | 1.3 | 1.9 | 1.0753 | 1.5185 | 0.65 | 0.66 | 0.67 | 0.67 | 0.67 | 3.7 | 2.5938 | 6.2938 | 3.32 | -47.25%
|  | Transformers | 0.1 | 0.3 | 1 | 0.62191 | 0.36121 | 1.46 | 1.52 | 1.59 | 1.7 | 1.76 | 1.4 | 0.98312 | 2.3831 | 8.03 | 237%
|  | Substation | 0.4 | 0.1 | 0.3 | 0.1382 | 0.21272 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.8 | 0.35092 | 1.1509 | 2.4 | 108.5%
| 132kV | Overhead lines | 0.5 | 1.3 | 1.1 | 0.88575 | 0.33383 | 0.6 | 0.77 | 0.96 | 0.98 | 1 | 2.9 | 1.2196 | 4.1196 | 4.31 | 4.622%
|  | Underground cables | 0 | 0 | 0.4 | 0.13087 | 0.16217 | 0.36 | 0.48 | 0.6 | 0.6 | 0.71 | 0.4 | 0.29305 | 0.69305 | 2.75 | 296.8%
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 1 | 1.8 | 0.1 | 0.557 | 0.13585 | 0.16 | 0.17 | 0.18 | 0.2 | 0.21 | 2.9 | 0.69284 | 3.5928 | 0.92 | -74.39%
|  | Transformers | 0.1 | 0.6 | 0.8 | 1.0418 | 0 | 2.29 | 2.29 | 2.29 | 2.14 | 2.14 | 1.5 | 1.0418 | 2.5418 | 11.15 | 338.7%
|  | Substation | 0.2 | 0.2 | 0.9 | 0.23662 | 0.19377 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 1.3 | 0.43039 | 1.7304 | 1.05 | -39.32%
| Total non-load replacement (£m) |  | 11.2 | 19.0959 | 22 | 17.324 | 14.4 | 21.43 | 24.9 | 28.5 | 29 | 29.74 | 52.2959 | 31.7239 | 84.0198 | 133.57 | 58.97%
Proactive condition based replacement (non fault)
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 1 | 0.9 | 1.5 | 0.97998 | 0.44857 | 0.82 | 0.89 | 1 | 1 | 1 | 3.4 | 1.4285 | 4.8285 | 4.71 | -2.455%
|  | Underground | 0.5 | 0.7 | 0.6 | 0.6795 | 0.39907 | 1.04 | 1.18 | 1.32 | 1.47 | 1.62 | 1.8 | 1.0786 | 2.8786 | 6.63 | 130.3%
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0.0094229 | 0.031592 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041015 | 0.041015 | 0 | -100%
|  | Underground | 0 | -0.10413 | -0.2 | -0.034053 | -0.053771 | -0.1 | -0.1 | -0.1 | -0.1 | -0.1 | -0.30413 | -0.087824 | -0.39195 | -0.5 | 27.57%
| LV System | Overhead mains | 1.7 | 1.7 | 2 | 1.4574 | 1.4107 | 1.61 | 1.76 | 1.94 | 1.94 | 1.94 | 5.4 | 2.8681 | 8.2681 | 9.19 | 11.15%
|  | Underground mains | 0.2 | 0.2 | 0.2 | 0.080082 | 0.12106 | 0.48 | 0.57 | 0.65 | 0.73 | 0.83 | 0.6 | 0.20114 | 0.80114 | 3.26 | 306.9%
|  | Switchgear (incl other plant & equipment) | 0.2 | 0.1 | 0.1 | 0.26593 | 0.30855 | 0.47 | 0.51 | 0.56 | 0.61 | 0.66 | 0.4 | 0.57449 | 0.97449 | 2.81 | 188.4%
| HV | Overhead lines | 1.9 | 5.2 | 5 | 3.4247 | 3.2169 | 5.15 | 7.1 | 9.07 | 9.07 | 9.07 | 12.1 | 6.6416 | 18.7416 | 39.46 | 110.5%
|  | Underground cables | 0.2 | 0.6 | 1.1 | 0.43136 | 0.24747 | 0.43 | 0.48 | 0.55 | 0.61 | 0.69 | 1.9 | 0.67883 | 2.5788 | 2.76 | 7.025%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.9 | 1.1 | 2.5 | 1.8861 | 2.4316 | 1.71 | 1.78 | 1.84 | 1.89 | 1.94 | 4.5 | 4.3177 | 8.8177 | 9.16 | 3.882%
|  | Transformers | 0.1 | 0.8 | 0.7 | 0.38476 | 0.81513 | 1.66 | 1.75 | 1.83 | 1.91 | 1.98 | 1.6 | 1.1999 | 2.7999 | 9.13 | 226.1%
|  | Substation | 0.6 | 1 | 0.8 | 0.64704 | 0.48758 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 2.4 | 1.1346 | 3.5346 | 3.5 | -0.9793%
| EHV | Overhead lines | 0.3 | 0.4 | 0.9 | 2.0772 | 1.2089 | 0.66 | 1.08 | 1.51 | 1.51 | 1.52 | 1.6 | 3.2862 | 4.8862 | 6.28 | 28.53%
|  | Underground cables | 0.8 | 0.9 | 0 | 0.047114 | 0.10847 | 0.14 | 0.17 | 0.2 | 0.23 | 0.26 | 1.7 | 0.15558 | 1.8556 | 1 | -46.11%
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.5 | 1.3 | 1.9 | 1.0753 | 1.5185 | 0.65 | 0.66 | 0.67 | 0.67 | 0.67 | 3.7 | 2.5938 | 6.2938 | 3.32 | -47.25%
|  | Transformers | 0.1 | 0.3 | 0.8 | 0.42191 | 0.16121 | 1.26 | 1.32 | 1.39 | 1.5 | 1.56 | 1.2 | 0.58312 | 1.7831 | 7.03 | 294.3%
|  | Substation | 0.4 | 0.1 | 0.3 | 0.1382 | 0.21272 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.8 | 0.35092 | 1.1509 | 2.4 | 108.5%
| 132kV | Overhead lines | 0.5 | 1.3 | 1.1 | 0.88575 | 0.33383 | 0.6 | 0.77 | 0.96 | 0.98 | 1 | 2.9 | 1.2196 | 4.1196 | 4.31 | 4.622%
|  | Underground cables | 0 | 0 | 0.4 | 0.13087 | 0.16217 | 0.36 | 0.48 | 0.6 | 0.6 | 0.71 | 0.4 | 0.29305 | 0.69305 | 2.75 | 296.8%
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 1 | 1.8 | 0.1 | 0.557 | 0.13585 | 0.16 | 0.17 | 0.18 | 0.2 | 0.21 | 2.9 | 0.69284 | 3.5928 | 0.92 | -74.39%
|  | Transformers | 0.1 | 0.6 | 0.8 | 1.0418 | 0 | 2.29 | 2.29 | 2.29 | 2.14 | 2.14 | 1.5 | 1.0418 | 2.5418 | 11.15 | 338.7%
|  | Substation | 0.2 | 0.2 | 0.9 | 0.23662 | 0.19377 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 1.3 | 0.43039 | 1.7304 | 1.05 | -39.32%
| Total proactive condition based replacement (£m) |  | 11.2 | 19.0959 | 21.5 | 16.824 | 13.9 | 20.78 | 24.25 | 27.85 | 28.35 | 29.09 | 51.7959 | 30.7239 | 82.5198 | 130.32 | 57.93%
Reactive condition-based replacement (fault)
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/15 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| Metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Un-metered LV Services | Overhead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| LV System | Overhead mains | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground mains | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 66.67%
|  | Switchgear (incl other plant & equipment) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV | Overhead lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0.25 | 0
|  | Switchgear (incl other plant & equipment) | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 66.67%
|  | Transformers | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 66.67%
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV | Overhead lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0.5 | 0
|  | Switchgear (incl other plant & equipment) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transformers | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 1 | 66.67%
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV | Overhead lines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Underground cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Submarine cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Transformers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Substation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total reactive condition based replacement (£m) |  | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 1 | 1.5 | 3.25 | 116.7%
Overhead line refurbishment / replacement
| Asset Categories |  | DPCR 4 2005/06: DPCR 4; DPCR 5 2010/11: DPCR 5 | DPCR4 |  |  | DPCR5
|  |  | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10 | 2010/11 | 2011/12 | 2012/13 | 2013/14 | 2014/015 | Actuals | Forecast | Total | Forecast | % change
|  |  | £m | £m | £m | £m | £m | £m | £m | £m | £m | £m
| LV Mains | Refurbishment | 0.5 | 0.6 | 0.7 | 0.63238 | 0.58003 | 0.35 | 0.43 | 0.52 | 0.52 | 0.52 | 1.8 | 1.2124 | 3.0124 | 2.34 | -22.32%
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Covered Conductor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 1.2 | 1.1 | 1.3 | 0.82503 | 0.83067 | 1.26 | 1.33 | 1.42 | 1.42 | 1.42
|  | Total OHL expenditure (£m) | 1.7 | 1.7 | 2 | 1.4574 | 1.4107 | 1.61 | 1.76 | 1.94 | 1.94 | 1.94 | 5.4 | 2.8681 | 8.2681 | 9.19 | 11.15%
| HV | Refurbishment | 1.3 | 4.3 | 3.9 | 2.6698 | 2.3452 | 3.9 | 4.43 | 5.04 | 5.04 | 5.04 | 9.5 | 5.015 | 14.515 | 23.45 | 61.56%
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Covered Conductor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0.6 | 0.9 | 1.1 | 0.75488 | 0.87174 | 1.25 | 2.67 | 4.03 | 4.03 | 4.03
|  | Total OHL expenditure (£m) | 1.9 | 5.2 | 5 | 3.4247 | 3.2169 | 5.15 | 7.1 | 9.07 | 9.07 | 9.07 | 12.1 | 6.6416 | 18.7416 | 39.46 | 110.5%
| EHV - Pole line | Refurbishment | 0 | 0.1 | 0.4 | 1.6909 | 1.1394 | 0.24 | 0.38 | 0.52 | 0.52 | 0.52 | 0.5 | 2.8303 | 3.3303 | 2.18 | -34.54%
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0.3 | 0.3 | 0.5 | 0.38634 | 0.069503 | 0.27 | 0.53 | 0.8 | 0.8 | 0.8
| EHV - Tower line | Fittings only | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Reconductoring | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.11 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0.53 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Tower Refurbishment | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.06 | 0.09 | 0.09 | 0.1
| EHV Total | Total OHL expenditure (£m) | 0.3 | 0.4 | 0.9 | 2.0772 | 1.2089 | 0.66 | 1.08 | 1.51 | 1.51 | 1.52 | 1.6 | 3.2862 | 4.8862 | 6.28 | 28.53%
| 132kV - Pole Line | Refurbishment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Full rebuild | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pole replacement only (i.e. D poles) | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.06 | 0.08 | 0.08 | 0.08
| 132kV - Tower line | Fittings only | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.29 | 0.31 | 0.31 | 0.31
|  | Reconductoring | 0.5 | 1.3 | 1.1 | 0.88575 | 0.33383 | 0.2 | 0.33 | 0.46 | 0.46 | 0.46 | 2.9 | 1.2196 | 4.1196 | 1.91 | -53.64%
|  | Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Tower Refurbishment | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.11 | 0.13 | 0.15 | 0 | 0 | 0 | 0.57 | 0
| 132 kV Total | Total OHL expenditure (£m) | 0.5 | 1.3 | 1.1 | 0.88575 | 0.33383 | 0.6 | 0.77 | 0.96 | 0.98 | 1 | 2.9 | 1.2196 | 4.1196 | 4.31 | 4.622%

## FBPQ C2
Main Forecast Business Plan DPCR5 |  |  |  | Index
C2 - Unit costs
|  |  | Asset categories | Units | New build |  | Replacement
[5 empty] | Direct costs | Cost including indirects (absorbed costs in T2A) | Direct costs | Cost including indirects (absorbed costs in T2A)
[5 empty] | (£k) | (£k) | (£k) | (£k)
LV Network
Overhead lines
|  |  | LV Main (OHL) | km |  |  | 14.06 | 19.99
|  |  | LV Service (OHL) | Each |  |  | 0.2 | 0.32
Overhead lines - Support
|  |  | LV Support | Each |  |  | 1.43 | 1.92
Underground cables
|  |  | LV Main (UG Consac) | km
|  |  | LV Main (UG Plastic) | km | 33.4 | 40.08 | 67.22 | 67.22
|  |  | LV Main (UG Paper) | km |  |  | 67.22 | 75.91
|  |  | LV Service (UG) | Each | 0.93 | 1.116 | 0.6 | 0.71
Switchgear
|  |  | LV Pillar (ID) | Each | 2.22 | 2.664 | 6.41 | 8.06
|  |  | LV Pillar (OD) | Each |  |  | 6.78 | 8.47
|  |  | LV Board (WM) | Each |  |  | 8.37 | 10.53
|  |  | LV UGB | Each
|  |  | LV Fuses (PM) | Each
|  |  | LV Fuses (TM) | Each
HV network
Overhead lines
|  |  | 6.6/11 kV OHL (Open) | km | 35.26 | 42.312 | 18.35 | 20.82
|  |  | 6.6/11 kV OHL (Covered) | km
|  |  | 20 kV OHL (Open) | km
|  |  | 20 kV OHL (Covered) | km
Overhead lines - Support
|  |  | 6.6/11 kV Support | Each |  |  | 1.52 | 2.05
|  |  | 20 kV Support | Each
Underground cables (kms)
|  |  | 6.6/11kV UG Cable | km | 32.92 | 39.504 | 73.02 | 84.36
|  |  | 20kV UG Cable | km
Submarine cables (kms)
|  |  | HV Sub Cable | km |  |  | 471.36 | 535.69
Switchgear
|  |  | 6.6/11 kV CB (PM) | Each | 7.13 | 8.556 | 7.17 | 8.31
|  |  | 6.6/11 kV CB (GM) | Each | 20.49 | 24.588 | 21.37 | 24.52
|  |  | 6.6/11 kV Switch (PM) | Each | 6.01 | 7.212 | 6.05 | 7.06
|  |  | 6.6/11 kV Switch (GM) | Each | 6.71 | 8.052 | 8.17 | 10.15
|  |  | 6.6/11 kV RMU | Each | 6.99 | 8.388 | 10 | 12.28
|  |  | 6.6/11 kV Switchgear - Other (PM) | Each
|  |  | 6.6/11 kV Switchgear - Other (GM) | Each
|  |  | 20 kV CB (PM) | Each
|  |  | 20 kV CB (GM) | Each
|  |  | 20 kV Switch (PM) | Each
|  |  | 20 kV Switch (GM) | Each
|  |  | 20 kV RMU | Each
|  |  | 20 kV Switchgear - Other (PM) | Each
|  |  | 20 kV Switchgear - Other (GM) | Each
Transformers
|  |  | 6.6/11 kV Transformer (PM) | Each | 1.66 | 1.992 | 1.33 | 1.78
|  |  | 6.6/11 kV Transformer (GM) | Each | 9.32 | 11.184 | 10.86 | 12.82
|  |  | 20 kV Transformer (PM) | Each
|  |  | 20 kV Transformer (GM) | Each
EHV Network
Overhead lines
|  |  | 33kV OHL (Pole Line) | km | 41.59 | 49.908 | 23.76 | 26.88
|  |  | 33kV OHL (Tower Line) | km |  |  | 29.82 | 33.67
|  |  | 66kV OHL (Pole Line) | km | 55.8 | 66.96 | 36.97 | 41.55
|  |  | 66kV OHL (Tower Line) | km |  |  | 46.81 | 52.49
Overhead lines - Support
|  |  | 33kV Pole | Each |  |  | 1.99 | 2.61
|  |  | 33kV Tower | Each |  |  | 39.15 | 45.36
|  |  | 66kV Pole | Each |  |  | 2.74 | 3.61
|  |  | 66kV Tower | Each |  |  | 64.96 | 74.53
Underground cables (kms)
|  |  | 33kV UG Cable (Non Pressurised) | km | 148.69 | 178.428 | 152.89 | 173.04
|  |  | 33kV UG Cable (Oil) | km |  |  | 152.89 | 152.89
|  |  | 33kV UG Cable (Gas) | km |  |  | 152.89 | 173.42
|  |  | 66kV UG Cable (Non Pressurised) | km | 440.09 | 528.108 | 444.45
|  |  | 66kV UG Cable (Oil) | km |  |  | 444.45
|  |  | 66kV UG Cable (Gas) | km |  |  | 444.45
Submarine cables (kms)
|  |  | EHV Sub Cable | km |  |  | 1020.97 | 1134.52
Switchgear
|  |  | 33 KV CB (ID) | Each | 74.24 | 89.088 | 59.25 | 66.58
|  |  | 33 kV CB (OD) | Each | 51.24 | 61.488 | 44.23 | 51.4
|  |  | 33 kV Switch (GM) | Each |  |  | 29.05 | 33.17
|  |  | 33 kV Switch (PM) | Each
|  |  | 33 kV RMU | Each
|  |  | 33 kV Switchgear - Other | Each
|  |  | 66 KV CB (ID & OD) | Each | 77.24 | 92.688 | 77.24 | 88.11
|  |  | 66 KV Switchgear - Other | Each
Transformers
|  |  | 33 kV Transformer (PM) | Each
|  |  | 33 kV Transformer (GM) | Each | 228.25 | 273.9 | 223.81 | 262.73
|  |  | 33 kV AuxiliaryTransfomer | Each
|  |  | 66 kV Transformer | Each | 411.49 | 493.788 | 399.61 | 457.92
|  |  | 66 kV AuxiliaryTransfomer | Each
132kV Network
Overhead lines
|  |  | 132kV OHL Conductor (Pole Line) | km | 74.69 | 89.628 | 52.85 | 52.85
|  |  | 132kV OHL Conductor (Tower Line) | km | 637 | 764.4 | 47.77 | 53.51
Overhead lines - Support
|  |  | 132kV Pole | Each |  |  | 2.61 | 3.64
|  |  | 132kV Tower | Each |  |  | 86.15 | 98.62
|  |  | 132kV Fittings (Tower Line) | Each |  |  | 2.98 | 3.8
Underground cables (kms)
|  |  | 132kV UG Cable (Non Pressurised) | km | 1170.88 | 1405.056 | 1191.4 | 0
|  |  | 132kV UG Cable (Oil) | km |  |  | 1191.4 | 1323.44
|  |  | 132kV UG Cable (Gas) | km
Submarine cables (kms)
|  |  | 132 kV Sub Cable | km
Switchgear
|  |  | 132 kV CB (ID & OD) | Each | 120.95 | 145.14 | 131.08 | 146.88
|  |  | 132 kV Switchgear (other) | Each
Transformers
|  |  | 132 kV Transformer | Each | 975.14 | 1170.168 | 1018.69 | 1139.95
|  |  | 132 kV AuxiliaryTransfomer | Each
Tele-control / SCADA
Primary substation
|  |  | 132 kV/EHV RTU (PM) | Each
|  |  | 132 kV/EHV RTU (GM) | Each
Secondary substation
|  |  | HV RTU (PM) | Each
|  |  | HV RTU (GM) | Each
HV network switchgear
6.6/11 kV CB (GM)
|  |  | Primary | Each | 20.49 | 24.588 | 21.37 | 24.52
|  |  | Distribution | Each | 20.49 | 24.588 | 21.37 | 24.52
20 kV Switch (GM)
|  |  | Primary | Each
|  |  | Distribution | Each

## RRP 1.3
Regulatory Reporting Pack (RRP) |  |  |  | Index |  | CAUTION - THIS PACK DOES NOT BALANCE
2007/08
Electricity Distribution Industry Activity Costs - individual DNO input
|  | Cash typical costs (excluding disallowed related party margins) | [20 empty] | Atypical cash costs | Pension deficit payments | Metering | Excluded services & de minimis | Relevant distributed generation (less contributions) | IFI | Disallowed Related Party Margins | Statutory Depreciation | Network Rates | Transmission Exit Charges | Pension deficit repair payments by related parties (note 2) | Non activity costs and reconciling amounts (note 3) | Total Annual Operating & Capital Expenditure per Regulatory Accounts
|  | Direct activities | [5 empty] | Indirect activities
| Year ended | Load related new connections & reinforcement (net of contributions) | Non-load new & replacement assets (net of contributions) | Non-operational capex | Faults | Inspections, & Maintenance | Tree Cutting | Network Policy | Network Design & Engineering | Project Management | Engineering Mgt & Clerical Support | Control Centre | System Mapping - Cartographical | Customer Call Centre | Stores | Vehicles & Transport | IT & Telecoms | Property Mgt | HR & Non-operational Training | Health & Safety & Operational Training | Finance & Regulation | CEO etc
|  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
| 31 March 2008 | -0.5 | 32.3 | 3 | 8.3 | 5.5 | 4.1 | 0.6 | 3.5 | 2.9 | 7.2 | 1.9 | 1 | 0.7 | 0.9 | 2.7 | 6.8 | 2.1 | 0.9 | 1.1 | 5.8 | 1.8 | 4.3 | 13.4 | 1.8 | 8.9 | -0.1 | 0.1 | -2.7756e-17 | 25.3 | 15.1 | 4.2 | 0 | -2.9 | 162.7
| Adjustments on T4.3 | [33 empty] | 0
| 31 March 2008 | -0.5 | 32.3 | 3 | 8.3 | 5.5 | 4.1 | 0.6 | 3.5 | 2.9 | 7.2 | 1.9 | 1 | 0.7 | 0.9 | 2.7 | 6.8 | 2.1 | 0.9 | 1.1 | 5.8 | 1.8 | 4.3 | 13.4 | 1.8 | 8.9 | -0.1 | 0.1 | -2.7756e-17 | 25.3 | 15.1 | 4.2 | 0 | -2.9 | 162.7
| 31 March 2007 | 2.8 | 25.5 | 4.3 | 8.6 | 5.3 | 2.9 | 0.6 | 3 | 2.2 | 5.2 | 1.9 | 0.8 | 0.6 | 1.6 | 2.8 | 6.3 | 2.1 | 1 | 0.9 | 4.8 | 1.5 | 4.9 | 6.9 | 5.9 | 13.7 | 0.2 | 0 | 0 | 33.9 | 14.6 | 4.2 | 0 | -8.8 | 160.2
| 31 March 2006 | 5.5 | 17.3 | 2.4 | 8.1 | 6.8 | 3.3 | 0.6 | 3.2 | 2.3 | 6.5 | 2.5 | 0.8 | 0.9 | 1.5 | 2.9 | 6.2 | 2.2 | 0.8 | 0.7 | 4 | 1.9 | 1.6 | 4.3 | 5.1 | 5 | 0 | 0 | 0 | 31.3956 | 14.3 | 3.9 | -0.9 | -4.8956 | 140.2
Notes
| 1 | The individual activities are defined in the Electricity Distribution Price Control Review Price control cost reporting rules: Instructions and Guidance April 2008
| 2 | Pension deficit payments made by a related party and not charged in the regulatory accounts of the DNO
| 3 | Non-activity costs include Ofgem licence fee, Shetland Balancing Costs (SHEPD only), Scottish Electricity Settlements run-off (Scottish DNOs only) and proceeds of asset sales; and reconciling amounts, e.g. intra-group recharges treated as de minimis costs
| 4 | Total Annual Operating & Capital Expenditure per Regulatory Accounts has been adjusted, where appropriate, to include intangible fixed assets and customer contributions, the latter may be reported within Creditors as deferred income
| 5 | This information has not been audited.

## RRP 2.3
Regulatory Reporting Pack (RRP) |  |  | Index
2007/08
Inspections & Maintenance, Tree Cutting and Fault Costs
Memorandum Information - Scottish DNOs 132kV
|  |  | Inspections & Maintenance |  |  | Fault Costs |  | Inspections & Maintenance |  |  | Faults
|  |  |  | Cash typicals |  | Cash typicals | Atypicals
Inspection and Maintenance |  |  | Inspections | Maintenance | Total | Total | Total | Inspections | Maintenance | Total | Total
|  |  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
LV Services | Overhead |  | 0.1 | 0.3 | 0.4 | 0.6
| Underground |  |  |  |  | 1.4
LV System | Overhead Mains |  | 0.1 | 0.1 | 0.2 | 0.5
| Underground Mains - Consac |  |  | 0.1 | 0.1
| Underground Mains - Non Consac |  |  |  |  | 2.1
| Switchgear (incl other plant & equipment) |  |  |  |  | 0.3
HV | Overhead lines |  | 0.5 | 0.1 | 0.6 | 0.8
| Underground Cables |  |  |  | 0 | 1.5
| Switchgear, Transformers, Substation |  | 0.1 | 1.5 | 1.6 | 0.2
EHV | Overhead lines |  | 0.1 |  | 0.1 | 0.1
| Underground - Pressure assisted |  |  |  | 0
| Underground - Non Pressure assisted |  |  |  | 0 | 0.3
| Switchgear, Transformers, Substation |  | 0.1 | 0.7 | 0.8 | 0.2
132kV | Overhead lines |  | 0.2 | 0.6 | 0.8
| Underground - Pressure assisted |  |  |  | 0
| Underground - Non Pressure assisted |  |  |  | 0
| Switchgear, Transformers, Substation |  | 0.1 | 0.5 | 0.6
Submarine cables - all voltages
Non-QoS Faults | [5 empty] | 1
Substation electricity |  |  |  | 0.6 | 0.6
Diesel generation costs (permanent emergency back up on islands) |  |  |  | 0.1 | 0.1
Third party cable damage - recoveries | [5 empty] | -0.6
Dismantlement |  |  |  |  | 0
Total |  |  | 1.3 | 4.6 | 5.9 | 8.4
|  |  | Fault costs allocated to Opex and Capex |  |  | Cash typicals | Atypicals
[6 empty] | £'m | £'m
|  |  | Fault opex |  |  | 2.4
|  |  | Fault capex |  |  | 6
|  |  | Total Fault Costs |  |  | 8.4
|  | Tree Cutting | [5 empty] | Tree Cutting
[5 empty] | £'m |  |  |  |  | £'m
|  | LV |  |  | 1.1655 |  |  | 132kV |  | 0.1
|  | HV |  |  | 2.3631
|  | EHV |  |  | 0.48131
|  | 132kV |  |  | 0.14847
|  | Total Tree Cutting |  |  | 4.1584

## RRP 2.4
Regulatory Reporting Pack (RRP) |  |  | Index
2007/08
NEW AND REPLACEMENT ASSETS (EXCL. FAULTS)
Load Related New Connections & Reinforcement
| Direct Costs only |  | New Connections (carried out by DNO/RP) | New Connections (carried out by Third Parties) | Customer Specific Reinforcement - Chargeable | Customer Specific Reinforcement - Non Chargeable | General Reinforcement | Fault Level Reinforcement | Non Relevant Distributed Generation | Total
|  |  | £'m | £'m | £'m | £'m | £'m | £'m | £'m | £'m
New Connections & Customer Specific Reinforcement:
| Connections provided at LV |  | 13.8 |  | 0.9 | 0.8 |  |  |  | 15.5
| Connections provided at HV |  | 2.4 |  | 0.2 | 0.3 |  |  |  | 2.9
| Connections provided at EHV |  | 0.5 |  | 1.1 | 0.6 |  |  |  | 2.2
| Connections provided at 132kV |  | 0 |  | 0 | 0 |  |  |  | 0
| General Reinforcement: | [8 empty] | 0
| LV System | [5 empty] | 0.3 |  |  | 0.3
| HV System | [5 empty] | 0.9 |  |  | 0.9
| EHV System | [5 empty] | 1.4 |  |  | 1.4
| 132kV System | [5 empty] | 1.1 |  |  | 1.1
| Non Relevant Distributed Generation | [8 empty] | 0
| Total Direct Costs excluding Reallocations |  | 16.7 | 0 | 2.2 | 1.7 | 3.7 | 0 | 0 | 24.3
| Direct Cost Reallocation | [8 empty] | 0
| Total Costs including Reallocations |  | 16.7 | 0 | 2.2 | 1.7 | 3.7 | 0 | 0 | 24.3
| Customer Contributions (-ve) |  | -22 |  | -2.8 |  |  |  |  | -24.8
| Total Costs less Capital Contributions |  | -5.3 | 0 | -0.6 | 1.7 | 3.7 | 0 | 0 | -0.5
Non-load related replacement (Condition based)
Condition based
| Direct Costs only |  | Non-fault Related | Fault Related | Total
|  |  | £'m | £'m | £'m
| Metered LV Services | Overhead | 1.5 | 0 | 1.5
|  | Underground | 0.6 | 0 | 0.6
| Un-metered LV Services | Overhead | 0 | 0 | 0
|  | Underground | 0.1 | 0 | 0.1
| LV System | Overhead Mains | 2 | 0 | 2
|  | Underground Mains | 0.2 | 0.1 | 0.3
|  | Switchgear (incl other plant & equipment) | 0.1 | 0 | 0.1
| HV | Overhead lines | 5.6 | 0 | 5.6
|  | Underground Cables | 1.1 | 0 | 1.1
|  | Submarine | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 2.5 | 0.1 | 2.6
|  | Transformers | 0.7 | 0.1 | 0.8
|  | Substation | 0.8 | 0 | 0.8
| EHV | Overhead lines | 1 | 0 | 1
|  | Underground Cables | 0 | 0 | 0
|  | Submarine | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 1.9 | 0 | 1.9
|  | Transformers | 0.8 | 0.2 | 1
|  | Substation | 0.3 | 0 | 0.3
| 132kV | Overhead lines | 2 | 0 | 2
|  | Underground Cables | 0.4 | 0 | 0.4
|  | Submarine Cables | 0 | 0 | 0
|  | Switchgear (incl other plant & equipment) | 0.1 | 0 | 0.1
|  | Transformers | 0.8 | 0 | 0.8
|  | Substation | 0.9 | 0 | 0.9
| Total Non-load replacement |  | 23.4 | 0.5 | 23.9
| Customer Contributions (-ve) |  | -0.3 |  | -0.3
| Total Net Non-load replacement |  | 23.1 | 0.5 | 23.6
| Non-load related (other) |  | LV | HV | EHV | 132kV | Total
| Direct Costs only |  | £'m | £'m | £'m | £'m | £'m
| Quality of Service |  | 0.2 | 3.4 | 0 | 0 | 3.6
| Safety |  | 0 | 0 | 0 | 0 | 0
| Environment |  | 0 | 0 | 0 | 0 | 0
| Visual Amenity |  | 0 | 0 | 0 | 0 | 0
| ESQCR |  | 0 | 0 | 0 | 0 | 0
| Resilience |  | 0 | 0 | 0 | 0 | 0
| Operational IT & Telecoms - BT 21CN |  | 0 | 0 | 0 | 0 | 0
| Operational IT & Telecoms - other |  | 0 | 3.4 | 0 | 0 | 3.4
| Non - rechargeable diversions |  | 0.4 | 0.8 | 0.1 | 0 | 1.3
| Total Non-load related (other non-fault) |  | 0.6 | 7.6 | 0.1 | 0 | 8.3
| Customer Contributions (-ve) | [5 empty] | 0
| Total Net Non-load related (other non-fault) |  | 0.6 | 7.6 | 0.1 | 0 | 8.3
| Total Non-load related expenditure (direct costs) |  | 32.2
| Customer Contributions (-ve) |  | -0.3
| Total Net Non-load replacement (Direct Costs) |  | 31.9
Non-operational
| Direct Costs only |  | Total | Owned by DNO | Owned by related party
|  |  | £'m | £'m | £'m
| Vehicles |  | 0.2 | 0.2 | 0
| Plant & Machinery |  | 0 | 0 | 0
| Small Tools & Equipment |  | 1.3 | 1.3 | 0
| Office Equipment |  | 0.1 | 0.1 | 0
| Non-operational property |  | 0.3 | 0.3 | 0
| IT Non-operational Capital Expenditure |  | 0.6 | 0.6 | 0
| Telecoms Non-operational Capital Expenditures |  | 0.5 | 0 | 0.5
| Total Non-operational New Assets & Replacement |  | 3 | 2.5 | 0.5

## RRP 2.6
Regulatory Reporting Pack |  |  |  | Index
2007/08
MISCELLANEOUS
Non-activity based costs (excluded from Table 2.2)(enter as positive)
[5 empty] | £'m | £'m
Pass through Costs
|  | Transmission exit charges |  |  | 4.2
|  | Wheeled units imported |  |  | 0.2
|  | Network rates |  |  | 15.1
|  | Ofgem licence fee |  |  | 0.5
|  | Shetland Balancing Costs (SHEPD only) |  |  | 0
|  | Scottish Electricity Settlements run-off (Scottish DNOs only) |  |  | 0 | 20
Costs inside scope of DPCR4 allowances
|  | Guaranteed standard of performance compensation payments |  |  | 0
|  | Ex-gratia compensation payments |  |  | 0
|  | Bad debt expense (net of recoveries) |  |  | 0.1 | 0.1
Costs outside scope of DPCR4 allowances
|  | (Profit)/loss on sale of fixed assets and scrap[(-ve)/+ve] |  |  | -0.3
|  | Statutory Depreciation on operational assets |  |  | 17.8
|  | Pension deficit repair payments |  |  | 13.5 | 31
|  |  | Total Non-Activity Based Costs |  |  | 51.1
OTHER ITEMS adjusting RAV
Proceeds of sale of assets and scrap (not recorded on Table 2.2)
|  |  | Cash proceeds received on sale of: |  | £'m
|  |  | Operational assets (-ve) |  | -0.1
|  |  | Sales of scrap (-ve) |  | -0.5
|  |  | Non-operational assets (-ve) |  | 0
|  |  | Total |  | -0.6
|  |  | ANALYSIS OF ASSET DISPOSALS |  | Cost | Depn. | Net Book Value | Net Sales Proceeds | (Profit) / Loss on Disposal | Asset Owner
|  |  | Asset Type |  | £m | £m | £m | £m | £m
[5 empty] | 20.9 | 20.8 | 0.1 | 0.1 | 0
[5 empty] | 1.1 | 0.9 | 0.2 | 0.5 | -0.3
|  |  | Total |  | 22 | 21.7 | 0.3 | 0.6 | -0.3
[8 empty] | OK | OK
|  | Use of System Bad Debts |  |  | £m | £m
previously allowed
|  |  | Costs incurred (excluding VAT) |  | 0.1
Receipts/(recoveries)
|  |  | Total Use of System Bad Debts |  | 0.1
|  | Salary sacrifice schemes (including flexible benefit schemes) |  |  | Total | Direct capex | Direct opex, faults & Non-op capex | Indirect costs | All Other non-distrib'n activities
[5 empty] | £m | £m | £m | £m | £m
Salary element sacrificed by employee(-ve)
Additional employer pension contributions (+ve)
|  | Lane rentals analysis: including logged up costs (see below): |  |  | Total | Load Related New Connections & Reinforcement | Non-load non-fault new & replacement assets | Faults | Inspectns & Maint. (exc. Tree Cutting) | Tree Cutting
[5 empty] | £m | £m | £m | £m | £m | £m
Fines and penalties
Road occupation costs
Permit scheme costs
Congestion charges
Total per Table 2.2
Uncertain Costs (included in table 2.2 costs)
|  | Road Occupation & Permit Scheme Costs included within Lane Rentals, previously agreed in writing with Ofgem to be treated as logged up costs: |  |  | Total | Load Related New Connections & Reinforcement | Non-load non-fault new & replacement assets | Faults | Inspectns & Maint. (exc. Tree Cutting) | Tree Cutting
[5 empty] | £m | £m | £m | £m | £m | £m
Road occupation costs
Permit scheme costs
Congestion charges
Total
Costs previously agreed with Ofgem in writing for additional security
Miscellaneous costs (included in table 2.2 costs)
£m
Pension administration costs (reported in HR & Non-op training)
LV Control centre costs (where it remotely controls LV network)
[5 empty] | £m | km
Expenditure replacing Pressure Assisted cables
|  | Undergrounding in National Parks / AONB - direct costs |  |  | £m | km
LV
HV
EHV/132kV
Undergrounding in National Parks / AONB - indirect costs
Total Undergrounding in National Parks / AONB

## RRP 5.1
Regulatory Reporting Pack (RRP) |  |  |  | Index
2007/08
Network Data
|  | Units | 2005/06 | 2006/07 | 2007/08 | 2008/09 | 2009/10
| QUALITY OF SERVICE |  | Historical data |  |  | For Future years
| Customer Numbers | Millions |  |  | 1.0796
| Total CIs (Excluding EE) | CIs |  |  | 80.6
| Total CMLs (Excluding EE) | CMLs |  |  | 46.3
NETWORK ACTIVITY INDICATORS
CONNECTIONS
Number of new connections
| EHV (Includes 132kV) | No. Connections |  |  | 1
| HV | No. Connections |  |  | 19
| LV | No. Connections |  |  | 10819
| DG | No. Connections |  |  | 1
Total Connected Distributed Generation
| 132kV | MW |  |  | 277.6
| EHV | MW |  |  | 186.7
| HV | MW |  |  | 93.7
| LV | MW |  |  | 12.3
| Total |  | 0 | 0 | 570.3
DEMANDS
| System Maximum Demand | MW |  |  | 2179.2926
| System Maximum Demand (Weather corrected) | MW |  |  | 2179.2926
Units Distributed
| EHV (Includes 132kV) | GWh |  |  | 2954.8379
| HV | GWh |  |  | 2482.1084
| LV | GWh |  |  | 7216.2042
| Total |  | 0 | 0 | 12653.1505
LOSSES
| Units of distribution losses | (GWh) |  |  | 675.237
| Losses | (%) |  |  | 5.337%
SYSTEM PARAMETERS
Distribution Circuit Length - Overhead (km)
| 132kV | Circuit km |  |  | 1180
| EHV | Circuit km |  |  | 1584
| HV | Circuit km |  |  | 12207
| LV | Circuit km |  |  | 3193
| Total | Circuit km | 0 | 0 | 18164
Distribution Circuit Length - Underground (km)
| 132kV | Circuit km |  |  | 93.4
| EHV | Circuit km |  |  | 397.264
| HV | Circuit km |  |  | 5366.7
| LV | Circuit km |  |  | 10735.59
| Total | Circuit km | 0 | 0 | 16592.954
Distribution Circuit Length - Total (km)
| 132kV | Circuit km | 0 | 0 | 1273.4
| EHV | Circuit km | 0 | 0 | 1981.264
| HV | Circuit km | 0 | 0 | 17573.7
| LV | Circuit km | 0 | 0 | 13928.59
| Total | Circuit km | 0 | 0 | 34756.954
Number of Substations and Switching Stations
| 132kV | No. Subs |  |  | 77
| EHV ground mounted | No. Subs |  |  | 196
| EHV pole mounted | No. Subs |  |  | 0
| HV ground mounted | No. Subs |  |  | 8329
| HV pole mounted | No. Subs |  |  | 31138
| Total | No. Subs | 0 | 0 | 39740