## Metadata
Data Dictionary
Column Heading | Description
Associated GSP Group | Name of the upstream Grid Supply Point (GSP) group which supplies the substation. Note that multiple GSPs can run in parallel so are therefore reported as groups.
Bulk Supply Point | Name of the upstream Bulk Supply Point (BSP) which supplies the substation.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'Network Headroom Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Latitude | Latitude and longitude of the location of the substation.
Longitude
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) or WPD Best View scenario the headroom figures refer to
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below)
Limiting constraint | For generation headroom worksheet only. Identifier for the limiting factor (either thermal or fault level) that triggers the constraint when the generation headroom falls below zero.
2020 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the calendar year
2021
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2040
2045
2050

## Demand headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Consumer Transformation | Thermal headroom (MW) | 53.4077 | 50.6758 | 47.6854 | 44.5824 | 40.318 | 35.1176 | 26.8282 | 16.8744 | 5.2778 | -8.2629 | -22.9513 | -40.8151 | -59.2237 | -78.2075 | -97.3602 | -116.0385 | -184.5616 | -208.9201 | -211.5694
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Leading the Way | Thermal headroom (MW) | 53.0559 | 49.9696 | 46.8921 | 43.2153 | 39.1926 | 33.7777 | 25.3989 | 14.9797 | 1.7557 | -13.0424 | -30.2662 | -49.1747 | -69.1239 | -89.2355 | -108.7782 | -126.1497 | -169.5839 | -169.6305 | -140.9571
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Steady Progression | Thermal headroom (MW) | 54.1518 | 53.2403 | 52.8314 | 51.9514 | 50.971 | 49.6134 | 48.1116 | 46.1594 | 43.7013 | 40.6085 | 36.3765 | 30.6725 | 24.3268 | 16.8817 | 8.4684 | -1.4466 | -66.7764 | -129.5003 | -145.0199
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | System Transformation | Thermal headroom (MW) | 53.7726 | 52.4477 | 51.3218 | 50.1633 | 48.5942 | 46.9161 | 44.5478 | 41.4675 | 36.9663 | 31.4551 | 24.0931 | 14.6857 | 3.8942 | -9.091 | -23.5205 | -39.2874 | -123.0731 | -160.9857 | -159.6819
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | WPD Best View | Thermal headroom (MW) | 53.4003 | 50.6366 | 47.5986 | 44.4476 | 40.1402 | 34.8786 | 26.5877 | 16.6264 | 5.0373 | -8.5087 | -23.1845 | -41.021 | -59.4253 | -78.3887 | -97.5334 | -116.1622 | -184.5271 | -208.7892 | -211.3068
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Consumer Transformation | Thermal headroom (MW) | 0.5329 | 0.23241 | -0.15975 | -0.66378 | -1.3125 | -2.1737 | -3.3144 | -4.6402 | -6.2358 | -8.0176 | -10.0237 | -12.4199 | -14.9548 | -17.6361 | -20.2376 | -22.8011 | -32.018 | -35.0517 | -35.2566
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Leading the Way | Thermal headroom (MW) | 0.52789 | 0.19364 | -0.16942 | -0.70861 | -1.3708 | -2.3126 | -3.4694 | -4.8604 | -6.6316 | -8.7178 | -11.1202 | -13.7767 | -16.6546 | -19.5669 | -22.3469 | -24.7562 | -30.6615 | -30.2338 | -26.1021
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Steady Progression | Thermal headroom (MW) | 0.60549 | 0.48633 | 0.38464 | 0.17297 | -0.035585 | -0.34919 | -0.67074 | -1.0963 | -1.5953 | -2.18 | -2.8667 | -3.705 | -4.665 | -5.7999 | -7.0768 | -8.4996 | -18.2416 | -27.2204 | -29.4332
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | System Transformation | Thermal headroom (MW) | 0.58885 | 0.42602 | 0.26692 | 0.034173 | -0.28306 | -0.61823 | -1.0956 | -1.6637 | -2.3995 | -3.2836 | -4.3966 | -5.7184 | -7.3489 | -9.2603 | -11.4048 | -13.7695 | -26.0382 | -31.3284 | -31.0321
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | WPD Best View | Thermal headroom (MW) | 0.5329 | 0.23241 | -0.15975 | -0.66378 | -1.3125 | -2.1737 | -3.3144 | -4.6402 | -6.2358 | -8.0176 | -10.0237 | -12.4199 | -14.9548 | -17.6361 | -20.2376 | -22.8011 | -32.018 | -35.0517 | -35.2566
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Consumer Transformation | Thermal headroom (MW) | 8.8671 | 8.0594 | 7.3724 | 7.3431 | 7.2521 | 7.0239 | 6.5937 | 6.2648 | 5.953 | 5.667 | 5.3161 | 4.9386 | 4.5631 | 4.1915 | 3.8387 | 3.4814 | 2.377 | 2.3151 | 2.7587
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Leading the Way | Thermal headroom (MW) | 8.688 | 7.6245 | 6.6746 | 6.6693 | 6.5758 | 6.445 | 6.1614 | 5.8618 | 5.6145 | 5.3594 | 4.9995 | 4.6669 | 4.3109 | 3.9386 | 3.6017 | 3.3169 | 2.8304 | 3.3877 | 4.496
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Steady Progression | Thermal headroom (MW) | 9.033 | 8.5001 | 8.1035 | 8.1475 | 8.1568 | 8.1101 | 8.0963 | 8.0362 | 7.986 | 7.9541 | 7.8667 | 7.7771 | 7.6929 | 7.5658 | 7.4348 | 7.2839 | 6.2433 | 4.891 | 4.9155
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | System Transformation | Thermal headroom (MW) | 8.8937 | 8.149 | 7.5248 | 7.5818 | 7.5846 | 7.5664 | 7.4011 | 7.2807 | 7.1617 | 7.0975 | 6.9505 | 6.8264 | 6.6257 | 6.4119 | 6.1352 | 5.8566 | 4.519 | 4.0771 | 4.6048
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | WPD Best View | Thermal headroom (MW) | 8.8671 | 8.0594 | 7.3724 | 7.3431 | 7.2521 | 7.0239 | 6.5937 | 6.2648 | 5.953 | 5.667 | 5.3161 | 4.9386 | 4.5631 | 4.1915 | 3.8387 | 3.4814 | 2.377 | 2.3151 | 2.7587
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Consumer Transformation | Thermal headroom (MW) | 9.3608 | 9.0399 | 8.7631 | 8.4344 | 7.7156 | 7.3356 | 6.6264 | 5.3316 | 3.8405 | 2.1878 | 0.39304 | -2.2437 | -4.6107 | -6.9777 | -9.761 | -12.217 | -22.0856 | -26.3114 | -27.4133
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Leading the Way | Thermal headroom (MW) | 9.3154 | 8.9589 | 8.7537 | 8.075 | 7.743 | 7.3914 | 6.6573 | 5.3426 | 3.726 | 1.9 | -0.13804 | -2.7009 | -5.0483 | -7.3893 | -10.053 | -12.1534 | -18.5322 | -20.1633 | -17.0613
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Steady Progression | Thermal headroom (MW) | 9.4523 | 9.4652 | 9.5978 | 9.5777 | 9.5752 | 9.6028 | 9.6186 | 9.5981 | 9.5508 | 9.492 | 9.3919 | 8.68 | 8.0513 | 7.2858 | 6.407 | 5.4145 | -1.8043 | -9.4175 | -11.7539
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | System Transformation | Thermal headroom (MW) | 9.3955 | 9.3589 | 9.4022 | 9.3875 | 9.3412 | 9.3426 | 9.2554 | 9.1452 | 8.653 | 8.4621 | 7.7878 | 6.865 | 5.75 | 4.0737 | 2.5402 | 0.8853 | -9.0531 | -14.2971 | -14.8103
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | WPD Best View | Thermal headroom (MW) | 9.3608 | 9.0399 | 8.7631 | 8.4344 | 7.7156 | 7.3356 | 6.6264 | 5.3316 | 3.8405 | 2.1878 | 0.39304 | -2.2437 | -4.6107 | -6.9777 | -9.761 | -12.217 | -22.0856 | -26.3114 | -27.4133
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Consumer Transformation | Thermal headroom (MW) | 3.2087 | 2.9306 | 2.5717 | 2.1499 | 1.5441 | 0.76497 | -0.2584 | -1.4896 | -2.9907 | -4.703 | -6.585 | -8.8585 | -11.2858 | -13.794 | -16.2826 | -18.727 | -27.5077 | -30.448 | -30.6817
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Leading the Way | Thermal headroom (MW) | 3.2082 | 2.9371 | 2.6026 | 2.1428 | 1.5352 | 0.74095 | -0.31379 | -1.6321 | -3.3091 | -5.264 | -7.5766 | -10.0917 | -12.829 | -15.5741 | -18.226 | -20.5198 | -26.1008 | -25.7446 | -21.7987
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Steady Progression | Thermal headroom (MW) | 3.2876 | 3.1791 | 3.1396 | 3.0052 | 2.8309 | 2.5689 | 2.2862 | 1.9345 | 1.468 | 0.94948 | 0.29504 | -0.49405 | -1.4091 | -2.4603 | -3.662 | -4.9996 | -14.1952 | -22.7539 | -24.838
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | System Transformation | Thermal headroom (MW) | 3.2772 | 3.171 | 3.0594 | 2.8893 | 2.6194 | 2.3046 | 1.9238 | 1.3706 | 0.6804 | -0.15266 | -1.1803 | -2.4704 | -3.9929 | -5.7799 | -7.8164 | -10.0619 | -21.6517 | -26.6961 | -26.3954
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | WPD Best View | Thermal headroom (MW) | 3.2087 | 2.9306 | 2.5717 | 2.1499 | 1.5441 | 0.76497 | -0.2584 | -1.4896 | -2.9907 | -4.703 | -6.585 | -8.8585 | -11.2858 | -13.794 | -16.2826 | -18.727 | -27.5077 | -30.448 | -30.6817
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Consumer Transformation | Thermal headroom (MW) | 12.8124 | 12.7431 | 12.6638 | 12.5022 | 12.2756 | 11.9626 | 11.5348 | 10.9626 | 10.3223 | 9.5769 | 8.6837 | 7.654 | 6.5661 | 5.4208 | 4.2637 | 3.1436 | -0.92556 | -2.2344 | -2.2074
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Leading the Way | Thermal headroom (MW) | 12.8156 | 12.7539 | 12.6989 | 12.4895 | 12.2751 | 11.9371 | 11.466 | 10.8447 | 10.1081 | 9.2441 | 8.1933 | 7.0224 | 5.7791 | 4.5014 | 3.3135 | 2.2416 | -0.31556 | -0.024792 | 1.9676
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Steady Progression | Thermal headroom (MW) | 12.8382 | 12.8667 | 12.9266 | 12.9252 | 12.9012 | 12.8367 | 12.7164 | 12.6154 | 12.4542 | 12.2446 | 11.9884 | 11.661 | 11.2669 | 10.8372 | 10.3247 | 9.7611 | 5.6309 | 1.775 | 0.91068
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | System Transformation | Thermal headroom (MW) | 12.8296 | 12.854 | 12.9018 | 12.8547 | 12.8074 | 12.6772 | 12.5447 | 12.3149 | 12.0764 | 11.7251 | 11.279 | 10.7345 | 10.091 | 9.2907 | 8.3819 | 7.3882 | 2.0855 | -0.14156 | 0.1361
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | WPD Best View | Thermal headroom (MW) | 12.8124 | 12.7431 | 12.6638 | 12.5022 | 12.2756 | 11.9626 | 11.5348 | 10.9626 | 10.3223 | 9.5769 | 8.6837 | 7.654 | 6.5661 | 5.4208 | 4.2637 | 3.1436 | -0.92556 | -2.2344 | -2.2074
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Consumer Transformation | Thermal headroom (MW) | 2.6932 | 2.1779 | 1.6075 | 0.9869 | 0.26335 | -0.54903 | -2.5345 | -4.7081 | -7.1708 | -10.2107 | -13.223 | -16.8764 | -20.6463 | -24.4141 | -28.2209 | -31.9956 | -46.1343 | -51.5594 | -52.3572
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Leading the Way | Thermal headroom (MW) | 2.4873 | 1.8834 | 1.1771 | 0.44484 | -0.40272 | -1.3914 | -3.3918 | -5.6522 | -8.617 | -11.5854 | -14.9144 | -18.456 | -22.2359 | -26.0051 | -29.6199 | -33.1536 | -42.038 | -42.7234 | -37.4821
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Steady Progression | Thermal headroom (MW) | 2.9091 | 2.7759 | 2.6923 | 2.4907 | 2.2295 | 2.0976 | 1.9261 | 1.7301 | 1.48 | 1.0514 | 0.18402 | -0.8909 | -2.0778 | -3.4729 | -4.9983 | -7.1034 | -19.0129 | -30.7416 | -33.5214
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | System Transformation | Thermal headroom (MW) | 2.7322 | 2.4885 | 2.2274 | 1.9155 | 1.5573 | 1.3482 | 1.0873 | 0.75758 | 0.057671 | -1.0594 | -2.467 | -4.4927 | -6.5346 | -8.839 | -11.4713 | -14.3143 | -29.8252 | -37.1432 | -37.1177
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | WPD Best View | Thermal headroom (MW) | 2.6797 | 2.1066 | 1.45 | 0.7422 | -0.059246 | -0.98289 | -2.971 | -5.1582 | -7.6073 | -10.6569 | -13.6463 | -17.25 | -21.0123 | -24.743 | -28.5352 | -32.2201 | -46.0717 | -51.3218 | -51.8806
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Consumer Transformation | Thermal headroom (MW) | 8.5139 | 8.2729 | 7.9988 | 7.4932 | 7.0001 | 6.2985 | 4.6183 | 2.7029 | 0.55556 | -2.3345 | -5.2136 | -8.5467 | -11.9599 | -15.4256 | -18.889 | -22.3899 | -35.339 | -40.58 | -41.6747
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Leading the Way | Thermal headroom (MW) | 8.4816 | 8.2573 | 8.0226 | 7.4857 | 6.9876 | 6.2907 | 4.5542 | 2.5565 | -0.19391 | -2.9979 | -6.275 | -9.6442 | -13.1457 | -16.6741 | -20.0138 | -23.3395 | -31.555 | -32.4957 | -28.1187
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Steady Progression | Thermal headroom (MW) | 8.5916 | 8.6551 | 8.7731 | 8.645 | 8.5728 | 8.5188 | 8.4529 | 8.328 | 8.1797 | 7.7823 | 7.0244 | 6.0531 | 4.9822 | 3.7057 | 2.2916 | 0.32236 | -10.6528 | -21.6378 | -24.6332
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | System Transformation | Thermal headroom (MW) | 8.5453 | 8.5878 | 8.6245 | 8.4199 | 8.2743 | 8.1582 | 8.011 | 7.786 | 7.2097 | 6.1838 | 4.8654 | 2.9617 | 1.1458 | -1.0054 | -3.4529 | -6.0971 | -20.3162 | -27.3846 | -27.7886
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | WPD Best View | Thermal headroom (MW) | 8.5139 | 8.2729 | 7.9988 | 7.4932 | 7.0001 | 6.2985 | 4.6183 | 2.7029 | 0.55556 | -2.3345 | -5.2136 | -8.5467 | -11.9599 | -15.4256 | -18.889 | -22.3899 | -35.339 | -40.58 | -41.6747
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Consumer Transformation | Thermal headroom (MW) | 57.3974 | 56.7391 | 56.2714 | 55.2389 | 54.1391 | 51.8524 | 49.1875 | 45.9307 | 41.6932 | 36.6526 | 32.33 | 27.157 | 21.8637 | 16.8471 | 11.7794 | 6.3337 | -14.694 | -22.6188 | -23.1033
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Leading the Way | Thermal headroom (MW) | 56.9639 | 56.1786 | 55.9497 | 54.8433 | 53.7255 | 51.3826 | 48.8249 | 45.1951 | 39.445 | 34.7864 | 29.8561 | 24.8223 | 19.8735 | 14.9886 | 10.0843 | 4.6841 | -8.0436 | -8.816 | -1.3466
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Steady Progression | Thermal headroom (MW) | 57.8791 | 58.0089 | 58.5912 | 58.3537 | 58.2697 | 57.9318 | 57.7139 | 57.0271 | 56.3308 | 55.8403 | 55.1965 | 54.2988 | 52.9777 | 51.0439 | 48.8461 | 45.5522 | 29.4944 | 13.2642 | 9.0251
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | System Transformation | Thermal headroom (MW) | 57.4867 | 57.5105 | 57.813 | 57.5415 | 57.25 | 56.6425 | 55.9016 | 54.4917 | 53.1907 | 52.1281 | 50.96 | 47.5671 | 44.6398 | 41.2642 | 37.5428 | 33.6048 | 13.514 | 3.9347 | 4.1007
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | WPD Best View | Thermal headroom (MW) | 57.3974 | 56.7391 | 56.2714 | 55.2389 | 54.1391 | 51.8524 | 49.1875 | 45.9086 | 41.6932 | 36.6526 | 32.33 | 27.157 | 21.8637 | 16.7834 | 11.6982 | 6.3337 | -14.694 | -22.6188 | -23.1033
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Consumer Transformation | Thermal headroom (MW) | 9.4398 | 9.382 | 9.4103 | 9.336 | 9.2442 | 9.0958 | 8.7183 | 8.3474 | 7.9515 | 7.5528 | 7.0868 | 6.4866 | 5.9569 | 5.4635 | 5.0631 | 4.3956 | 0.61322 | -1.5164 | -2.4514
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Leading the Way | Thermal headroom (MW) | 9.4383 | 9.3802 | 9.4448 | 9.3884 | 9.3098 | 9.1677 | 8.7855 | 8.4336 | 8.0262 | 7.5926 | 7.1121 | 6.6996 | 6.3604 | 6.1269 | 5.803 | 5.1291 | 2.4702 | 1.0342 | 1.8968
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Steady Progression | Thermal headroom (MW) | 9.4732 | 9.5747 | 9.7988 | 9.8878 | 9.9637 | 10.0429 | 10.1078 | 10.1535 | 10.1898 | 10.2092 | 10.1741 | 10.0587 | 9.9306 | 9.7708 | 9.5877 | 9.394 | 8.2064 | 7.2737 | 6.9136
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | System Transformation | Thermal headroom (MW) | 9.4614 | 9.5496 | 9.7463 | 9.82 | 9.8882 | 9.9519 | 9.957 | 9.9526 | 9.916 | 9.8354 | 9.6845 | 9.4751 | 9.2285 | 8.949 | 8.6466 | 8.352 | 7.185 | 6.4637 | 6.4843
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | WPD Best View | Thermal headroom (MW) | 9.4398 | 9.382 | 9.4103 | 9.336 | 9.2442 | 9.0958 | 8.7183 | 8.3474 | 7.9515 | 7.5528 | 7.0868 | 6.4866 | 5.9569 | 5.4635 | 5.0631 | 4.3956 | 0.61322 | -1.5164 | -2.4514
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Consumer Transformation | Thermal headroom (MW) | 10.1603 | 9.9576 | 9.8247 | 9.606 | 9.434 | 8.8912 | 8.2933 | 7.3709 | 5.908 | 4.2282 | 2.8884 | 1.2419 | -0.49789 | -2.2065 | -3.9124 | -5.6405 | -12.0236 | -14.3277 | -14.3687
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Leading the Way | Thermal headroom (MW) | 9.9558 | 9.7385 | 9.6365 | 9.4043 | 9.2729 | 8.7734 | 8.2943 | 7.2242 | 5.1049 | 3.6103 | 2.0176 | 0.21038 | -1.5942 | -3.3818 | -5.0793 | -6.9207 | -10.793 | -10.5825 | -8.2753
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Steady Progression | Thermal headroom (MW) | 10.3523 | 10.3306 | 10.4233 | 10.363 | 10.3993 | 10.3519 | 10.3151 | 10.0515 | 9.7836 | 9.66 | 9.5281 | 9.3146 | 8.9294 | 8.2691 | 7.5085 | 6.3083 | 0.57932 | -5.722 | -7.4407
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | System Transformation | Thermal headroom (MW) | 10.183 | 10.1334 | 10.1685 | 10.1106 | 10.1086 | 10.0112 | 9.8336 | 9.3158 | 8.8204 | 8.5773 | 8.3397 | 7.1122 | 6.1051 | 4.91 | 3.5899 | 2.1687 | -5.3926 | -9.1249 | -9.31
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | WPD Best View | Thermal headroom (MW) | 10.1603 | 9.9576 | 9.8247 | 9.606 | 9.434 | 8.8912 | 8.2933 | 7.3709 | 5.908 | 4.2282 | 2.8884 | 1.2419 | -0.49789 | -2.2065 | -3.9124 | -5.6405 | -12.0236 | -14.3277 | -14.3687
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Consumer Transformation | Thermal headroom (MW) | 17.7855 | 17.5245 | 17.2161 | 16.7201 | 16.2489 | 15.1334 | 14.0353 | 12.8846 | 11.6378 | 9.7287 | 8.1088 | 6.2312 | 4.2084 | 2.267 | 0.25352 | -1.6466 | -8.7143 | -11.059 | -10.7353
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Leading the Way | Thermal headroom (MW) | 17.7125 | 17.3403 | 17.1562 | 16.6054 | 16.1148 | 14.9463 | 13.87 | 12.6769 | 10.988 | 9.295 | 7.4644 | 5.666 | 3.7535 | 1.782 | -0.091511 | -2.029 | -6.0881 | -5.7947 | -2.9384
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Steady Progression | Thermal headroom (MW) | 17.8921 | 17.9349 | 18.0692 | 17.929 | 17.883 | 17.6653 | 17.576 | 17.433 | 17.2 | 16.9304 | 16.5225 | 16.1107 | 15.6218 | 14.9892 | 14.275 | 13.1019 | 7.3181 | 1.4912 | 0.33943
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | System Transformation | Thermal headroom (MW) | 17.808 | 17.793 | 17.7892 | 17.6523 | 17.5535 | 17.1917 | 16.9811 | 16.6635 | 16.3183 | 15.7205 | 15.0853 | 13.931 | 12.9959 | 11.8715 | 10.5996 | 9.2042 | 1.3731 | -2.2137 | -1.9955
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | WPD Best View | Thermal headroom (MW) | 17.7855 | 17.5245 | 17.2161 | 16.7201 | 16.2489 | 15.1334 | 14.0353 | 12.8846 | 11.6378 | 9.7287 | 8.1088 | 6.2312 | 4.2084 | 2.267 | 0.25352 | -1.6466 | -8.7143 | -11.059 | -10.7353
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Consumer Transformation | Thermal headroom (MW) | 50.6643 | 48.1756 | 44.5558 | 38.7551 | 33.4607 | 24.8846 | 14.0162 | 2.8017 | -9.0818 | -22.8458 | -36.0891 | -53.1987 | -68.7309 | -83.9967 | -99.3942 | -114.1443 | -175.5786 | -193.4925 | -192.2098
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Leading the Way | Thermal headroom (MW) | 50.5046 | 47.7869 | 42.7454 | 37.4907 | 32.0042 | 23.1069 | 11.5424 | -0.86137 | -15.6672 | -28.7145 | -43.2935 | -60.1991 | -75.0851 | -90.0971 | -104.4528 | -118.6069 | -156.3507 | -154.9393 | -135.6046
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Steady Progression | Thermal headroom (MW) | 51.2409 | 50.8319 | 50.0731 | 48.2459 | 44.9567 | 42.5037 | 39.3225 | 35.4389 | 31.092 | 26.3635 | 21.2866 | 15.0792 | 9.1054 | 2.5362 | -4.4149 | -13.6214 | -58.7745 | -104.2378 | -115.5827
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | System Transformation | Thermal headroom (MW) | 50.9857 | 50.2757 | 48.6507 | 44.9068 | 42.4094 | 38.8238 | 33.8481 | 28.14 | 21.8937 | 15.2077 | 7.6122 | -3.3285 | -12.0825 | -21.7321 | -31.9027 | -42.1292 | -103.6559 | -131.4649 | -131.6518
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | WPD Best View | Thermal headroom (MW) | 50.667 | 48.1827 | 44.5713 | 38.773 | 33.486 | 24.9178 | 14.0607 | 2.8724 | -8.9962 | -22.7516 | -35.9795 | -53.0663 | -68.5932 | -83.8984 | -99.2958 | -114.1659 | -175.4284 | -193.2148 | -191.7512
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Consumer Transformation | Thermal headroom (MW) | 12.8969 | 12.5785 | 12.1816 | 11.5831 | 10.7875 | 9.6145 | 8.2344 | 6.8621 | 5.4721 | 3.6227 | 2.1493 | -0.11967 | -2.5305 | -4.9257 | -7.3224 | -9.6578 | -18.3624 | -21.404 | -21.4727
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Leading the Way | Thermal headroom (MW) | 12.8913 | 12.6094 | 12.2281 | 11.5967 | 10.7878 | 9.6047 | 8.1986 | 6.7996 | 4.9797 | 3.4088 | 1.5885 | -0.82997 | -3.231 | -5.6418 | -7.9735 | -10.3564 | -15.6952 | -15.6765 | -12.906
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Steady Progression | Thermal headroom (MW) | 12.9743 | 12.9697 | 12.9517 | 12.8282 | 12.6122 | 12.32 | 11.9758 | 11.5822 | 11.1255 | 10.5721 | 9.9519 | 9.2124 | 8.4422 | 7.5771 | 6.645 | 5.2766 | -0.36263 | -7.6987 | -9.6286
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | System Transformation | Thermal headroom (MW) | 12.9498 | 12.9236 | 12.8458 | 12.6345 | 12.3282 | 11.8974 | 11.4135 | 10.8252 | 10.1339 | 9.3171 | 8.3473 | 6.8835 | 5.7206 | 4.4574 | 3.1199 | 1.7092 | -7.2497 | -11.9526 | -12.2176
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | WPD Best View | Thermal headroom (MW) | 12.8969 | 12.5785 | 12.1816 | 11.5831 | 10.7875 | 9.6145 | 8.2344 | 6.8621 | 5.4721 | 3.6227 | 2.1493 | -0.11967 | -2.5305 | -4.9257 | -7.3224 | -9.6578 | -18.3624 | -21.404 | -21.4727
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Consumer Transformation | Thermal headroom (MW) | 12.448 | 12.3452 | 12.1066 | 11.6698 | 11.2973 | 10.6547 | 9.9511 | 9.2239 | 8.3715 | 7.4846 | 6.4158 | 5.0295 | 3.8391 | 2.6608 | 1.5171 | 0.38621 | -4.2532 | -5.4103 | -5.2781
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Leading the Way | Thermal headroom (MW) | 12.4492 | 12.3552 | 11.9038 | 11.6166 | 11.2051 | 10.5338 | 9.8114 | 9.0146 | 8.0979 | 7.1406 | 5.9617 | 4.5663 | 3.3471 | 2.2019 | 1.1326 | 0.1899 | -2.8044 | -2.5941 | -1.0819
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Steady Progression | Thermal headroom (MW) | 12.473 | 12.4475 | 12.3531 | 12.251 | 11.8774 | 11.672 | 11.4621 | 11.1977 | 10.8849 | 10.5024 | 10.0843 | 9.6005 | 9.1462 | 8.6467 | 8.1205 | 7.5604 | 4.0739 | 0.65865 | -0.20888
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | System Transformation | Thermal headroom (MW) | 12.4679 | 12.4333 | 12.3047 | 11.9719 | 11.7499 | 11.4763 | 11.1634 | 10.8074 | 10.3702 | 9.8513 | 9.2501 | 8.5231 | 7.8843 | 7.1873 | 6.4433 | 5.7106 | 0.84269 | -1.2122 | -1.1302
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | WPD Best View | Thermal headroom (MW) | 12.448 | 12.3452 | 12.1066 | 11.6698 | 11.2973 | 10.6547 | 9.9511 | 9.2239 | 8.3715 | 7.4846 | 6.4158 | 5.0295 | 3.8391 | 2.6608 | 1.5171 | 0.38621 | -4.2532 | -5.4103 | -5.2781
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Consumer Transformation | Thermal headroom (MW) | 11.0921 | 10.6859 | 10.1692 | 9.4158 | 8.9522 | 8.1866 | 6.6893 | 5.056 | 3.6236 | 1.8005 | 0.68078 | -0.49793 | -1.367 | -2.1375 | -2.7929 | -3.4873 | -7.8953 | -9.2259 | -8.8409
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Leading the Way | Thermal headroom (MW) | 11.0096 | 10.5426 | 9.9137 | 8.9898 | 8.4767 | 7.7043 | 5.9169 | 3.9458 | 1.529 | 0.3088 | -0.7893 | -1.6657 | -2.0921 | -2.755 | -3.5348 | -4.9069 | -7.2401 | -6.8611 | -5.9995
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Steady Progression | Thermal headroom (MW) | 11.2068 | 11.0446 | 10.8679 | 10.4843 | 10.3178 | 10.0987 | 9.4757 | 8.7313 | 8.1396 | 7.6437 | 7.1101 | 6.4799 | 5.858 | 5.2021 | 4.5379 | 3.1331 | -0.40893 | -3.3644 | -3.8477
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | System Transformation | Thermal headroom (MW) | 11.1258 | 10.8772 | 10.5745 | 10.0372 | 9.8201 | 9.5418 | 8.5349 | 7.3945 | 6.4888 | 5.8252 | 5.0573 | 3.3841 | 2.4833 | 1.5666 | 0.71727 | -0.090868 | -3.9888 | -5.1528 | -5.5321
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | WPD Best View | Thermal headroom (MW) | 11.0921 | 10.6869 | 10.1717 | 9.4153 | 8.9512 | 8.1839 | 6.6863 | 5.0475 | 3.6118 | 1.7833 | 0.66578 | -0.5022 | -1.3508 | -2.1294 | -2.7937 | -3.5788 | -7.8835 | -9.095 | -8.582
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Consumer Transformation | Thermal headroom (MW) | 4.3413 | 3.6765 | 3.1927 | 2.7571 | 2.2187 | 1.5135 | 0.36657 | -0.81867 | -2.1926 | -4.106 | -5.9234 | -8.1076 | -10.7915 | -13.1242 | -15.8796 | -18.2557 | -28.1292 | -32.2073 | -33.1166
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Leading the Way | Thermal headroom (MW) | 4.2972 | 3.3843 | 3.2136 | 2.8037 | 2.2677 | 1.5614 | 0.46546 | -0.77489 | -2.6319 | -4.439 | -6.4882 | -9.0806 | -11.4385 | -14.1818 | -16.4852 | -18.9039 | -24.8929 | -25.8769 | -22.663
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Steady Progression | Thermal headroom (MW) | 4.4309 | 4.4591 | 4.6517 | 4.3805 | 4.343 | 4.241 | 4.1402 | 3.9801 | 3.392 | 3.0732 | 2.6836 | 2.151 | 1.5084 | 0.74988 | -0.12083 | -1.4573 | -9.2597 | -16.8296 | -18.8248
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | System Transformation | Thermal headroom (MW) | 4.3787 | 4.3774 | 4.2521 | 4.1987 | 4.084 | 3.6105 | 3.3708 | 3.0413 | 2.5907 | 2.0289 | 1.2907 | 0.029855 | -1.0976 | -2.456 | -4.357 | -6.447 | -16.6688 | -22.0696 | -22.1203
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | WPD Best View | Thermal headroom (MW) | 4.3413 | 3.6765 | 3.1927 | 2.7571 | 2.2187 | 1.5135 | 0.36657 | -0.81867 | -2.1926 | -4.106 | -5.9234 | -8.1076 | -10.7915 | -13.1242 | -15.8796 | -18.2557 | -28.1292 | -32.2073 | -33.1166
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Consumer Transformation | Thermal headroom (MW) | 82.5607 | 80.8321 | 78.002 | 76.4305 | 73.2189 | 69.8462 | 66.5486 | 63.4117 | 60.1449 | 56.2714 | 52.9821 | 48.4634 | 44.7125 | 41.0505 | 36.4573 | 33.0908 | 16.766 | 11.7874 | 13.5308
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Leading the Way | Thermal headroom (MW) | 82.4248 | 79.5805 | 77.4472 | 74.5286 | 72.5222 | 68.8846 | 65.4038 | 62.0949 | 58.1038 | 54.427 | 50.9776 | 45.9902 | 42.3668 | 39.0017 | 34.0934 | 30.5034 | 21.9817 | 22.4466 | 27.463
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Steady Progression | Thermal headroom (MW) | 82.9584 | 82.482 | 82.0959 | 80.9098 | 80.3912 | 79.2902 | 78.4081 | 77.4336 | 76.303 | 74.9835 | 73.5082 | 70.3344 | 68.3081 | 66.0938 | 63.7473 | 61.0584 | 47.0586 | 35.2653 | 31.0704
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | System Transformation | Thermal headroom (MW) | 82.7345 | 81.892 | 80.1646 | 79.5829 | 78.7522 | 77.1655 | 75.5978 | 73.9214 | 70.7421 | 68.5196 | 66.0743 | 62.774 | 59.6093 | 55.0208 | 51.7507 | 48.7048 | 32.1276 | 25.279 | 24.754
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | WPD Best View | Thermal headroom (MW) | 82.9272 | 82.4047 | 81.8298 | 80.5859 | 79.9259 | 78.6286 | 77.5369 | 76.3235 | 74.9155 | 72.8701 | 71.2066 | 67.9273 | 65.9281 | 63.7523 | 61.564 | 59.5637 | 46.8885 | 37.0336 | 33.2647
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Consumer Transformation | Thermal headroom (MW) | 11.2088 | 10.3107 | 8.4135 | 7.8694 | 6.8502 | 5.144 | 3.7241 | 2.3588 | 0.96217 | -0.50331 | -1.9287 | -3.6649 | -5.3628 | -7.2131 | -9.3686 | -10.6349 | -15.3895 | -15.6764 | -13.9793
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Leading the Way | Thermal headroom (MW) | 11.1791 | 9.2311 | 7.9112 | 6.9592 | 6.2326 | 4.2826 | 2.6929 | 1.124 | -0.46133 | -2.0943 | -3.7347 | -6.0359 | -8.011 | -9.9509 | -12.0905 | -12.9777 | -14.4885 | -13.0862 | -11.146
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Steady Progression | Thermal headroom (MW) | 11.3314 | 10.9146 | 10.448 | 9.4764 | 9.2341 | 8.486 | 7.9909 | 7.4575 | 6.8639 | 6.2025 | 5.5014 | 4.3056 | 3.43 | 2.4853 | 1.5338 | 0.76049 | -3.4991 | -7.1858 | -8.5556
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | System Transformation | Thermal headroom (MW) | 11.2611 | 10.6114 | 9.0395 | 8.7815 | 8.4283 | 7.3985 | 6.5277 | 5.6313 | 4.3128 | 3.248 | 2.1381 | 0.89403 | -0.45517 | -2.1663 | -3.4678 | -4.3964 | -9.4483 | -11.5772 | -10.9711
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | WPD Best View | Thermal headroom (MW) | 11.3263 | 10.9036 | 10.4188 | 9.4284 | 9.1646 | 8.3894 | 7.8634 | 7.2971 | 6.666 | 5.9729 | 5.2486 | 4.0396 | 3.1712 | 2.2544 | 1.3534 | 0.64005 | -3.4369 | -6.9558 | -8.7
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Consumer Transformation | Thermal headroom (MW) | 13.8355 | 13.5438 | 13.2471 | 12.89 | 12.1175 | 11.5702 | 10.9769 | 10.3793 | 9.7486 | 8.7389 | 8.1092 | 7.1356 | 6.4661 | 5.8564 | 5.0267 | 4.6309 | 0.84451 | -0.92734 | -0.87435
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Leading the Way | Thermal headroom (MW) | 13.8074 | 13.5088 | 13.2271 | 12.5036 | 12.0898 | 11.5231 | 10.9179 | 10.3311 | 9.3138 | 8.6251 | 8.0068 | 7.0716 | 6.5194 | 6.1132 | 5.5305 | 4.5105 | 2.2354 | 1.9277 | 2.7118
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Steady Progression | Thermal headroom (MW) | 13.9319 | 13.9057 | 13.9467 | 13.8982 | 13.8194 | 13.7173 | 13.585 | 13.4347 | 13.2634 | 13.0352 | 12.7723 | 12.0402 | 11.6465 | 11.2048 | 10.7226 | 9.8603 | 6.3738 | 3.0852 | 2.0477
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | System Transformation | Thermal headroom (MW) | 13.8834 | 13.8026 | 13.7849 | 13.6771 | 13.5255 | 13.3486 | 13.1192 | 12.8513 | 12.1618 | 11.7567 | 11.2898 | 10.3852 | 9.748 | 8.705 | 8.0157 | 7.2844 | 2.9145 | 1.0046 | 0.43871
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | WPD Best View | Thermal headroom (MW) | 13.9168 | 13.8677 | 13.8475 | 13.7415 | 13.5945 | 13.396 | 13.1633 | 12.895 | 12.59 | 11.8802 | 11.5302 | 10.7632 | 10.4029 | 9.9662 | 9.537 | 9.1171 | 6.3187 | 4.0123 | 3.4504
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Consumer Transformation | Thermal headroom (MW) | 4.9149 | 4.5626 | 4.1403 | 3.6965 | 2.7598 | 2.0118 | 1.141 | 0.35952 | -0.46578 | -1.3215 | -2.1429 | -3.3359 | -4.265 | -5.0624 | -6.1279 | -7.3877 | -12.6432 | -14.5351 | -14.5657
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Leading the Way | Thermal headroom (MW) | 4.8595 | 4.4689 | 4.1227 | 3.315 | 2.7298 | 1.9871 | 1.1192 | 0.35327 | -0.49197 | -1.3938 | -2.1815 | -3.3338 | -4.0601 | -4.7619 | -6.355 | -7.4407 | -10.6549 | -11.092 | -9.4637
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Steady Progression | Thermal headroom (MW) | 5.0332 | 5.0158 | 5.0402 | 4.926 | 4.789 | 4.6187 | 4.4512 | 4.2596 | 4.0136 | 3.7309 | 3.392 | 2.586 | 2.0843 | 1.5382 | 0.93433 | 0.31337 | -3.7924 | -6.7992 | -7.9613
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | System Transformation | Thermal headroom (MW) | 4.9615 | 4.8966 | 4.8012 | 4.6571 | 4.4363 | 4.1832 | 3.872 | 3.5351 | 2.779 | 2.285 | 1.714 | 1.028 | 0.25307 | -0.94291 | -1.786 | -2.7066 | -7.306 | -9.0618 | -9.3756
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | WPD Best View | Thermal headroom (MW) | 5.0282 | 5.0028 | 4.9551 | 4.8705 | 4.7097 | 4.5056 | 4.3011 | 4.069 | 3.772 | 3.4417 | 3.0626 | 2.2195 | 1.6983 | 1.1552 | 0.58143 | -0.0031127 | -3.9212 | -6.5463 | -7.5662
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Consumer Transformation | Thermal headroom (MW) | 17.4812 | 16.0284 | 15.1095 | 14.1128 | 12.962 | 11.3368 | 9.2333 | 7.6641 | 5.7082 | 3.4029 | 0.92992 | -1.8515 | -4.852 | -7.2486 | -10.1803 | -12.7318 | -22.3505 | -25.4934 | -25.1923
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Leading the Way | Thermal headroom (MW) | 17.425 | 15.8324 | 14.901 | 13.8473 | 12.6201 | 10.8122 | 8.5022 | 6.8592 | 4.6075 | 2.6151 | -0.078631 | -2.7705 | -5.0606 | -7.5329 | -9.7091 | -11.8729 | -16.9103 | -17.1432 | -13.555
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Steady Progression | Thermal headroom (MW) | 17.7232 | 17.6699 | 17.9028 | 17.9431 | 17.8942 | 17.6862 | 17.4611 | 17.4419 | 16.9315 | 16.7804 | 16.3645 | 15.7382 | 15.1486 | 14.4863 | 13.7064 | 12.4928 | 5.5681 | -2.668 | -5.5064
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | System Transformation | Thermal headroom (MW) | 17.5764 | 17.2981 | 17.2201 | 17.0992 | 16.8666 | 15.9433 | 15.2021 | 14.8196 | 14.283 | 13.6989 | 12.6268 | 11.079 | 9.8633 | 8.5978 | 6.7644 | 4.782 | -4.2572 | -9.5906 | -9.2864
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | WPD Best View | Thermal headroom (MW) | 17.4825 | 16.0312 | 15.1155 | 14.1226 | 12.9767 | 11.3581 | 9.2631 | 7.7045 | 5.7627 | 3.4737 | 1.0199 | -1.7379 | -4.7129 | -7.0829 | -9.9893 | -12.5132 | -22.096 | -25.3327 | -25.0479
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Consumer Transformation | Thermal headroom (MW) | 78.3854 | 76.6123 | 75.133 | 72.7959 | 68.8917 | 65.3944 | 60.9754 | 56.6697 | 52.2032 | 45.9746 | 41.5201 | 36.0094 | 31.5152 | 27.3054 | 22.3097 | 17.7009 | -3.8226 | -12.1202 | -10.936
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Leading the Way | Thermal headroom (MW) | 78.0687 | 76.0355 | 74.7522 | 71.5242 | 68.0523 | 64.4813 | 59.9621 | 55.7042 | 49.5976 | 44.5056 | 40.0513 | 35.6499 | 32.0438 | 28.5311 | 23.9817 | 18.5735 | 4.9859 | 4.6614 | 11.9713
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Steady Progression | Thermal headroom (MW) | 78.9531 | 78.8738 | 79.4472 | 79.1143 | 78.306 | 77.6216 | 76.9875 | 76.1331 | 75.1154 | 73.7955 | 72.2849 | 69.5493 | 67.2865 | 64.7558 | 62.004 | 57.4514 | 40.0626 | 26.6791 | 22.6777
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | System Transformation | Thermal headroom (MW) | 78.5897 | 78.1235 | 78.2088 | 77.6164 | 76.2375 | 75.1507 | 73.7507 | 72.155 | 69.3961 | 66.9333 | 64.323 | 59.6232 | 55.9962 | 51.1208 | 46.9835 | 42.893 | 23.4618 | 14.8332 | 13.9979
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | WPD Best View | Thermal headroom (MW) | 78.5293 | 77.2744 | 76.4803 | 74.838 | 71.9667 | 69.2523 | 65.8658 | 62.5776 | 59.0945 | 54.8442 | 51.3325 | 46.5534 | 42.701 | 38.7391 | 34.4434 | 29.8529 | 10.9069 | -0.72796 | -1.698
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Consumer Transformation | Thermal headroom (MW) | 4.8576 | 4.1473 | 3.4644 | 2.8819 | 2.1045 | 1.2111 | 0.037246 | -0.97698 | -2.0012 | -3.3696 | -4.19 | -5.0955 | -5.9043 | -6.6136 | -7.631 | -8.8448 | -13.3286 | -14.7415 | -14.2963
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Leading the Way | Thermal headroom (MW) | 4.7092 | 3.8122 | 3.1164 | 2.4953 | 1.6117 | 0.75119 | -0.39088 | -1.3339 | -2.6407 | -3.6184 | -4.2686 | -4.7355 | -5.0932 | -5.6995 | -6.8024 | -8.0706 | -10.5605 | -10.3928 | -8.9935
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Steady Progression | Thermal headroom (MW) | 5.0134 | 4.7096 | 4.5223 | 4.2831 | 3.9783 | 3.8032 | 3.5868 | 3.3568 | 3.1036 | 2.8103 | 2.4986 | 2.1417 | 1.7314 | 1.2445 | 0.73655 | -0.14876 | -2.6365 | -4.2622 | -4.5429
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | System Transformation | Thermal headroom (MW) | 4.8888 | 4.4475 | 4.0469 | 3.7899 | 3.3598 | 3.1184 | 2.7676 | 2.4181 | 2.02 | 1.5596 | 1.0921 | 0.17845 | -0.43653 | -1.1399 | -1.7797 | -2.3808 | -4.8541 | -6.0454 | -6.1336
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | WPD Best View | Thermal headroom (MW) | 4.8985 | 4.3434 | 3.8564 | 3.4585 | 2.9181 | 2.2151 | 1.3261 | 0.56904 | -0.18722 | -0.93461 | -1.5581 | -2.2576 | -2.9119 | -3.5467 | -4.0028 | -4.7395 | -7.8082 | -10.1417 | -10.1528
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Consumer Transformation | Thermal headroom (MW) | 2.8131 | 2.5287 | 2.3549 | 1.7729 | 1.1687 | 0.89504 | 0.37226 | -0.20218 | -0.77138 | -1.3423 | -1.9014 | -2.8913 | -3.4469 | -3.9302 | -4.6678 | -5.212 | -9.1938 | -10.8272 | -10.9304
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Leading the Way | Thermal headroom (MW) | 2.7744 | 2.4398 | 2.35 | 1.31 | 1.096 | 0.83499 | 0.32783 | -0.19479 | -0.77859 | -1.3385 | -1.8704 | -2.6179 | -2.9217 | -3.0926 | -3.7893 | -4.4137 | -6.7775 | -7.691 | -6.5645
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Steady Progression | Thermal headroom (MW) | 2.8998 | 2.9357 | 3.137 | 2.9177 | 2.9859 | 3.0544 | 3.0704 | 3.0763 | 3.064 | 3.0327 | 2.9502 | 2.413 | 2.1988 | 1.9533 | 1.676 | 1.3776 | -0.60276 | -2.605 | -3.3904
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | System Transformation | Thermal headroom (MW) | 2.8457 | 2.8164 | 2.927 | 2.6188 | 2.6557 | 2.6739 | 2.6324 | 2.5325 | 2.0389 | 1.861 | 1.6038 | 1.2848 | 0.91361 | 0.15054 | -0.26488 | -0.67435 | -3.1886 | -4.5177 | -4.6214
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | WPD Best View | Thermal headroom (MW) | 2.8182 | 2.5397 | 2.4169 | 1.8085 | 1.2202 | 0.96646 | 0.46622 | -0.041818 | -0.57351 | -1.1128 | -1.6486 | -2.6253 | -3.1805 | -3.6914 | -4.4793 | -4.9765 | -8.9334 | -10.6605 | -10.7809
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Consumer Transformation | Thermal headroom (MW) | 1.1605 | 0.68157 | 0.2292 | -0.3532 | -1.3927 | -2.1852 | -3.1346 | -4.0699 | -5.0378 | -6.0125 | -6.9204 | -8.1342 | -9.1181 | -9.9818 | -11.271 | -12.7399 | -18.6923 | -20.5649 | -20.3365
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Leading the Way | Thermal headroom (MW) | 1.1373 | 0.68584 | 0.29288 | -0.61443 | -1.2297 | -1.9665 | -2.8974 | -3.7848 | -4.7756 | -5.8041 | -6.7321 | -7.9684 | -8.8038 | -9.9629 | -11.8896 | -13.2607 | -16.7972 | -16.8422 | -14.7381
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Steady Progression | Thermal headroom (MW) | 1.3035 | 1.3069 | 1.3897 | 1.338 | 1.2469 | 1.1063 | 0.92179 | 0.7096 | 0.44648 | 0.13542 | -0.22994 | -1.115 | -1.6844 | -2.3443 | -3.0641 | -3.8044 | -8.7067 | -12.594 | -14.1127
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | System Transformation | Thermal headroom (MW) | 1.2358 | 1.1705 | 1.1882 | 1.0619 | 0.86204 | 0.64269 | 0.26896 | -0.16161 | -1.0599 | -1.6484 | -2.3369 | -3.1887 | -4.1407 | -5.5392 | -6.5777 | -7.6446 | -13.0816 | -16.1802 | -16.411
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | WPD Best View | Thermal headroom (MW) | 1.2401 | 1.0472 | 0.90508 | 0.63345 | 0.29416 | -0.13533 | -0.6273 | -1.1328 | -1.674 | -2.2365 | -2.8047 | -3.7739 | -4.3516 | -4.976 | -5.6467 | -6.297 | -9.859 | -14.263 | -15.601
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Consumer Transformation | Thermal headroom (MW) | 0.18686 | -0.31455 | -0.85241 | -1.7351 | -2.7338 | -4.2823 | -6.1896 | -8.0135 | -9.657 | -11.4505 | -12.7829 | -14.5212 | -15.7809 | -17.501 | -19.6895 | -21.3781 | -27.6192 | -29.1236 | -28.1576
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Leading the Way | Thermal headroom (MW) | 0.17195 | -0.4627 | -0.93998 | -2.3135 | -2.9723 | -4.6942 | -6.8596 | -8.9032 | -10.7475 | -12.7341 | -13.9985 | -15.1479 | -16.5014 | -17.8908 | -19.5408 | -20.5858 | -23.6251 | -23.5853 | -21.0701
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Steady Progression | Thermal headroom (MW) | 0.30755 | 0.30832 | 0.43708 | 0.10961 | 0.016061 | -0.37267 | -0.82193 | -1.3185 | -1.7229 | -2.3033 | -2.6902 | -3.575 | -4.2145 | -4.8834 | -5.5716 | -6.3023 | -10.0773 | -13.2604 | -14.1752
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | System Transformation | Thermal headroom (MW) | 0.25112 | 0.13841 | 0.021799 | -0.44347 | -0.64064 | -1.2388 | -2.0833 | -2.9771 | -4.03 | -5.0228 | -5.7069 | -6.5675 | -7.5666 | -8.8696 | -9.7813 | -10.6325 | -14.237 | -16.8902 | -16.5855
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | WPD Best View | Thermal headroom (MW) | 0.19194 | -0.30353 | -0.82986 | -1.6995 | -2.6823 | -4.2109 | -6.0956 | -7.8535 | -9.4592 | -11.221 | -12.5301 | -14.2552 | -15.5626 | -17.3352 | -19.4985 | -21.1595 | -27.3647 | -28.9629 | -28.0132
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Consumer Transformation | Thermal headroom (MW) | 12.361 | 12.3325 | 12.4112 | 12.3651 | 11.4546 | 11.087 | 10.9464 | 10.8404 | 10.631 | 10.3868 | 10.1736 | 9.8883 | 9.6444 | 9.4081 | 9.148 | 8.8823 | 7.9577 | 7.842 | 8.1527
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Leading the Way | Thermal headroom (MW) | 12.3381 | 12.289 | 12.3754 | 12.328 | 11.0515 | 10.5516 | 10.4337 | 10.2699 | 10.1131 | 9.81 | 9.5637 | 9.3927 | 9.218 | 8.9956 | 8.8358 | 8.6618 | 8.3035 | 8.5613 | 9.2632
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Steady Progression | Thermal headroom (MW) | 12.3901 | 12.4459 | 12.6302 | 12.6941 | 12.1164 | 11.9334 | 12.0214 | 12.0289 | 12.0467 | 12.0646 | 12.0506 | 12.0525 | 12.0318 | 11.9927 | 11.9999 | 11.9532 | 11.5967 | 10.9283 | 10.9195
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | System Transformation | Thermal headroom (MW) | 12.3605 | 12.3916 | 12.5586 | 12.6006 | 11.7699 | 11.4923 | 11.5412 | 11.6076 | 11.5729 | 11.4762 | 11.4173 | 11.3716 | 11.3286 | 11.2564 | 11.1754 | 11.071 | 10.3761 | 10.199 | 10.5922
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | WPD Best View | Thermal headroom (MW) | 12.361 | 12.3325 | 12.4112 | 12.3651 | 11.4546 | 11.087 | 10.9464 | 10.8404 | 10.631 | 10.3868 | 10.1736 | 9.8883 | 9.6444 | 9.4081 | 9.148 | 8.8823 | 7.9577 | 7.842 | 8.1527
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Consumer Transformation | Thermal headroom (MW) | 9.4955 | 9.3835 | 9.2714 | 9.0057 | 8.6696 | 8.2706 | 7.763 | 7.2148 | 6.6307 | 5.6316 | 4.9343 | 4.2296 | 3.5768 | 3.041 | 2.6165 | 2.2685 | 0.096886 | -1.0931 | -1.0853
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Leading the Way | Thermal headroom (MW) | 9.4865 | 9.386 | 9.2906 | 9.0176 | 8.6828 | 8.2809 | 7.7597 | 7.2223 | 6.2373 | 5.4921 | 4.7501 | 4.1074 | 3.5492 | 3.1814 | 2.9714 | 2.1662 | 0.37246 | 0.44125 | 1.1264
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Steady Progression | Thermal headroom (MW) | 9.5305 | 9.5458 | 9.6179 | 9.6339 | 9.5721 | 9.4597 | 9.3173 | 9.1382 | 8.9112 | 8.652 | 8.3247 | 7.9478 | 7.5106 | 7.0416 | 6.5159 | 5.5418 | 2.3794 | 0.59119 | 0.021853
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | System Transformation | Thermal headroom (MW) | 9.5123 | 9.5092 | 9.5638 | 9.5356 | 9.4231 | 9.2621 | 9.0202 | 8.7481 | 8.3846 | 7.9625 | 7.4826 | 6.5453 | 5.8757 | 5.0838 | 4.2597 | 3.4598 | 0.33974 | -0.49732 | -0.80275
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | WPD Best View | Thermal headroom (MW) | 9.5214 | 9.506 | 9.5365 | 9.4464 | 9.2794 | 9.0635 | 8.7945 | 8.4756 | 8.115 | 7.7253 | 7.2978 | 6.7919 | 6.2669 | 5.7593 | 5.2602 | 4.4127 | 2.1148 | 0.56051 | 0.23289
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Consumer Transformation | Thermal headroom (MW) | 15.9839 | 15.8712 | 15.8253 | 15.765 | 15.6822 | 15.5438 | 15.3035 | 15.0577 | 14.8017 | 14.1686 | 13.9043 | 13.6172 | 13.3617 | 13.0946 | 12.8739 | 12.6998 | 11.4057 | 10.6579 | 10.6942
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Leading the Way | Thermal headroom (MW) | 15.9114 | 15.774 | 15.7258 | 15.6742 | 15.5661 | 15.437 | 15.1923 | 14.9696 | 14.3369 | 14.0546 | 13.79 | 13.5852 | 13.3485 | 13.1695 | 13.0665 | 12.6619 | 11.64 | 11.6986 | 11.9971
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Steady Progression | Thermal headroom (MW) | 16.0536 | 16.0321 | 16.0786 | 16.0974 | 16.0979 | 16.0946 | 16.0847 | 16.0655 | 16.0115 | 15.9068 | 15.805 | 15.6658 | 15.5115 | 15.3399 | 15.1386 | 14.5896 | 13.4198 | 12.5216 | 12.3875
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | System Transformation | Thermal headroom (MW) | 16.0037 | 15.9501 | 15.9814 | 16.0071 | 16.01 | 16.0052 | 15.9669 | 15.8932 | 15.7851 | 15.6375 | 15.4698 | 14.8856 | 14.6412 | 14.3671 | 14.0914 | 13.8265 | 12.2971 | 11.7693 | 11.5633
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | WPD Best View | Thermal headroom (MW) | 15.9839 | 15.8712 | 15.8253 | 15.765 | 15.6822 | 15.5438 | 15.3035 | 15.0577 | 14.8017 | 14.1686 | 13.9043 | 13.6172 | 13.3617 | 13.0946 | 12.8739 | 12.6998 | 11.4057 | 10.6579 | 10.6942
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Consumer Transformation | Thermal headroom (MW) | 2.1343 | 1.8794 | 1.6487 | 1.3565 | 0.71934 | 0.2784 | -0.43906 | -1.0583 | -1.7514 | -2.5078 | -3.3659 | -4.754 | -5.8319 | -6.8158 | -8.1952 | -9.2759 | -13.7541 | -15.3894 | -15.2732
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Leading the Way | Thermal headroom (MW) | 2.1051 | 1.7886 | 1.6723 | 1.0468 | 0.7706 | 0.37479 | -0.41313 | -1.022 | -1.7408 | -2.5611 | -3.5066 | -4.7089 | -5.654 | -6.5437 | -7.786 | -8.5596 | -11.1663 | -11.8408 | -10.2794
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Steady Progression | Thermal headroom (MW) | 2.2437 | 2.4164 | 2.6726 | 2.7442 | 2.8955 | 2.9623 | 3.0668 | 3.1398 | 3.224 | 3.2705 | 3.2562 | 2.805 | 2.6785 | 2.5273 | 2.3404 | 2.0925 | -0.2007 | -3.4576 | -4.6193
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | System Transformation | Thermal headroom (MW) | 2.1754 | 2.2461 | 2.3676 | 2.4617 | 2.5283 | 2.575 | 2.5239 | 2.4711 | 2.0457 | 1.8927 | 1.6784 | 1.4311 | 1.1105 | 0.36777 | -0.077439 | -0.59616 | -4.3515 | -6.6826 | -6.8283
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | WPD Best View | Thermal headroom (MW) | 2.1343 | 1.8794 | 1.6487 | 1.3565 | 0.71934 | 0.2784 | -0.43906 | -1.0583 | -1.7514 | -2.5078 | -3.3659 | -4.754 | -5.8319 | -6.8158 | -8.1952 | -9.2759 | -13.7541 | -15.3894 | -15.2732
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Consumer Transformation | Thermal headroom (MW) | 31.1858 | 29.336 | 27.608 | 25.4379 | 23.2191 | 20.5795 | 17.5553 | 14.6032 | 11.4332 | 4.9575 | 1.4285 | -1.983 | -5.5169 | -8.8128 | -11.7922 | -14.621 | -29.0388 | -35.4708 | -33.9707
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Leading the Way | Thermal headroom (MW) | 31.0333 | 29.1811 | 27.7357 | 25.6129 | 23.5294 | 20.7812 | 17.5944 | 14.7957 | 8.2918 | 4.7096 | 0.91264 | -2.3925 | -5.8589 | -8.7944 | -11.2563 | -17.1375 | -25.7018 | -24.1107 | -22.027
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Steady Progression | Thermal headroom (MW) | 31.7529 | 31.8185 | 32.0736 | 31.8687 | 31.7595 | 31.5851 | 31.1837 | 30.5746 | 29.7062 | 28.7025 | 27.3571 | 25.5407 | 23.5219 | 21.2754 | 18.8528 | 13.0254 | -1.97 | -15.98 | -20.7566
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | System Transformation | Thermal headroom (MW) | 31.4138 | 31.1172 | 30.9341 | 30.4165 | 29.9661 | 29.2525 | 27.9716 | 26.5371 | 24.6327 | 22.5204 | 20.1535 | 14.0446 | 10.7646 | 7.158 | 3.4689 | -0.27676 | -17.1156 | -25.7752 | -28.5248
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | WPD Best View | Thermal headroom (MW) | 31.4029 | 30.2598 | 29.2394 | 27.7851 | 26.4241 | 24.6799 | 22.5953 | 20.5156 | 18.2491 | 13.4907 | 10.8518 | 8.0103 | 4.961 | 1.8988 | -1.1511 | -5.0786 | -19.8947 | -28.8907 | -29.178
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Consumer Transformation | Thermal headroom (MW) | 5.7204 | 5.313 | 4.9692 | 4.549 | 4.1571 | 3.7168 | 3.2608 | 2.861 | 2.4063 | 1.169 | 0.60219 | 0.11111 | -0.42974 | -0.98743 | -1.5103 | -2.08 | -4.6465 | -5.6002 | -5.1777
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Leading the Way | Thermal headroom (MW) | 5.6876 | 5.2992 | 5.0161 | 4.6464 | 4.2832 | 3.8056 | 3.2955 | 2.9423 | 1.7204 | 1.1475 | 0.4982 | -0.074486 | -0.74229 | -1.3734 | -2.0022 | -3.2933 | -4.3418 | -3.8227 | -3.7385
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Steady Progression | Thermal headroom (MW) | 5.8475 | 5.8864 | 5.9601 | 5.9737 | 5.9889 | 6.0211 | 6.0092 | 5.9713 | 5.8476 | 5.7092 | 5.4975 | 5.2109 | 4.8792 | 4.5311 | 4.1546 | 3.0318 | 0.68217 | -2.0301 | -2.975
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | System Transformation | Thermal headroom (MW) | 5.7621 | 5.7227 | 5.7047 | 5.6524 | 5.5996 | 5.4965 | 5.2959 | 5.0925 | 4.7552 | 4.3856 | 4.0154 | 2.7944 | 2.2562 | 1.6764 | 1.1205 | 0.53541 | -2.3712 | -4.3113 | -4.9974
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | WPD Best View | Thermal headroom (MW) | 5.76 | 5.4911 | 5.2948 | 4.9827 | 4.7303 | 4.4483 | 4.1417 | 3.8726 | 3.5649 | 2.8489 | 2.4431 | 2.0818 | 1.6806 | 1.274 | 0.86104 | 0.04203 | -2.1821 | -3.9688 | -4.0223
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Consumer Transformation | Thermal headroom (MW) | 3.0915 | 3.0393 | 3.0663 | 3.0185 | 3.0014 | 2.947 | 2.8894 | 2.822 | 2.7666 | 2.6511 | 2.5326 | 2.4339 | 2.3596 | 2.2465 | 2.1242 | 2.016 | 1.6508 | 1.7741 | 2.1281
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Leading the Way | Thermal headroom (MW) | 3.0728 | 2.9941 | 3.0435 | 3.0006 | 2.9886 | 2.9493 | 2.9027 | 2.846 | 2.7602 | 2.6475 | 2.5406 | 2.4616 | 2.323 | 2.1849 | 2.0404 | 1.9274 | 1.76 | 2.1657 | 2.7423
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Steady Progression | Thermal headroom (MW) | 3.1268 | 3.1798 | 3.3189 | 3.3654 | 3.4264 | 3.5027 | 3.5738 | 3.6236 | 3.6917 | 3.7354 | 3.7631 | 3.7396 | 3.6835 | 3.5984 | 3.4962 | 3.3969 | 2.8497 | 2.6236 | 2.5946
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | System Transformation | Thermal headroom (MW) | 3.0994 | 3.1293 | 3.2257 | 3.2692 | 3.3139 | 3.3773 | 3.3907 | 3.4227 | 3.4339 | 3.4165 | 3.3529 | 3.2344 | 3.0888 | 2.9236 | 2.7655 | 2.6104 | 2.291 | 2.2822 | 2.5674
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | WPD Best View | Thermal headroom (MW) | 3.0915 | 3.0393 | 3.0663 | 3.0185 | 3.0014 | 2.947 | 2.8894 | 2.822 | 2.7666 | 2.6511 | 2.5326 | 2.4339 | 2.3596 | 2.2465 | 2.1242 | 2.016 | 1.6508 | 1.7741 | 2.1281
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Consumer Transformation | Thermal headroom (MW) | 8.4888 | 8.1656 | 7.8126 | 7.3526 | 6.7752 | 5.7815 | 4.5044 | 3.3467 | 2.1403 | 0.56385 | -0.6078 | -2.1376 | -4.16 | -6.0051 | -7.9436 | -9.7672 | -16.8015 | -18.8957 | -18.1789
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Leading the Way | Thermal headroom (MW) | 8.4559 | 8.0737 | 7.8346 | 7.3604 | 6.7642 | 5.767 | 4.4737 | 3.3084 | 1.6906 | 0.43614 | -0.64502 | -1.8283 | -3.4607 | -5.0502 | -6.5863 | -8.2759 | -12.333 | -12.5229 | -10.9226
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Steady Progression | Thermal headroom (MW) | 8.5829 | 8.6474 | 8.8096 | 8.7141 | 8.6319 | 8.5133 | 8.3963 | 8.2262 | 8.0031 | 7.7468 | 7.4496 | 7.0649 | 6.6298 | 6.1369 | 5.6244 | 4.707 | 1.7726 | -1.4726 | -2.5379
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | System Transformation | Thermal headroom (MW) | 8.5284 | 8.5393 | 8.5647 | 8.4627 | 8.2756 | 8.061 | 7.7434 | 7.413 | 7.0034 | 6.5501 | 6.0469 | 5.0703 | 4.4051 | 3.7166 | 3.0419 | 2.3745 | -1.441 | -4.3222 | -4.4333
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | WPD Best View | Thermal headroom (MW) | 8.4938 | 8.1767 | 7.8351 | 7.3882 | 6.8448 | 5.8782 | 4.632 | 3.5071 | 2.3382 | 0.79337 | -0.35502 | -2.024 | -4.0209 | -5.8394 | -7.7526 | -9.5486 | -16.5471 | -18.735 | -18.0345
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Consumer Transformation | Thermal headroom (MW) | 9.7668 | 9.5307 | 9.2785 | 8.9833 | 8.7106 | 8.4023 | 8.0381 | 7.675 | 7.2835 | 6.5296 | 6.0977 | 5.6891 | 5.2984 | 4.9688 | 4.6957 | 4.4574 | 3.0102 | 2.1143 | 2.1153
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Leading the Way | Thermal headroom (MW) | 9.7492 | 9.515 | 9.2774 | 8.9695 | 8.7153 | 8.3972 | 8.0176 | 7.6755 | 6.9118 | 6.4823 | 6.023 | 5.6398 | 5.3009 | 5.0549 | 4.8965 | 4.3532 | 3.2456 | 3.2809 | 3.4158
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Steady Progression | Thermal headroom (MW) | 9.8245 | 9.7875 | 9.74 | 9.6646 | 9.6079 | 9.5394 | 9.4498 | 9.3386 | 9.21 | 9.0624 | 8.8758 | 8.636 | 8.3787 | 8.0941 | 7.7832 | 7.0627 | 5.1187 | 3.4608 | 2.8602
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | System Transformation | Thermal headroom (MW) | 9.7945 | 9.7134 | 9.628 | 9.5003 | 9.4092 | 9.2991 | 9.1246 | 8.9203 | 8.6768 | 8.4153 | 8.1032 | 7.3851 | 6.9779 | 6.5134 | 6.0288 | 5.5363 | 3.4582 | 2.5429 | 2.146
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | WPD Best View | Thermal headroom (MW) | 9.797 | 9.6598 | 9.506 | 9.3183 | 9.1457 | 8.9565 | 8.7251 | 8.4734 | 8.2085 | 7.5748 | 7.2751 | 6.944 | 6.6022 | 6.2712 | 5.9523 | 5.6421 | 3.9277 | 2.7586 | 2.5384
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Consumer Transformation | Thermal headroom (MW) | 22.6051 | 20.5084 | 19.5549 | 17.9138 | 16.3055 | 14.4359 | 12.0982 | 9.5485 | 7.3015 | 3.7238 | 1.0343 | -1.9748 | -6.5124 | -9.8572 | -14.756 | -19.1864 | -36.5175 | -42.7573 | -42.3278
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Leading the Way | Thermal headroom (MW) | 22.4269 | 20.3513 | 19.5946 | 18.2094 | 16.7458 | 14.8982 | 12.0336 | 10.1488 | 6.4485 | 3.7201 | 1.3512 | -2.719 | -5.8536 | -10.5057 | -14.6704 | -19.4664 | -28.5479 | -28.6391 | -23.6225
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Steady Progression | Thermal headroom (MW) | 23.2379 | 23.6903 | 24.7591 | 25.1082 | 25.4249 | 25.7814 | 25.95 | 26.013 | 25.319 | 25.2069 | 25.0149 | 24.287 | 23.5353 | 22.1435 | 21.1444 | 18.5936 | 7.8235 | -8.6113 | -14.637
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | System Transformation | Thermal headroom (MW) | 22.8267 | 22.9482 | 23.6211 | 23.5847 | 23.6719 | 22.8869 | 22.2874 | 21.6228 | 20.6779 | 19.7743 | 18.1899 | 15.3145 | 13.1916 | 11.4165 | 8.5017 | 5.4369 | -11.901 | -23.8141 | -25.2167
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | WPD Best View | Thermal headroom (MW) | 22.8647 | 23.0218 | 23.7305 | 23.7443 | 23.874 | 23.1356 | 22.6122 | 22.0358 | 21.1666 | 20.3563 | 18.8432 | 16.0409 | 13.9854 | 12.2821 | 9.4354 | 6.4277 | -11.0477 | -23.2405 | -24.9619
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Consumer Transformation | Thermal headroom (MW) | 1.0641 | 0.53963 | 0.40422 | 0.22386 | 0.026955 | -0.1889 | -0.47159 | -0.74718 | -1.0341 | -1.6882 | -1.9976 | -2.6716 | -3.6512 | -4.2299 | -5.2006 | -5.8178 | -8.9834 | -10.3491 | -10.5942
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Leading the Way | Thermal headroom (MW) | 1.0461 | 0.51773 | 0.42273 | 0.2768 | 0.093031 | -0.1261 | -0.41903 | -0.67772 | -1.3203 | -1.6308 | -2.0635 | -3.069 | -3.6978 | -4.6712 | -5.2483 | -6.125 | -7.745 | -8.0496 | -7.5992
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Steady Progression | Thermal headroom (MW) | 1.1327 | 1.1863 | 1.2839 | 1.3091 | 1.347 | 1.3694 | 1.3763 | 1.3536 | 0.97787 | 0.91117 | 0.87783 | 0.73631 | 0.60895 | 0.4694 | 0.31673 | -0.21733 | -2.3388 | -5.1216 | -6.186
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | System Transformation | Thermal headroom (MW) | 1.0877 | 1.1073 | 1.1492 | 1.1549 | 1.1637 | 0.76523 | 0.69333 | 0.60886 | 0.48172 | 0.35622 | 0.20044 | -0.40408 | -0.63731 | -0.89447 | -1.5117 | -2.1464 | -5.5499 | -7.8592 | -8.1488
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | WPD Best View | Thermal headroom (MW) | 1.0877 | 1.1073 | 1.1492 | 1.1549 | 1.1637 | 0.76523 | 0.69333 | 0.60886 | 0.48172 | 0.35622 | 0.20044 | -0.40408 | -0.63731 | -0.89447 | -1.5117 | -2.1464 | -5.5499 | -7.8592 | -8.1488
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Consumer Transformation | Thermal headroom (MW) | 2.9405 | 2.7133 | 2.5223 | 2.2646 | 1.9815 | 1.6863 | 1.4209 | 1.1949 | 0.96021 | 0.35601 | 0.094379 | -0.063381 | -0.22102 | -0.47541 | -0.86886 | -1.2461 | -2.6744 | -2.9776 | -2.4798
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Leading the Way | Thermal headroom (MW) | 2.9247 | 2.7094 | 2.5388 | 2.2954 | 2.0295 | 1.7341 | 1.4548 | 1.2556 | 0.66102 | 0.3959 | 0.18116 | 0.0094688 | -0.13238 | -0.59337 | -0.95949 | -1.6951 | -2.1826 | -1.6403 | -1.3217
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Steady Progression | Thermal headroom (MW) | 3.0386 | 3.1033 | 3.2219 | 3.2568 | 3.2909 | 3.333 | 3.3452 | 3.358 | 3.3682 | 3.3567 | 3.3553 | 3.2424 | 3.1419 | 3.0257 | 2.8856 | 2.3835 | 1.3767 | -0.41833 | -1.2913
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | System Transformation | Thermal headroom (MW) | 2.9786 | 2.9895 | 3.0471 | 3.0164 | 2.9851 | 2.9446 | 2.821 | 2.6964 | 2.5826 | 2.4415 | 2.2817 | 1.7166 | 1.4678 | 1.2164 | 0.96516 | 0.70738 | -0.70666 | -2.1101 | -2.3905
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | WPD Best View | Thermal headroom (MW) | 2.9786 | 2.9895 | 3.0471 | 3.0164 | 2.9851 | 2.9446 | 2.821 | 2.6964 | 2.5826 | 2.4415 | 2.2817 | 1.7166 | 1.4678 | 1.2164 | 0.96516 | 0.70738 | -0.70666 | -2.1101 | -2.3905
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Consumer Transformation | Thermal headroom (MW) | -2.0301 | -2.6352 | -2.7488 | -2.9627 | -3.1564 | -3.4266 | -3.8356 | -4.1847 | -4.528 | -5.235 | -5.6875 | -6.0378 | -6.6948 | -6.9597 | -8.0949 | -8.8537 | -12.6205 | -13.9253 | -13.7076
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Leading the Way | Thermal headroom (MW) | -2.0849 | -2.7244 | -2.7968 | -2.9883 | -3.1623 | -3.4208 | -3.7962 | -4.1138 | -4.7954 | -5.1293 | -5.6173 | -6.2082 | -6.394 | -7.3333 | -8.0575 | -9.006 | -10.9783 | -10.8704 | -9.6941
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Steady Progression | Thermal headroom (MW) | -1.9016 | -1.8046 | -1.5368 | -1.4398 | -1.3085 | -1.1801 | -1.0748 | -0.99264 | -1.2938 | -1.2405 | -1.288 | -1.3504 | -1.4316 | -1.5254 | -1.6595 | -2.1561 | -3.9214 | -6.3966 | -7.5058
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | System Transformation | Thermal headroom (MW) | -1.9934 | -1.9676 | -1.8064 | -1.7401 | -1.666 | -1.9725 | -1.9844 | -2.0333 | -2.1164 | -2.2073 | -2.4544 | -3.0155 | -3.228 | -3.4854 | -4.1043 | -4.7218 | -7.3214 | -9.864 | -9.8321
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | WPD Best View | Thermal headroom (MW) | -1.9934 | -1.9676 | -1.8064 | -1.7401 | -1.666 | -1.9725 | -1.9844 | -2.0333 | -2.1164 | -2.2073 | -2.4544 | -3.0155 | -3.228 | -3.4854 | -4.1043 | -4.7218 | -7.3214 | -9.864 | -9.8321
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Consumer Transformation | Thermal headroom (MW) | 5.5438 | 5.5331 | 5.6835 | 5.6787 | 5.669 | 5.6275 | 5.5342 | 5.4684 | 5.4206 | 5.3631 | 5.3127 | 5.2571 | 5.1923 | 5.1341 | 5.1117 | 5.0945 | 5.032 | 5.1432 | 5.6306
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Leading the Way | Thermal headroom (MW) | 5.5332 | 5.5316 | 5.7067 | 5.7229 | 5.728 | 5.6946 | 5.5895 | 5.5355 | 5.4925 | 5.4229 | 5.3811 | 5.3848 | 5.3732 | 5.3876 | 5.4606 | 5.5363 | 5.7853 | 6.2267 | 7.0744
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Steady Progression | Thermal headroom (MW) | 5.5909 | 5.743 | 6.0547 | 6.2102 | 6.3659 | 6.5107 | 6.6387 | 6.7617 | 6.8818 | 7.0003 | 7.1047 | 7.1593 | 7.2196 | 7.2604 | 7.3042 | 7.3369 | 7.1615 | 6.9305 | 7.1314
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | System Transformation | Thermal headroom (MW) | 5.5623 | 5.6849 | 5.9748 | 6.0994 | 6.2312 | 6.3389 | 6.4036 | 6.4666 | 6.5377 | 6.587 | 6.6245 | 6.6403 | 6.6399 | 6.6203 | 6.6017 | 6.5265 | 6.435 | 6.6349 | 7.1955
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | WPD Best View | Thermal headroom (MW) | 5.5623 | 5.6849 | 5.9748 | 6.0994 | 6.2312 | 6.3389 | 6.4036 | 6.4666 | 6.5377 | 6.587 | 6.6245 | 6.6403 | 6.6399 | 6.6203 | 6.6017 | 6.5265 | 6.435 | 6.6349 | 7.1955
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Consumer Transformation | Thermal headroom (MW) | 3.4695 | 3.1958 | 2.9832 | 2.637 | 2.3368 | 2.0017 | 1.602 | 1.2412 | 0.73571 | -0.010504 | -0.40639 | -0.87254 | -1.4987 | -2.1395 | -2.7903 | -3.5248 | -5.9126 | -6.7241 | -6.388
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Leading the Way | Thermal headroom (MW) | 3.4343 | 3.1604 | 2.9182 | 2.6582 | 2.4032 | 2.048 | 1.6264 | 1.3021 | 0.3823 | -0.02916 | -0.46089 | -1.0528 | -1.701 | -2.308 | -2.927 | -3.9472 | -5.0916 | -4.7416 | -4.1754
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Steady Progression | Thermal headroom (MW) | 3.5727 | 3.6027 | 3.7129 | 3.7355 | 3.6859 | 3.6997 | 3.6898 | 3.6735 | 3.5699 | 3.5085 | 3.4213 | 3.2672 | 3.113 | 2.9274 | 2.7298 | 2.1138 | 0.7925 | -2.1047 | -3.0946
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | System Transformation | Thermal headroom (MW) | 3.5042 | 3.4757 | 3.5254 | 3.4276 | 3.3983 | 3.3474 | 3.2067 | 3.0414 | 2.728 | 2.5206 | 2.3056 | 1.6774 | 1.3643 | 1.0353 | 0.71936 | 0.32097 | -2.3958 | -4.2026 | -4.4836
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | WPD Best View | Thermal headroom (MW) | 3.5042 | 3.4757 | 3.5254 | 3.4276 | 3.3983 | 3.3474 | 3.2067 | 3.0414 | 2.728 | 2.5206 | 2.3056 | 1.6774 | 1.3643 | 1.0353 | 0.71936 | 0.32097 | -2.3958 | -4.2026 | -4.4836
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Consumer Transformation | Thermal headroom (MW) | 4.7227 | 4.5614 | 4.482 | 4.2952 | 4.0999 | 3.8546 | 3.398 | 2.6372 | 2.2264 | 1.8057 | 1.0559 | 0.36885 | -0.88806 | -1.7526 | -2.9956 | -4.2058 | -8.3237 | -10.2413 | -11.0776
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Leading the Way | Thermal headroom (MW) | 4.708 | 4.5714 | 4.5425 | 4.4103 | 4.2257 | 3.9973 | 3.1877 | 2.7965 | 2.3986 | 1.6163 | 1.2015 | 0.26869 | -0.4794 | -1.6036 | -2.7134 | -3.3631 | -6.0223 | -7.229 | -6.1524
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Steady Progression | Thermal headroom (MW) | 4.7883 | 4.8486 | 5.0019 | 5.0726 | 5.1321 | 5.1913 | 5.1757 | 5.1439 | 5.1124 | 5.0926 | 5.0468 | 4.9463 | 4.8279 | 4.3223 | 4.1608 | 3.9855 | 1.7032 | -1.5036 | -2.443
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | System Transformation | Thermal headroom (MW) | 4.7485 | 4.7877 | 4.9232 | 4.9615 | 5.0063 | 4.9841 | 4.9053 | 4.8348 | 4.7281 | 4.62 | 4.1233 | 3.9307 | 3.3362 | 3.0888 | 2.4559 | 1.8299 | -2.18 | -4.5995 | -5.2734
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | WPD Best View | Thermal headroom (MW) | 4.7485 | 4.7877 | 4.9232 | 4.9615 | 5.0063 | 4.9841 | 4.9053 | 4.8348 | 4.7281 | 4.62 | 4.1233 | 3.9307 | 3.3362 | 3.0888 | 2.4559 | 1.8299 | -2.18 | -4.5995 | -5.2734
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Consumer Transformation | Thermal headroom (MW) | 13.8236 | 13.3211 | 12.9499 | 12.4818 | 12.0369 | 11.4918 | 10.6999 | 9.6918 | 9.053 | 8.4111 | 7.4185 | 6.3309 | 4.5536 | 3.2377 | 1.4832 | -0.2567 | -5.9787 | -8.0753 | -8.4294
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Leading the Way | Thermal headroom (MW) | 13.7692 | 13.2525 | 12.9757 | 12.5671 | 12.1718 | 11.6686 | 10.4906 | 9.9198 | 9.3081 | 8.3181 | 7.7232 | 6.2583 | 4.9783 | 3.3044 | 1.6935 | 0.60184 | -2.9021 | -3.6213 | -1.5959
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Steady Progression | Thermal headroom (MW) | 14.0169 | 14.1148 | 14.4076 | 14.5074 | 14.6367 | 14.7603 | 14.8342 | 14.8652 | 14.9075 | 14.9318 | 14.9227 | 14.7694 | 14.5865 | 14.0002 | 13.7589 | 13.4902 | 10.0672 | 4.2462 | 2.0965
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | System Transformation | Thermal headroom (MW) | 13.8869 | 13.8813 | 14.0305 | 14.0589 | 14.112 | 14.0917 | 13.9095 | 13.7565 | 13.5594 | 13.3433 | 12.7311 | 12.3698 | 11.6128 | 11.1553 | 10.3425 | 9.5104 | 3.2234 | -0.67166 | -1.2931
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | WPD Best View | Thermal headroom (MW) | 13.8869 | 13.8813 | 14.0305 | 14.0589 | 14.112 | 14.0917 | 13.9095 | 13.7565 | 13.5594 | 13.3433 | 12.7311 | 12.3698 | 11.6128 | 11.1553 | 10.3425 | 9.5104 | 3.2234 | -0.67166 | -1.2931
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Consumer Transformation | Thermal headroom (MW) | 0.17963 | -0.095298 | -0.27252 | -0.63379 | -0.96687 | -1.3572 | -1.6799 | -1.9691 | -2.2663 | -2.5792 | -2.8643 | -3.0502 | -3.2089 | -3.3294 | -3.3979 | -3.6472 | -4.9333 | -4.9405 | -4.3736
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Leading the Way | Thermal headroom (MW) | 0.13899 | -0.12517 | -0.25685 | -0.6138 | -0.93149 | -1.3146 | -1.6297 | -1.8845 | -2.2101 | -2.5363 | -2.8081 | -2.9917 | -3.1299 | -3.175 | -3.6003 | -3.9655 | -4.5231 | -3.8669 | -3.0698
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Steady Progression | Thermal headroom (MW) | 0.30783 | 0.38357 | 0.56542 | 0.5916 | 0.63412 | 0.66719 | 0.69914 | 0.71458 | 0.7126 | 0.68417 | 0.63657 | 0.51502 | 0.36678 | 0.18262 | -0.00076497 | -0.19984 | -1.4515 | -2.7152 | -3.2683
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | System Transformation | Thermal headroom (MW) | 0.22482 | 0.23135 | 0.34335 | 0.28129 | 0.24596 | 0.19373 | 0.065545 | -0.090817 | -0.25726 | -0.45592 | -0.66411 | -0.93809 | -1.2481 | -1.5801 | -1.9121 | -2.2415 | -3.1701 | -3.737 | -3.5338
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | WPD Best View | Thermal headroom (MW) | 0.27345 | 0.32563 | 0.48332 | 0.48547 | 0.50456 | 0.51208 | 0.48124 | 0.4377 | 0.3681 | 0.2889 | 0.17182 | -0.0085337 | -0.23228 | -0.47245 | -0.71727 | -0.97364 | -2.0782 | -3.0031 | -3.2078
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Consumer Transformation | Thermal headroom (MW) | 24.9626 | 23.2289 | 22.0604 | 19.7184 | 17.0658 | 13.9346 | 9.7569 | 5.5538 | 1.3884 | -5.3806 | -9.8774 | -14.805 | -20.021 | -24.4481 | -29.1806 | -33.0919 | -52.9939 | -62.1805 | -61.4689
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Leading the Way | Thermal headroom (MW) | 24.7993 | 23.083 | 22.0331 | 19.6381 | 17.2836 | 14.1858 | 9.738 | 5.7152 | -1.0015 | -5.7667 | -10.3009 | -14.8754 | -18.9998 | -22.9272 | -26.1318 | -31.6972 | -44.4304 | -44.6725 | -39.7233
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Steady Progression | Thermal headroom (MW) | 25.5379 | 25.8481 | 26.7758 | 26.8236 | 26.8025 | 26.809 | 26.3622 | 25.7176 | 24.7757 | 23.7412 | 22.2574 | 20.0893 | 17.8401 | 15.0886 | 12.4081 | 6.9259 | -11.6841 | -28.8979 | -34.3162
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | System Transformation | Thermal headroom (MW) | 25.2128 | 25.1942 | 25.787 | 25.285 | 25.0685 | 24.3268 | 23.0433 | 21.4397 | 19.3929 | 17.1567 | 14.3457 | 8.583 | 4.6459 | 0.39444 | -4.0828 | -8.6236 | -30.2035 | -40.7677 | -42.8705
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | WPD Best View | Thermal headroom (MW) | 25.3534 | 25.374 | 25.9584 | 25.5239 | 25.2227 | 24.4541 | 23.4597 | 22.2298 | 20.6233 | 18.6914 | 16.6847 | 13.6471 | 11.1085 | 7.9291 | 4.9862 | 0.35466 | -17.8366 | -32.1488 | -35.6302
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Consumer Transformation | Thermal headroom (MW) | 2.3821 | 2.3866 | 2.4188 | 2.3954 | 2.2874 | 2.1541 | 1.969 | 1.7691 | 1.5437 | 1.3197 | 1.0945 | 0.80554 | 0.54837 | 0.32991 | 0.16145 | 0.026059 | -0.8056 | -1.2107 | -1.2604
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Leading the Way | Thermal headroom (MW) | 2.3824 | 2.3879 | 2.4259 | 2.4044 | 2.3009 | 2.1651 | 1.9789 | 1.7683 | 1.535 | 1.292 | 1.0057 | 0.75581 | 0.5519 | 0.40259 | 0.33651 | 0.12522 | -0.63424 | -0.66548 | -0.24139
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Steady Progression | Thermal headroom (MW) | 2.3889 | 2.4178 | 2.4787 | 2.5087 | 2.5362 | 2.549 | 2.5126 | 2.4546 | 2.3826 | 2.2924 | 2.1828 | 2.0471 | 1.8934 | 1.7153 | 1.5283 | 1.3292 | 0.081424 | -0.57314 | -0.77243
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | System Transformation | Thermal headroom (MW) | 2.3884 | 2.4136 | 2.4738 | 2.5016 | 2.5236 | 2.5044 | 2.438 | 2.3483 | 2.2342 | 2.0889 | 1.9173 | 1.705 | 1.4644 | 1.1956 | 0.90322 | 0.59607 | -0.50922 | -0.73788 | -0.71484
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | WPD Best View | Thermal headroom (MW) | 2.3876 | 2.4149 | 2.4727 | 2.499 | 2.5002 | 2.4592 | 2.385 | 2.2942 | 2.1848 | 2.0628 | 1.93 | 1.7811 | 1.627 | 1.4536 | 1.2721 | 1.084 | 0.1122 | -0.34609 | -0.47761
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Consumer Transformation | Thermal headroom (MW) | 1.4162 | 1.2359 | 1.0771 | 0.87938 | 0.65919 | 0.41991 | 0.091098 | -0.2258 | -0.55324 | -1.2548 | -1.5776 | -1.8918 | -2.1917 | -2.5031 | -2.7626 | -2.9831 | -4.5736 | -5.5209 | -5.5002
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Leading the Way | Thermal headroom (MW) | 1.3992 | 1.2237 | 1.0977 | 0.91277 | 0.69733 | 0.4682 | 0.15097 | -0.16511 | -0.8485 | -1.2154 | -1.5445 | -1.7931 | -2.0764 | -2.2824 | -2.4255 | -2.9745 | -3.9383 | -4.0302 | -3.926
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Steady Progression | Thermal headroom (MW) | 1.4703 | 1.4741 | 1.5232 | 1.5195 | 1.5098 | 1.4853 | 1.4477 | 1.3921 | 1.3248 | 1.2444 | 1.1011 | 0.9506 | 0.76809 | 0.56466 | 0.34989 | -0.25594 | -1.681 | -3.1569 | -3.5734
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | System Transformation | Thermal headroom (MW) | 1.4401 | 1.4141 | 1.437 | 1.4016 | 1.3635 | 1.3043 | 1.1924 | 1.0517 | 0.89554 | 0.7037 | 0.4889 | -0.1291 | -0.42912 | -0.75139 | -1.0718 | -1.388 | -3.1158 | -3.9531 | -4.2724
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | WPD Best View | Thermal headroom (MW) | 1.4703 | 1.4741 | 1.5232 | 1.5195 | 1.5098 | 1.4853 | 1.4477 | 1.3921 | 1.3248 | 1.2444 | 1.1011 | 0.9506 | 0.76809 | 0.56466 | 0.34989 | -0.25594 | -1.681 | -3.1569 | -3.5734
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Consumer Transformation | Thermal headroom (MW) | 1.8253 | 1.4426 | 1.076 | 0.62672 | 0.14744 | -0.35366 | -0.8858 | -1.3984 | -1.9592 | -3.2376 | -3.7943 | -4.2052 | -4.5582 | -4.9484 | -5.2749 | -5.551 | -7.3754 | -8.3572 | -7.8378
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Leading the Way | Thermal headroom (MW) | 1.7966 | 1.4313 | 1.1127 | 0.68056 | 0.23681 | -0.28965 | -0.85654 | -1.3305 | -2.6295 | -3.2114 | -3.7668 | -4.1428 | -4.5397 | -4.8566 | -5.0228 | -5.8991 | -6.9639 | -6.3743 | -6.1438
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Steady Progression | Thermal headroom (MW) | 1.968 | 1.9954 | 2.1056 | 2.1063 | 2.0804 | 2.0568 | 2.0034 | 1.9152 | 1.7935 | 1.6336 | 1.429 | 1.1064 | 0.75884 | 0.35489 | -0.053288 | -1.2373 | -3.7758 | -6.6224 | -7.4879
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | System Transformation | Thermal headroom (MW) | 1.8858 | 1.8339 | 1.8512 | 1.7597 | 1.6505 | 1.5339 | 1.2679 | 0.96624 | 0.61961 | 0.22545 | -0.19771 | -1.4644 | -2.0765 | -2.7238 | -3.3601 | -3.9793 | -7.0554 | -8.4931 | -8.943
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | WPD Best View | Thermal headroom (MW) | 1.8918 | 1.7054 | 1.5574 | 1.3126 | 1.0467 | 0.76782 | 0.45193 | 0.13142 | -0.23328 | -0.97367 | -1.3646 | -1.7373 | -2.0847 | -2.4092 | -2.6998 | -3.4417 | -5.326 | -6.8855 | -6.8547
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Consumer Transformation | Thermal headroom (MW) | 11.9544 | 11.8201 | 11.7752 | 11.6235 | 11.4993 | 11.2606 | 10.9331 | 10.628 | 10.3146 | 9.5931 | 9.2054 | 8.6704 | 8.0752 | 7.5659 | 7.0474 | 6.6028 | 4.6186 | 3.8899 | 4.1879
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Leading the Way | Thermal headroom (MW) | 11.9456 | 11.8153 | 11.8132 | 11.6964 | 11.554 | 11.3387 | 11.0031 | 10.6899 | 10.0028 | 9.6197 | 9.1969 | 8.7788 | 8.2543 | 7.8291 | 7.3975 | 6.7363 | 5.8769 | 5.9392 | 6.3675
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Steady Progression | Thermal headroom (MW) | 11.9964 | 12.0846 | 12.2513 | 12.3306 | 12.4023 | 12.4831 | 12.5529 | 12.586 | 12.6045 | 12.6164 | 12.6251 | 12.5835 | 12.5082 | 12.4559 | 12.387 | 11.8755 | 11.0242 | 9.6363 | 9.4276
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | System Transformation | Thermal headroom (MW) | 11.9691 | 12.0318 | 12.1555 | 12.2253 | 12.2728 | 12.2878 | 12.2739 | 12.2276 | 12.2006 | 12.1547 | 12.0876 | 11.6059 | 11.4392 | 11.2654 | 11.0342 | 10.8304 | 9.2855 | 8.3251 | 8.203
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | WPD Best View | Thermal headroom (MW) | 11.9964 | 12.0846 | 12.2513 | 12.3306 | 12.4023 | 12.4831 | 12.5529 | 12.586 | 12.6045 | 12.6164 | 12.6251 | 12.5835 | 12.5082 | 12.4559 | 12.387 | 11.8755 | 11.0242 | 9.6363 | 9.4276
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Consumer Transformation | Thermal headroom (MW) | 9.0471 | 8.7063 | 8.4632 | 7.7279 | 7.3181 | 6.5034 | 5.4079 | 4.0609 | 3.0873 | 2.1122 | 0.8041 | -0.4023 | -2.3537 | -3.9053 | -5.7896 | -7.6336 | -13.6161 | -15.5682 | -15.8593
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Leading the Way | Thermal headroom (MW) | 9.0077 | 8.6553 | 8.4583 | 7.5861 | 7.1805 | 6.3692 | 4.878 | 3.8964 | 2.8676 | 1.5465 | 0.69625 | -0.68085 | -1.9318 | -3.6265 | -5.1926 | -6.2403 | -9.807 | -10.6163 | -9.0634
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Steady Progression | Thermal headroom (MW) | 9.1297 | 9.157 | 9.2987 | 9.051 | 9.0274 | 8.9543 | 8.8502 | 8.703 | 8.5577 | 8.3684 | 8.129 | 7.7499 | 7.4005 | 6.6021 | 6.1806 | 5.7171 | 2.4511 | -0.74213 | -2.0108
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | System Transformation | Thermal headroom (MW) | 9.0673 | 9.0398 | 9.1289 | 8.7246 | 8.6361 | 8.4746 | 8.2212 | 7.9225 | 7.6017 | 7.2345 | 6.4837 | 5.8664 | 4.9776 | 4.3538 | 3.4379 | 2.5249 | -1.5891 | -4.6249 | -5.1528
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | WPD Best View | Thermal headroom (MW) | 9.1297 | 9.157 | 9.2987 | 9.051 | 9.0274 | 8.9543 | 8.8502 | 8.703 | 8.5577 | 8.3684 | 8.129 | 7.7499 | 7.4005 | 6.6021 | 6.1806 | 5.7171 | 2.4511 | -0.74213 | -2.0108
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Consumer Transformation | Thermal headroom (MW) | 3.1765 | 2.7617 | 2.428 | 1.6043 | 0.79215 | 0.25837 | -0.39452 | -0.98364 | -1.5966 | -2.6348 | -3.3602 | -4.4829 | -5.3558 | -6.0618 | -7.1587 | -7.8795 | -11.2488 | -12.2745 | -11.5903
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Leading the Way | Thermal headroom (MW) | 3.124 | 2.7106 | 2.1539 | 1.2497 | 0.8226 | 0.30664 | -0.37631 | -0.97583 | -1.9392 | -2.7095 | -3.4885 | -4.5137 | -5.3612 | -6.0969 | -7.1845 | -8.1612 | -9.6312 | -9.3665 | -8.5856
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Steady Progression | Thermal headroom (MW) | 3.3498 | 3.4115 | 3.593 | 3.5957 | 3.3627 | 3.4335 | 3.4056 | 3.4361 | 3.4632 | 3.4552 | 3.3502 | 2.7625 | 2.4474 | 2.1243 | 1.772 | 1.0426 | -1.4244 | -5.0003 | -6.3663
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | System Transformation | Thermal headroom (MW) | 3.2416 | 3.2114 | 3.2898 | 2.9142 | 2.8173 | 2.7701 | 2.6322 | 2.4221 | 1.8369 | 1.5882 | 1.2676 | 0.51509 | -0.051061 | -0.96981 | -1.4914 | -2.0048 | -5.9727 | -8.6062 | -9.125
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | WPD Best View | Thermal headroom (MW) | 3.2864 | 3.2969 | 3.4153 | 3.0833 | 3.0279 | 3.0126 | 2.9713 | 2.8666 | 2.4279 | 2.2954 | 2.0504 | 1.7895 | 1.3589 | 0.56135 | 0.12618 | -0.6875 | -4.0511 | -7.297 | -7.9919
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Consumer Transformation | Thermal headroom (MW) | 0.49537 | 0.30727 | 0.12408 | -0.099162 | -0.36828 | -0.70393 | -1.1887 | -1.6274 | -2.0597 | -2.868 | -3.2863 | -3.7168 | -4.1725 | -4.5718 | -4.9087 | -5.1881 | -6.9624 | -8.0874 | -8.124
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Leading the Way | Thermal headroom (MW) | 0.47936 | 0.29543 | 0.14041 | -0.085785 | -0.34645 | -0.67443 | -1.1658 | -1.6172 | -2.4072 | -2.8854 | -3.2686 | -3.6545 | -4.0113 | -4.2702 | -4.4443 | -4.8976 | -6.1302 | -6.2321 | -6.0066
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Steady Progression | Thermal headroom (MW) | 0.54991 | 0.54137 | 0.56156 | 0.53755 | 0.49756 | 0.43709 | 0.32968 | 0.21858 | 0.098623 | -0.047325 | -0.23898 | -0.45323 | -0.70524 | -0.98262 | -1.2851 | -1.9842 | -3.9405 | -5.7431 | -6.2409
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | System Transformation | Thermal headroom (MW) | 0.52556 | 0.48308 | 0.47981 | 0.41475 | 0.34478 | 0.22007 | 0.040739 | -0.15003 | -0.35813 | -0.62128 | -0.90459 | -1.6153 | -2.019 | -2.4454 | -2.8701 | -3.3206 | -5.5071 | -6.4868 | -6.8196
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | WPD Best View | Thermal headroom (MW) | 0.52531 | 0.48787 | 0.48581 | 0.42974 | 0.36432 | 0.25287 | 0.085838 | -0.089591 | -0.27084 | -0.50178 | -0.75127 | -1.4143 | -1.7647 | -2.1413 | -2.525 | -2.9049 | -5.1822 | -6.5326 | -7.0152
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Consumer Transformation | Thermal headroom (MW) | 5.0677 | 4.1668 | 3.7542 | 2.3801 | 1.1039 | -0.64171 | -3.6297 | -6.7076 | -10.0207 | -14.0427 | -17.43 | -21.6217 | -25.5321 | -29.6127 | -33.1147 | -36.4359 | -51.2372 | -59.1495 | -59.4637
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Leading the Way | Thermal headroom (MW) | 4.9581 | 3.9704 | 3.5356 | 2.6167 | 1.4232 | -0.3074 | -3.3334 | -6.3205 | -10.306 | -14.0719 | -17.6911 | -21.4403 | -24.9189 | -28.1142 | -31.389 | -35.2284 | -46.0886 | -46.8781 | -39.92
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Steady Progression | Thermal headroom (MW) | 5.4536 | 5.8112 | 6.8895 | 7.1404 | 6.9562 | 7.2114 | 7.2985 | 7.1503 | 6.5707 | 5.788 | 4.689 | 3.0836 | 1.3518 | -0.89723 | -3.3626 | -6.6533 | -21.9928 | -33.424 | -37.0218
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | System Transformation | Thermal headroom (MW) | 5.2349 | 5.4316 | 6.192 | 5.9992 | 6.104 | 6.1228 | 5.7536 | 4.8557 | 3.5837 | 1.907 | -0.017575 | -3.2932 | -6.2804 | -10.0024 | -13.8938 | -17.876 | -33.9431 | -39.9521 | -39.765
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | WPD Best View | Thermal headroom (MW) | 5.0677 | 4.1668 | 3.7542 | 2.3801 | 1.0743 | -0.64171 | -3.6297 | -6.7076 | -10.0207 | -14.0427 | -17.43 | -21.6217 | -25.5321 | -29.6127 | -33.1147 | -36.4359 | -51.2372 | -59.1495 | -59.4637
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Consumer Transformation | Thermal headroom (MW) | 14.9145 | 14.8893 | 14.9013 | 14.8662 | 14.8156 | 14.727 | 14.4789 | 14.2184 | 13.9382 | 13.659 | 13.3843 | 13.0896 | 12.8314 | 12.5585 | 12.3459 | 12.1449 | 10.7513 | 9.7429 | 9.419
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Leading the Way | Thermal headroom (MW) | 14.911 | 14.8868 | 14.9244 | 14.9076 | 14.8693 | 14.7675 | 14.5224 | 14.2633 | 13.9654 | 13.6637 | 13.3758 | 13.1647 | 12.9047 | 12.7343 | 12.3699 | 12.0212 | 11.1645 | 10.8328 | 11.4786
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Steady Progression | Thermal headroom (MW) | 14.9353 | 14.989 | 15.1078 | 15.1703 | 15.2266 | 15.2826 | 15.3116 | 15.349 | 15.2913 | 15.2104 | 15.1073 | 14.9611 | 14.7971 | 14.6105 | 14.4071 | 14.1715 | 12.8733 | 11.7034 | 11.1851
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | System Transformation | Thermal headroom (MW) | 14.921 | 14.9683 | 15.0798 | 15.1276 | 15.1764 | 15.218 | 15.222 | 15.158 | 15.0286 | 14.8783 | 14.689 | 14.4428 | 14.1708 | 13.8676 | 13.559 | 13.2733 | 12.0334 | 11.2406 | 10.9944
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | WPD Best View | Thermal headroom (MW) | 14.9145 | 14.8893 | 14.9013 | 14.8662 | 14.8156 | 14.727 | 14.4789 | 14.2184 | 13.9382 | 13.659 | 13.3843 | 13.0896 | 12.8314 | 12.5585 | 12.3459 | 12.1449 | 10.7513 | 9.7429 | 9.419
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Consumer Transformation | Thermal headroom (MW) | 4.7556 | 4.6203 | 4.5921 | 4.3668 | 4.1796 | 3.9644 | 3.4441 | 2.9315 | 2.3862 | 1.8553 | 1.3652 | 0.43293 | -0.21679 | -0.79316 | -1.1415 | -1.7632 | -4.1626 | -5.7129 | -5.7861
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Leading the Way | Thermal headroom (MW) | 4.7338 | 4.6119 | 4.6122 | 4.4281 | 4.2709 | 4.084 | 3.5882 | 3.0831 | 2.5278 | 1.9865 | 1.4875 | 0.68353 | 0.21972 | -0.10609 | -0.326 | -0.9887 | -2.9909 | -3.304 | -2.0659
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Steady Progression | Thermal headroom (MW) | 4.8267 | 4.9373 | 5.2056 | 5.2917 | 5.3588 | 5.4503 | 5.5171 | 5.5518 | 5.5574 | 5.5296 | 5.4462 | 5.0974 | 4.8154 | 4.496 | 4.2154 | 3.7543 | 1.9482 | 0.30128 | -0.21317
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | System Transformation | Thermal headroom (MW) | 4.791 | 4.8808 | 5.1189 | 5.1472 | 5.223 | 5.2606 | 5.2571 | 5.2222 | 5.1309 | 4.9632 | 4.746 | 4.1346 | 3.65 | 3.1179 | 2.7029 | 2.024 | 0.32864 | -0.47474 | -0.1762
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | WPD Best View | Thermal headroom (MW) | 4.7556 | 4.6203 | 4.5921 | 4.3668 | 4.1796 | 3.9644 | 3.4441 | 2.9315 | 2.3862 | 1.8553 | 1.3652 | 0.43293 | -0.21679 | -0.79316 | -1.1415 | -1.7632 | -4.1626 | -5.7129 | -5.7861
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Consumer Transformation | Thermal headroom (MW) | 6.4083 | 6.3039 | 6.2496 | 5.62 | 5.4868 | 5.2665 | 4.8475 | 4.4416 | 3.9601 | 3.4049 | 2.8176 | 2.0428 | 1.2443 | 0.0065297 | -1.312 | -2.4749 | -6.2629 | -7.6515 | -7.4128
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Leading the Way | Thermal headroom (MW) | 6.4071 | 6.2349 | 5.8145 | 5.6814 | 5.5349 | 5.3459 | 4.909 | 4.4816 | 4.013 | 3.3822 | 2.7317 | 2.0133 | 1.2518 | -0.15929 | -1.6329 | -2.7958 | -5.1993 | -5.0024 | -3.3487
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Steady Progression | Thermal headroom (MW) | 6.496 | 6.6034 | 6.8512 | 6.8751 | 6.5171 | 6.5828 | 6.6345 | 6.6802 | 6.665 | 6.6679 | 6.6358 | 6.5511 | 6.424 | 5.9986 | 5.5045 | 5.0065 | 2.2868 | -0.19932 | -0.9685
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | System Transformation | Thermal headroom (MW) | 6.4416 | 6.53 | 6.663 | 6.2407 | 6.3328 | 6.3795 | 6.3899 | 6.3707 | 6.3003 | 6.1672 | 6.0558 | 5.8144 | 5.4927 | 4.6619 | 3.7525 | 2.9273 | -0.82611 | -2.5453 | -2.1126
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | WPD Best View | Thermal headroom (MW) | 6.4083 | 6.3039 | 6.2496 | 5.62 | 5.4868 | 5.2665 | 4.8475 | 4.4416 | 3.9601 | 3.4049 | 2.8176 | 2.0428 | 1.2443 | 0.0065297 | -1.312 | -2.4749 | -6.2629 | -7.6515 | -7.4128
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Consumer Transformation | Thermal headroom (MW) | 5.5422 | 5.5172 | 5.5467 | 5.5107 | 5.4446 | 5.2038 | 4.895 | 4.5562 | 4.1962 | 3.4539 | 3.092 | 2.7572 | 2.3765 | 2.0325 | 1.7773 | 1.5745 | -0.17123 | -0.86412 | -0.62864
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Leading the Way | Thermal headroom (MW) | 5.5268 | 5.5117 | 5.5709 | 5.5321 | 5.4753 | 5.2246 | 4.9115 | 4.5699 | 3.828 | 3.4078 | 3.0482 | 2.6763 | 2.3116 | 2.0894 | 1.802 | 0.96917 | -0.030965 | 0.27166 | 0.85
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Steady Progression | Thermal headroom (MW) | 5.575 | 5.6444 | 5.791 | 5.8618 | 5.9082 | 5.9764 | 6.0291 | 5.9822 | 5.8751 | 5.737 | 5.5574 | 5.3334 | 5.0764 | 4.777 | 4.4557 | 3.7495 | 1.848 | 0.62298 | 0.37519
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | System Transformation | Thermal headroom (MW) | 5.5531 | 5.6098 | 5.7376 | 5.799 | 5.8503 | 5.8776 | 5.8295 | 5.6722 | 5.4519 | 5.1987 | 4.8955 | 4.1772 | 3.7577 | 3.2907 | 2.8169 | 2.3591 | 0.22251 | -0.29615 | -0.43041
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | WPD Best View | Thermal headroom (MW) | 5.5422 | 5.5172 | 5.5467 | 5.5107 | 5.4245 | 5.2038 | 4.895 | 4.5562 | 4.1962 | 3.4539 | 3.092 | 2.7572 | 2.3765 | 2.0325 | 1.7773 | 1.5745 | -0.17123 | -0.86412 | -0.62864
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Consumer Transformation | Thermal headroom (MW) | 5.8355 | 5.7947 | 5.9215 | 5.8947 | 5.7166 | 5.6214 | 5.3788 | 5.1367 | 4.8326 | 4.4248 | 4.0579 | 3.5258 | 3.0024 | 2.4576 | 1.9014 | 1.3173 | -0.69862 | -1.3256 | -1.0975
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Leading the Way | Thermal headroom (MW) | 5.8341 | 5.782 | 5.9319 | 5.9196 | 5.7073 | 5.6193 | 5.3526 | 5.1038 | 4.7996 | 4.3316 | 3.9227 | 3.4745 | 3.0092 | 2.5364 | 2.0777 | 1.6841 | 0.57426 | 0.58294 | 1.7788
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Steady Progression | Thermal headroom (MW) | 5.8641 | 5.9977 | 6.2922 | 6.4006 | 6.4332 | 6.5711 | 6.6938 | 6.7867 | 6.8876 | 6.9136 | 6.9611 | 6.982 | 6.9465 | 6.956 | 6.8672 | 6.7971 | 5.8631 | 4.7485 | 4.7683
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | System Transformation | Thermal headroom (MW) | 5.853 | 5.9365 | 6.2038 | 6.3085 | 6.3008 | 6.4232 | 6.532 | 6.5918 | 6.6282 | 6.5688 | 6.5417 | 6.4556 | 6.3508 | 6.2105 | 6.0219 | 5.7591 | 4.3424 | 3.7452 | 4.1874
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | WPD Best View | Thermal headroom (MW) | 5.8355 | 5.7947 | 5.9215 | 5.8947 | 5.7166 | 5.6214 | 5.3788 | 5.1367 | 4.8326 | 4.4248 | 4.0579 | 3.5258 | 3.0024 | 2.4576 | 1.9014 | 1.3173 | -0.69862 | -1.3256 | -1.0975
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Consumer Transformation | Thermal headroom (MW) | 0.48061 | 0.21239 | -0.010506 | -0.27461 | -0.59101 | -0.95806 | -1.4871 | -2.033 | -2.5976 | -3.1746 | -3.738 | -4.4014 | -5.0262 | -5.6099 | -6.0889 | -6.4872 | -8.0725 | -9.1254 | -9.2775
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Leading the Way | Thermal headroom (MW) | 0.45316 | 0.1611 | -0.0077927 | -0.26596 | -0.55661 | -0.92131 | -1.4611 | -1.9597 | -2.5591 | -3.1664 | -3.7856 | -4.3847 | -4.9187 | -5.322 | -5.5771 | -5.7219 | -7.3645 | -7.6032 | -6.7651
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Steady Progression | Thermal headroom (MW) | 0.55132 | 0.50702 | 0.5289 | 0.47278 | 0.4019 | 0.33006 | 0.23365 | 0.11311 | -0.053267 | -0.24154 | -0.50126 | -0.80906 | -1.1261 | -1.5284 | -1.9568 | -2.4192 | -5.0974 | -6.6738 | -7.2585
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | System Transformation | Thermal headroom (MW) | 0.51394 | 0.44107 | 0.3975 | 0.33091 | 0.25183 | 0.14274 | -0.027854 | -0.26931 | -0.53847 | -0.87187 | -1.2513 | -1.7219 | -2.2463 | -2.8433 | -3.5022 | -4.1502 | -6.5875 | -7.2328 | -7.239
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | WPD Best View | Thermal headroom (MW) | 0.48061 | 0.21239 | -0.010506 | -0.27461 | -0.59101 | -0.95806 | -1.4871 | -2.033 | -2.5976 | -3.1746 | -3.738 | -4.4014 | -5.0262 | -5.6099 | -6.0889 | -6.4872 | -8.0725 | -9.1254 | -9.2775
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Consumer Transformation | Thermal headroom (MW) | 18.8801 | 18.2104 | 17.5932 | 16.7309 | 15.6584 | 14.3215 | 12.3241 | 10.2247 | 8.0916 | 5.0082 | 2.9439 | 0.42255 | -1.8821 | -3.9938 | -6.2167 | -8.0515 | -16.367 | -20.996 | -21.1782
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Leading the Way | Thermal headroom (MW) | 18.8357 | 18.1093 | 17.5322 | 16.4802 | 15.5379 | 14.1758 | 12.1621 | 10.0442 | 6.8644 | 4.4987 | 2.3759 | 0.48341 | -1.3471 | -3.0234 | -4.425 | -6.26 | -11.5699 | -12.3235 | -9.3704
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Steady Progression | Thermal headroom (MW) | 19.0717 | 19.1724 | 19.5382 | 19.5643 | 19.5848 | 19.5068 | 19.4298 | 19.1556 | 18.728 | 18.2439 | 17.6349 | 16.7266 | 15.7913 | 14.7422 | 13.5114 | 11.273 | 3.0855 | -4.1441 | -6.1265
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | System Transformation | Thermal headroom (MW) | 18.9974 | 19.0172 | 19.2322 | 19.166 | 19.0404 | 18.8262 | 18.3759 | 17.75 | 16.7721 | 15.7775 | 14.723 | 12.5511 | 10.9343 | 8.9819 | 7.1479 | 5.3149 | -4.4249 | -8.6289 | -9.076
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | WPD Best View | Thermal headroom (MW) | 18.8794 | 18.2097 | 17.5913 | 16.73 | 15.6574 | 14.3205 | 12.324 | 10.2238 | 8.0906 | 4.9972 | 2.9363 | 0.41332 | -1.8943 | -4.0082 | -6.2333 | -8.0691 | -16.3581 | -20.9557 | -21.11
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Consumer Transformation | Thermal headroom (MW) | 2.724 | 2.5159 | 2.2699 | 1.95 | 1.6301 | 1.2445 | 0.64197 | -0.011395 | -0.72037 | -2.1416 | -2.7729 | -3.4791 | -4.1562 | -4.839 | -5.3763 | -5.8279 | -8.1765 | -10.1819 | -10.3382
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Leading the Way | Thermal headroom (MW) | 2.7188 | 2.5147 | 2.2884 | 1.9491 | 1.6506 | 1.2694 | 0.66438 | -0.001192 | -1.4548 | -2.1723 | -2.8299 | -3.355 | -3.9103 | -4.3057 | -4.5392 | -5.4204 | -7.0211 | -7.4069 | -7.1025
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Steady Progression | Thermal headroom (MW) | 2.7808 | 2.8088 | 2.8603 | 2.8285 | 2.8071 | 2.7298 | 2.6517 | 2.5149 | 2.3535 | 2.1627 | 1.9206 | 1.6013 | 1.2489 | 0.8503 | 0.40813 | -0.78661 | -3.5003 | -5.9992 | -6.5628
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | System Transformation | Thermal headroom (MW) | 2.762 | 2.7627 | 2.7662 | 2.6948 | 2.6123 | 2.5205 | 2.3547 | 2.1369 | 1.8475 | 1.4853 | 1.0818 | -0.13452 | -0.68901 | -1.2985 | -1.9133 | -2.5182 | -5.8114 | -7.2691 | -7.9195
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | WPD Best View | Thermal headroom (MW) | 2.724 | 2.5159 | 2.2699 | 1.95 | 1.6301 | 1.2445 | 0.64197 | -0.011395 | -0.72037 | -2.1416 | -2.7729 | -3.4791 | -4.1562 | -4.839 | -5.3763 | -5.8279 | -8.1765 | -10.1819 | -10.3382
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Consumer Transformation | Thermal headroom (MW) | 17.9308 | 17.8192 | 17.7274 | 17.5863 | 17.4129 | 17.1898 | 16.88 | 16.5997 | 16.3083 | 16.0111 | 15.7326 | 15.432 | 15.1755 | 14.9265 | 14.6893 | 14.5116 | 13.5444 | 13.1951 | 13.316
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Leading the Way | Thermal headroom (MW) | 17.9242 | 17.8306 | 17.7645 | 17.6281 | 17.4686 | 17.2482 | 16.9305 | 16.6613 | 16.3525 | 16.0365 | 15.752 | 15.5435 | 15.3445 | 15.1497 | 15.0528 | 15.0027 | 14.2263 | 14.2549 | 14.8119
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Steady Progression | Thermal headroom (MW) | 17.9656 | 17.9999 | 18.0776 | 18.0961 | 18.0976 | 18.0851 | 18.0573 | 18.0226 | 17.9595 | 17.8857 | 17.7861 | 17.649 | 17.4922 | 17.3137 | 17.1223 | 16.9175 | 15.8214 | 15.2012 | 15.0133
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | System Transformation | Thermal headroom (MW) | 17.9462 | 17.9644 | 18.0221 | 18.0205 | 17.9944 | 17.9455 | 17.8481 | 17.7618 | 17.632 | 17.4719 | 17.3028 | 17.0696 | 16.8175 | 16.5341 | 16.2513 | 15.9876 | 14.9328 | 14.7525 | 14.9014
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | WPD Best View | Thermal headroom (MW) | 17.9308 | 17.8192 | 17.7274 | 17.5863 | 17.4129 | 17.1898 | 16.88 | 16.5997 | 16.3083 | 16.0111 | 15.7326 | 15.432 | 15.1755 | 14.9265 | 14.6893 | 14.5116 | 13.5444 | 13.1951 | 13.316
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Consumer Transformation | Thermal headroom (MW) | 17.6414 | 17.158 | 16.6222 | 16.0357 | 15.026 | 13.9485 | 12.3328 | 10.5001 | 8.7225 | 6.77 | 4.962 | 2.3445 | -0.13231 | -2.3914 | -5.079 | -7.3334 | -17.0801 | -21.3301 | -22.708
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Leading the Way | Thermal headroom (MW) | 17.6269 | 17.0276 | 16.4496 | 15.4703 | 14.675 | 13.495 | 11.882 | 9.9294 | 7.9172 | 5.6184 | 3.6148 | 1.4098 | -0.73412 | -2.7211 | -4.9561 | -6.5816 | -12.2891 | -14.0382 | -11.6069
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Steady Progression | Thermal headroom (MW) | 17.7383 | 17.7306 | 17.8229 | 17.8089 | 17.7452 | 17.6695 | 17.7083 | 17.5101 | 17.104 | 16.6581 | 16.223 | 15.4415 | 14.802 | 14.146 | 13.3856 | 12.5369 | 5.6432 | -2.3702 | -5.3446
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | System Transformation | Thermal headroom (MW) | 17.7404 | 17.7479 | 17.7911 | 17.7752 | 17.653 | 17.4743 | 17.1947 | 16.5984 | 15.5495 | 14.75 | 14.0619 | 13.381 | 12.2778 | 10.7559 | 9.5037 | 8.1169 | -1.4597 | -7.1746 | -7.9444
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | WPD Best View | Thermal headroom (MW) | 17.6397 | 17.1564 | 16.6174 | 16.0334 | 15.0235 | 13.9461 | 12.3328 | 10.4977 | 8.7198 | 6.7591 | 4.9466 | 2.3214 | -0.16296 | -2.4274 | -5.1204 | -7.3774 | -17.058 | -21.2296 | -22.5379
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Consumer Transformation | Thermal headroom (MW) | 10.4428 | 10.5617 | 10.7796 | 10.9029 | 11.0209 | 11.1324 | 11.2363 | 11.3217 | 11.4073 | 11.4704 | 11.4869 | 11.4781 | 11.4923 | 11.5386 | 11.486 | 11.4306 | 11.3143 | 11.5273 | 11.9139
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Leading the Way | Thermal headroom (MW) | 10.4428 | 10.5449 | 10.7805 | 10.9024 | 11.02 | 11.1304 | 11.233 | 11.3251 | 11.4056 | 11.4465 | 11.4586 | 11.4722 | 11.4451 | 11.3756 | 11.2948 | 11.2335 | 11.3259 | 11.7925 | 12.4404
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Steady Progression | Thermal headroom (MW) | 10.4454 | 10.5674 | 10.8086 | 10.9223 | 11.0502 | 11.175 | 11.2959 | 11.4138 | 11.5285 | 11.6388 | 11.7242 | 11.8277 | 11.9239 | 12.0014 | 11.9809 | 11.9463 | 11.7153 | 11.79 | 12.0205
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | System Transformation | Thermal headroom (MW) | 10.4454 | 10.5664 | 10.7904 | 10.9194 | 11.0462 | 11.1683 | 11.2865 | 11.4007 | 11.5091 | 11.6111 | 11.69 | 11.7779 | 11.7634 | 11.691 | 11.6306 | 11.5654 | 11.555 | 11.6832 | 12.111
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | WPD Best View | Thermal headroom (MW) | 10.4428 | 10.5617 | 10.7796 | 10.9029 | 11.0209 | 11.1324 | 11.2363 | 11.3217 | 11.4073 | 11.46 | 11.4848 | 11.4781 | 11.4923 | 11.5386 | 11.486 | 11.4306 | 11.3143 | 11.5273 | 11.9139
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Consumer Transformation | Thermal headroom (MW) | 36.9702 | 36.5149 | 36.2839 | 35.7876 | 34.986 | 34.1702 | 32.7715 | 31.0611 | 29.5166 | 27.3832 | 25.4821 | 23.395 | 21.1865 | 19.1099 | 16.5868 | 14.2393 | 5.1136 | 0.53423 | -0.20319
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Leading the Way | Thermal headroom (MW) | 36.9256 | 36.4516 | 36.2778 | 35.6128 | 34.9399 | 34.1252 | 32.4637 | 30.9365 | 28.7301 | 26.8354 | 25.0648 | 23.2163 | 21.3961 | 19.3529 | 17.2756 | 15.3125 | 9.7859 | 8.438 | 11.577
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Steady Progression | Thermal headroom (MW) | 37.1281 | 37.2814 | 37.7923 | 37.977 | 38.0641 | 38.1965 | 38.2124 | 38.1496 | 38.013 | 37.8781 | 37.555 | 36.9649 | 36.4617 | 35.591 | 34.8823 | 33.4936 | 27.5286 | 20.5937 | 18.9366
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | System Transformation | Thermal headroom (MW) | 37.0478 | 37.1254 | 37.5314 | 37.6053 | 37.6302 | 37.5949 | 37.4751 | 37.1636 | 36.5875 | 36.1551 | 35.2166 | 33.8161 | 32.6314 | 31.3747 | 29.949 | 28.4707 | 19.6007 | 14.7513 | 14.1721
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | WPD Best View | Thermal headroom (MW) | 36.9702 | 36.5149 | 36.2839 | 35.7876 | 34.986 | 34.1702 | 32.7715 | 31.0611 | 29.5166 | 27.3832 | 25.4821 | 23.395 | 21.1865 | 19.1099 | 16.5868 | 14.2393 | 5.1136 | 0.53423 | -0.20319
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Consumer Transformation | Thermal headroom (MW) | 7.782 | 7.5697 | 7.5357 | 7.2919 | 6.6238 | 6.1852 | 5.4275 | 4.6768 | 3.7474 | 2.5378 | 1.6779 | 0.24445 | -1.0329 | -2.8226 | -4.9867 | -6.8402 | -14.849 | -18.4693 | -19.0881
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Leading the Way | Thermal headroom (MW) | 7.7597 | 7.5662 | 7.5791 | 7.0024 | 6.6989 | 6.2531 | 5.4876 | 4.7528 | 3.3949 | 2.478 | 1.6041 | 0.47973 | -1.1901 | -2.8338 | -4.8351 | -6.5753 | -11.3311 | -12.5088 | -10.4404
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Steady Progression | Thermal headroom (MW) | 7.8657 | 8.0112 | 8.3869 | 8.5376 | 8.6498 | 8.7431 | 8.8283 | 8.8756 | 8.8106 | 8.7695 | 8.6694 | 8.0225 | 7.721 | 7.3491 | 6.94 | 6.1239 | 2.9096 | -2.8033 | -4.6314
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | System Transformation | Thermal headroom (MW) | 7.8208 | 7.9445 | 8.292 | 8.4023 | 8.4857 | 8.5025 | 8.4761 | 8.4086 | 7.8177 | 7.6206 | 7.2595 | 6.4139 | 5.8402 | 4.8685 | 4.2175 | 3.5543 | -2.6199 | -7.2148 | -7.883
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | WPD Best View | Thermal headroom (MW) | 7.782 | 7.5697 | 7.5357 | 7.2919 | 6.6238 | 6.1852 | 5.4275 | 4.6768 | 3.7474 | 2.5378 | 1.6779 | 0.24445 | -1.0329 | -2.8226 | -4.9867 | -6.8402 | -14.849 | -18.4693 | -19.0881
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Consumer Transformation | Thermal headroom (MW) | 2.2382 | 1.9497 | 1.6817 | 1.3718 | 1.0723 | 0.63037 | 0.013566 | -0.60396 | -1.2111 | -2.1409 | -2.6948 | -3.2765 | -3.7796 | -4.1765 | -4.5983 | -4.9413 | -6.2119 | -7.3321 | -7.2136
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Leading the Way | Thermal headroom (MW) | 2.205 | 1.8791 | 1.6014 | 1.2629 | 0.97252 | 0.54258 | -0.078853 | -0.66922 | -1.6515 | -2.1965 | -2.6785 | -3.0416 | -3.3026 | -3.598 | -3.7541 | -4.1706 | -4.9875 | -5.0646 | -4.3673
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Steady Progression | Thermal headroom (MW) | 2.3093 | 2.2473 | 2.2758 | 2.2232 | 2.1973 | 2.1395 | 2.0547 | 1.9168 | 1.7693 | 1.6255 | 1.4378 | 1.1795 | 0.89039 | 0.56806 | 0.21712 | -0.52559 | -2.3912 | -3.7762 | -4.0271
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | System Transformation | Thermal headroom (MW) | 2.2669 | 2.1512 | 2.112 | 2.0075 | 1.9408 | 1.8432 | 1.6642 | 1.4626 | 1.2021 | 0.9319 | 0.60637 | -0.16389 | -0.60902 | -1.1066 | -1.5958 | -2.0544 | -4.1533 | -4.7982 | -4.8755
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | WPD Best View | Thermal headroom (MW) | 2.2382 | 1.9497 | 1.6817 | 1.3718 | 1.0723 | 0.63037 | 0.013566 | -0.60396 | -1.2111 | -2.1409 | -2.6948 | -3.2765 | -3.7796 | -4.1765 | -4.5983 | -4.9413 | -6.2119 | -7.3321 | -7.2136
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Consumer Transformation | Thermal headroom (MW) | 8.1669 | 7.9804 | 7.8703 | 7.6494 | 7.3287 | 6.976 | 6.3038 | 5.1316 | 4.3427 | 3.4791 | 2.2076 | 0.98584 | -0.62039 | -1.864 | -3.4854 | -5.1433 | -11.2461 | -14.1312 | -15.4322
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Leading the Way | Thermal headroom (MW) | 8.1776 | 8.0117 | 7.96 | 7.7319 | 7.4042 | 7.03 | 5.9812 | 5.0519 | 4.2192 | 2.8476 | 1.7716 | 0.36339 | -0.77661 | -2.2327 | -3.7179 | -4.6998 | -8.6932 | -10.2297 | -8.5338
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Steady Progression | Thermal headroom (MW) | 8.2218 | 8.3263 | 8.5469 | 8.6573 | 8.6824 | 8.7727 | 8.7637 | 8.7139 | 8.6417 | 8.5719 | 8.4294 | 8.2563 | 8.0494 | 7.4027 | 7.0666 | 6.705 | 2.5552 | -1.8984 | -3.1699
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | System Transformation | Thermal headroom (MW) | 8.2058 | 8.2979 | 8.5017 | 8.5434 | 8.5896 | 8.5403 | 8.5367 | 8.2927 | 8.0882 | 7.8955 | 7.2736 | 6.9257 | 6.13 | 5.5871 | 4.5946 | 3.5134 | -2.4185 | -5.7988 | -6.5161
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | WPD Best View | Thermal headroom (MW) | 8.1669 | 7.9804 | 7.8703 | 7.6494 | 7.3287 | 6.976 | 6.3038 | 5.1316 | 4.3427 | 3.4791 | 2.2076 | 0.98584 | -0.62039 | -1.864 | -3.4854 | -5.1433 | -11.2461 | -14.1312 | -15.4322
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Consumer Transformation | Thermal headroom (MW) | -4.2721 | -4.1355 | -3.7015 | -3.5071 | -3.5831 | -3.475 | -3.6264 | -3.7217 | -3.8977 | -4.4822 | -5.1066 | -5.5519 | -6.0348 | -6.5013 | -7.033 | -7.5896 | -9.5675 | -9.8657 | -8.8864
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Leading the Way | Thermal headroom (MW) | -4.3095 | -4.1875 | -3.7211 | -3.5157 | -3.6961 | -3.5634 | -3.742 | -3.8732 | -4.3838 | -4.6817 | -5.5387 | -5.9104 | -6.3542 | -6.7705 | -7.1897 | -7.8817 | -8.3232 | -7.4632 | -5.6633
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Steady Progression | Thermal headroom (MW) | -4.2055 | -3.8917 | -3.2148 | -2.84 | -2.6575 | -2.3202 | -2.0636 | -1.7488 | -1.4445 | -1.1906 | -1.2099 | -1.0407 | -0.89147 | -0.80421 | -0.71308 | -1.0423 | -1.3375 | -2.3529 | -1.6526
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | System Transformation | Thermal headroom (MW) | -4.2428 | -3.9517 | -3.3356 | -2.9546 | -2.8629 | -2.5453 | -2.2929 | -2.0195 | -1.8002 | -1.6536 | -1.8859 | -2.147 | -2.1052 | -2.1425 | -2.2378 | -2.4033 | -3.7032 | -3.997 | -3.0729
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | WPD Best View | Thermal headroom (MW) | -4.2721 | -4.1355 | -3.7015 | -3.5071 | -3.5831 | -3.475 | -3.6264 | -3.7217 | -3.8977 | -4.4822 | -5.1066 | -5.5519 | -6.0348 | -6.5013 | -7.033 | -7.5896 | -9.5675 | -9.8657 | -8.8864
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Consumer Transformation | Thermal headroom (MW) | 58.9911 | 57.5023 | 56.2939 | 55.132 | 53.6507 | 51.4297 | 48.504 | 45.7957 | 43.0556 | 39.1704 | 36.3288 | 32.7934 | 29.519 | 26.8743 | 23.8799 | 21.0545 | 6.4798 | 0.59022 | 0.48791
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Leading the Way | Thermal headroom (MW) | 58.7939 | 57.0026 | 55.6771 | 54.3951 | 53.0934 | 50.8915 | 48.013 | 45.2829 | 41.3936 | 38.5445 | 35.7012 | 32.906 | 30.7137 | 28.804 | 26.5307 | 23.5365 | 15.7618 | 14.2345 | 17.6811
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Steady Progression | Thermal headroom (MW) | 59.3368 | 59.1633 | 59.3694 | 59.3726 | 59.1594 | 58.9186 | 58.7937 | 58.5903 | 58.1686 | 57.6895 | 57.0522 | 56.0048 | 55.0014 | 53.8169 | 52.5135 | 50.0815 | 41.3058 | 32.8042 | 30.7816
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | System Transformation | Thermal headroom (MW) | 59.087 | 58.6205 | 58.3581 | 58.182 | 57.9667 | 57.3273 | 56.7498 | 56.1515 | 55.1988 | 54.2433 | 53.0665 | 50.552 | 48.8067 | 46.7814 | 44.7628 | 42.8509 | 32.318 | 26.958 | 26.773
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | WPD Best View | Thermal headroom (MW) | 58.9923 | 57.505 | 56.2995 | 55.1411 | 53.6643 | 51.4496 | 48.5318 | 45.8334 | 43.1064 | 39.2365 | 36.4127 | 32.8994 | 29.6488 | 27.029 | 24.0582 | 21.2586 | 6.7173 | 0.74022 | 0.62266
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Consumer Transformation | Thermal headroom (MW) | 2.0772 | 1.8897 | 1.7967 | 1.6895 | 1.5339 | 1.1834 | 0.91005 | 0.66102 | 0.41366 | 0.15719 | -0.088815 | -0.38573 | -0.64843 | -0.83855 | -0.99505 | -1.2025 | -2.2926 | -2.7086 | -2.7321
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Leading the Way | Thermal headroom (MW) | 2.0659 | 1.8226 | 1.7632 | 1.6601 | 1.4942 | 1.1236 | 0.85997 | 0.60742 | 0.36146 | 0.10016 | -0.14148 | -0.34875 | -0.50245 | -0.57273 | -0.67538 | -0.91503 | -1.4989 | -1.6467 | -1.3353
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Steady Progression | Thermal headroom (MW) | 2.1032 | 2.0476 | 2.0893 | 2.0759 | 2.0415 | 1.9501 | 1.9331 | 1.9098 | 1.8681 | 1.8138 | 1.7464 | 1.6399 | 1.5167 | 1.4058 | 1.2865 | 1.1542 | 0.46857 | -0.12344 | -0.31384
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | System Transformation | Thermal headroom (MW) | 2.0872 | 1.9871 | 1.9989 | 1.9828 | 1.9295 | 1.7855 | 1.7291 | 1.6632 | 1.5785 | 1.464 | 1.3385 | 1.166 | 0.99448 | 0.83047 | 0.65728 | 0.5094 | -0.082075 | -0.34394 | -0.28571
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | WPD Best View | Thermal headroom (MW) | 2.0772 | 1.8897 | 1.7967 | 1.6895 | 1.5339 | 1.1834 | 0.91005 | 0.66102 | 0.41366 | 0.15719 | -0.088815 | -0.38573 | -0.64843 | -0.83855 | -0.99505 | -1.2025 | -2.2926 | -2.7086 | -2.7321
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Consumer Transformation | Thermal headroom (MW) | 9.9049 | 9.6721 | 9.4263 | 9.0248 | 8.6612 | 8.0659 | 7.1976 | 6.3769 | 5.62 | 4.5098 | 3.7092 | 2.8722 | 2.1916 | 1.6507 | 1.2624 | 0.83427 | -2.0666 | -3.5611 | -3.6975
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Leading the Way | Thermal headroom (MW) | 9.7971 | 9.5188 | 9.2149 | 8.8855 | 8.499 | 7.9199 | 7.0522 | 6.2564 | 5.0861 | 4.3451 | 3.5966 | 3.0709 | 2.6964 | 2.5391 | 2.3639 | 1.9212 | 0.21499 | -0.21853 | 0.31726
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Steady Progression | Thermal headroom (MW) | 10.0295 | 10.0423 | 10.1317 | 10.0573 | 9.8903 | 9.8233 | 9.725 | 9.6184 | 9.4926 | 9.2893 | 9.0431 | 8.7501 | 8.4505 | 8.114 | 7.7494 | 7.0082 | 4.9994 | 3.1156 | 2.716
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | System Transformation | Thermal headroom (MW) | 9.9336 | 9.9037 | 9.8875 | 9.7155 | 9.5879 | 9.4719 | 9.2414 | 9.0395 | 8.7863 | 8.4818 | 8.055 | 7.2223 | 6.7384 | 6.2445 | 5.767 | 5.3064 | 3.2287 | 2.227 | 2.0955
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | WPD Best View | Thermal headroom (MW) | 9.9049 | 9.6721 | 9.4263 | 9.0248 | 8.6612 | 8.0659 | 7.1976 | 6.3769 | 5.62 | 4.5098 | 3.7092 | 2.8722 | 2.1916 | 1.6507 | 1.2624 | 0.83427 | -2.0666 | -3.5611 | -3.6975
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Consumer Transformation | Thermal headroom (MW) | 0.45107 | -0.22025 | -0.39766 | -0.53225 | -1.0565 | -1.3367 | -1.8362 | -2.2591 | -2.74 | -3.2408 | -3.7634 | -4.8069 | -5.5153 | -6.1403 | -7.1928 | -7.8397 | -10.9711 | -12.0104 | -11.7901
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Leading the Way | Thermal headroom (MW) | 0.44415 | -0.43184 | -0.63385 | -1.1085 | -1.2683 | -1.5018 | -2.0464 | -2.4817 | -2.948 | -3.4646 | -4.0052 | -4.9295 | -5.5084 | -6.0927 | -7.0432 | -7.4788 | -9.3245 | -9.5861 | -8.3849
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Steady Progression | Thermal headroom (MW) | 0.50491 | 0.19366 | 0.27102 | 0.35206 | 0.34942 | 0.36722 | 0.3909 | 0.39405 | 0.35165 | 0.35344 | 0.26904 | -0.15762 | -0.3034 | -0.4354 | -0.59541 | -0.7764 | -2.7197 | -5.1436 | -5.7583
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | System Transformation | Thermal headroom (MW) | 0.4649 | -0.01679 | -0.048235 | -0.005678 | 0.057375 | 0.0025985 | -0.04745 | -0.13539 | -0.56473 | -0.66483 | -0.79592 | -0.99385 | -1.2446 | -1.8823 | -2.2235 | -2.5486 | -5.7421 | -7.4199 | -7.469
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | WPD Best View | Thermal headroom (MW) | 0.45107 | -0.22025 | -0.39766 | -0.53225 | -1.0565 | -1.3367 | -1.8362 | -2.2591 | -2.74 | -3.2408 | -3.7634 | -4.8069 | -5.5153 | -6.1403 | -7.1928 | -7.8397 | -10.9711 | -12.0104 | -11.7901
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Consumer Transformation | Thermal headroom (MW) | 2.0732 | 1.2808 | 1.0021 | 0.4867 | -0.087884 | -0.82092 | -1.8724 | -2.8878 | -3.8799 | -5.6746 | -6.6559 | -7.8366 | -9.2372 | -10.193 | -12.0714 | -13.7319 | -23.4092 | -26.8782 | -27.3499
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Leading the Way | Thermal headroom (MW) | 2.0107 | 1.2338 | 1.0236 | 0.51455 | -0.06884 | -0.81861 | -1.8732 | -2.8407 | -4.5443 | -5.6714 | -6.6563 | -7.7734 | -8.3748 | -9.5981 | -11.0768 | -12.9832 | -17.6216 | -19.1629 | -18.1335
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Steady Progression | Thermal headroom (MW) | 2.1818 | 2.2456 | 2.5078 | 2.5038 | 2.4669 | 2.3972 | 2.4009 | 2.3701 | 1.9782 | 1.866 | 1.6804 | 1.3962 | 1.0402 | 0.64042 | 0.185 | -1.0534 | -5.8525 | -9.014 | -9.9893
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | System Transformation | Thermal headroom (MW) | 2.1145 | 2.1158 | 2.2987 | 2.2188 | 2.1008 | 1.5718 | 1.4189 | 1.3061 | 1.1395 | 0.76338 | 0.37716 | -0.84772 | -1.3989 | -2.02 | -3.0683 | -4.1174 | -9.4914 | -12.0282 | -12.3461
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | WPD Best View | Thermal headroom (MW) | 2.0732 | 1.2808 | 1.0021 | 0.4867 | -0.087884 | -0.82092 | -1.8724 | -2.8878 | -3.8799 | -5.6746 | -6.6559 | -7.8366 | -9.2372 | -10.193 | -12.0714 | -13.7319 | -23.4092 | -26.8782 | -27.3499
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Consumer Transformation | Thermal headroom (MW) | 9.4083 | 9.2769 | 8.7314 | 8.5363 | 8.3328 | 7.9611 | 7.2978 | 6.6879 | 5.9858 | 4.8715 | 4.1381 | 3.2398 | 2.2098 | 1.2841 | 0.35916 | -0.5764 | -4.1454 | -5.5414 | -5.3792
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Leading the Way | Thermal headroom (MW) | 9.3919 | 9.2442 | 8.5663 | 8.3601 | 8.165 | 7.8117 | 7.2083 | 6.5392 | 5.4179 | 4.6851 | 3.8854 | 3.076 | 2.1674 | 1.3487 | 0.57542 | -0.49403 | -2.2773 | -2.2437 | -1.1203
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Steady Progression | Thermal headroom (MW) | 9.4809 | 9.5768 | 9.436 | 9.514 | 9.5947 | 9.6368 | 9.6512 | 9.6332 | 9.6194 | 9.5327 | 9.4464 | 9.3303 | 9.1497 | 8.8056 | 8.4293 | 7.6904 | 5.5776 | 3.0588 | 2.6158
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | System Transformation | Thermal headroom (MW) | 9.4264 | 9.4968 | 9.1595 | 9.2345 | 9.291 | 9.3133 | 9.2115 | 9.0792 | 8.9205 | 8.7572 | 8.5648 | 7.9497 | 7.4661 | 6.9616 | 6.4374 | 5.9408 | 2.8839 | 1.1274 | 1.1352
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | WPD Best View | Thermal headroom (MW) | 9.4096 | 9.2798 | 8.7374 | 8.5461 | 8.3474 | 7.9825 | 7.3276 | 6.7284 | 6.0403 | 4.9424 | 4.228 | 3.3534 | 2.3489 | 1.4498 | 0.55019 | -0.35781 | -3.8909 | -5.3807 | -5.2348
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Consumer Transformation | Thermal headroom (MW) | 69.442 | 68.0192 | 66.8699 | 65.5135 | 63.8909 | 61.5418 | 58.6622 | 55.9439 | 52.1483 | 48.7432 | 45.6092 | 42.1071 | 38.5539 | 35.3236 | 31.8765 | 28.7882 | 13.2704 | 8.5724 | 8.6966
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Leading the Way | Thermal headroom (MW) | 69.3113 | 67.6358 | 66.506 | 64.8161 | 63.241 | 60.8244 | 57.8162 | 55.1012 | 50.5719 | 46.8148 | 43.427 | 40.1415 | 36.9998 | 34.1366 | 31.5515 | 29.365 | 18.4168 | 17.9191 | 22.4826
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Steady Progression | Thermal headroom (MW) | 69.7237 | 69.543 | 69.7109 | 69.4056 | 69.2138 | 68.7139 | 68.3707 | 67.8969 | 66.6255 | 65.7126 | 64.7255 | 63.3318 | 61.8565 | 60.2147 | 58.4057 | 56.2959 | 42.65 | 32.7352 | 29.7077
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | System Transformation | Thermal headroom (MW) | 69.5307 | 69.1001 | 68.8689 | 68.3802 | 67.9387 | 67.0455 | 66.2578 | 65.3526 | 63.1027 | 61.5079 | 59.9133 | 57.759 | 55.4166 | 52.5733 | 49.7308 | 46.9599 | 32.5306 | 27.0234 | 27.545
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | WPD Best View | Thermal headroom (MW) | 69.442 | 68.0192 | 66.8699 | 65.49 | 63.8801 | 61.5418 | 58.6622 | 55.9439 | 52.1483 | 48.7432 | 45.6092 | 42.1071 | 38.5539 | 35.3236 | 31.8765 | 28.7882 | 13.2265 | 8.5415 | 8.6966
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Consumer Transformation | Thermal headroom (MW) | 9.5509 | 9.4661 | 9.4797 | 9.412 | 9.3369 | 9.1762 | 8.9726 | 8.8029 | 8.6174 | 8.4822 | 8.3163 | 8.154 | 7.9599 | 7.7607 | 7.5993 | 7.4316 | 4.7753 | 4.9694 | 5.4247
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Leading the Way | Thermal headroom (MW) | 9.5228 | 9.4222 | 9.4335 | 9.3708 | 9.2766 | 9.1247 | 8.9004 | 8.7432 | 8.5358 | 8.3909 | 8.2227 | 8.1171 | 7.9355 | 7.7735 | 7.6456 | 7.5143 | 5.0013 | 5.4486 | 6.1252
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Steady Progression | Thermal headroom (MW) | 9.5918 | 9.6306 | 9.7676 | 9.8054 | 9.8468 | 9.8869 | 9.913 | 9.9464 | 9.9921 | 10.025 | 10.0547 | 10.0666 | 10.0479 | 10.0399 | 10.0201 | 9.9771 | 8.2691 | 7.888 | 8.0001
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | System Transformation | Thermal headroom (MW) | 9.5621 | 9.5668 | 9.677 | 9.6936 | 9.7127 | 9.712 | 9.7082 | 9.703 | 9.676 | 9.681 | 9.6427 | 9.6065 | 9.5637 | 9.4926 | 9.4008 | 9.3163 | 6.6706 | 6.6642 | 7.068
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | WPD Best View | Thermal headroom (MW) | 9.5509 | 9.4661 | 9.4797 | 9.412 | 9.3369 | 9.1762 | 8.9726 | 8.8029 | 8.6174 | 8.4822 | 8.3163 | 8.154 | 7.9599 | 7.7607 | 7.5993 | 7.4316 | 4.7753 | 4.9694 | 5.4247
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Consumer Transformation | Thermal headroom (MW) | 3.8757 | 3.817 | 3.729 | 3.6413 | 3.5215 | 3.3765 | 3.2017 | 2.9994 | 2.7817 | 2.5472 | 2.2949 | 2.0325 | 1.787 | 1.575 | 1.4037 | 1.2405 | 0.44834 | -0.13943 | -0.34948
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Leading the Way | Thermal headroom (MW) | 3.8765 | 3.8037 | 3.747 | 3.6473 | 3.529 | 3.3868 | 3.2024 | 3.0046 | 2.7766 | 2.4893 | 2.1915 | 1.9165 | 1.6726 | 1.5044 | 1.385 | 1.3058 | 0.48245 | 0.34444 | 0.60619
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Steady Progression | Thermal headroom (MW) | 3.8976 | 3.8892 | 3.8909 | 3.8643 | 3.8275 | 3.7901 | 3.7342 | 3.6699 | 3.5904 | 3.4914 | 3.3802 | 3.2364 | 3.0704 | 2.8958 | 2.6873 | 2.451 | 1.0325 | -0.097363 | -0.53019
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | System Transformation | Thermal headroom (MW) | 3.8868 | 3.878 | 3.8561 | 3.827 | 3.7813 | 3.7268 | 3.639 | 3.5373 | 3.4106 | 3.2523 | 3.0756 | 2.8421 | 2.5984 | 2.2905 | 1.9663 | 1.6474 | 0.34768 | -0.18486 | -0.29974
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | WPD Best View | Thermal headroom (MW) | 3.8757 | 3.817 | 3.729 | 3.6413 | 3.5215 | 3.3765 | 3.2017 | 2.9994 | 2.7817 | 2.5472 | 2.2949 | 2.0325 | 1.787 | 1.575 | 1.4037 | 1.2405 | 0.44834 | -0.13943 | -0.34948
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Consumer Transformation | Thermal headroom (MW) | 16.9378 | 16.8102 | 16.6917 | 16.5707 | 16.4377 | 16.1843 | 15.7917 | 15.4212 | 15.0375 | 14.6483 | 14.2195 | 13.7544 | 13.2868 | 12.7775 | 12.2374 | 11.6591 | 8.9621 | 8.313 | 8.3604
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Leading the Way | Thermal headroom (MW) | 16.9248 | 16.7691 | 16.6692 | 16.537 | 16.4213 | 16.1543 | 15.7217 | 15.3491 | 14.9458 | 14.5016 | 14.0494 | 13.5565 | 13.007 | 12.465 | 11.9429 | 11.4709 | 9.0799 | 9.0387 | 9.6193
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Steady Progression | Thermal headroom (MW) | 16.9623 | 16.9677 | 17.0114 | 16.9667 | 16.9937 | 16.9016 | 16.8688 | 16.796 | 16.697 | 16.5771 | 16.4182 | 16.2069 | 15.9886 | 15.7634 | 15.5284 | 15.2747 | 13.619 | 12.5529 | 12.1808
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | System Transformation | Thermal headroom (MW) | 16.9429 | 16.9356 | 16.9293 | 16.8655 | 16.8834 | 16.7958 | 16.6913 | 16.5609 | 16.3794 | 16.1604 | 15.9017 | 15.6036 | 15.2719 | 14.9321 | 14.5897 | 14.2593 | 12.3634 | 11.6011 | 11.7106
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | WPD Best View | Thermal headroom (MW) | 16.9378 | 16.8102 | 16.6917 | 16.5628 | 16.4296 | 16.1843 | 15.7917 | 15.4212 | 15.0375 | 14.6483 | 14.2195 | 13.7544 | 13.2868 | 12.7775 | 12.2374 | 11.6591 | 8.9621 | 8.313 | 8.3604
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Consumer Transformation | Thermal headroom (MW) | 6.0442 | 5.8975 | 5.877 | 5.6651 | 5.1304 | 4.6766 | 4.0572 | 3.5093 | 2.9167 | 2.2955 | 1.6232 | 0.39504 | -0.45944 | -1.1835 | -2.3534 | -3.0932 | -6.7205 | -8.0632 | -7.8933
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Leading the Way | Thermal headroom (MW) | 6.0327 | 5.907 | 5.9203 | 5.3731 | 5.1747 | 4.7434 | 4.0985 | 3.5401 | 2.9344 | 2.2626 | 1.5986 | 0.5956 | -0.029843 | -0.61547 | -1.534 | -2.0013 | -4.22 | -4.9046 | -3.8326
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Steady Progression | Thermal headroom (MW) | 6.0968 | 6.2165 | 6.5074 | 6.5965 | 6.7223 | 6.7206 | 6.8223 | 6.9063 | 6.9376 | 6.9688 | 7.0168 | 6.592 | 6.5189 | 6.3281 | 6.1234 | 5.9039 | 4.2399 | 2.7807 | 2.2184
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | System Transformation | Thermal headroom (MW) | 6.0723 | 6.1597 | 6.4226 | 6.472 | 6.5242 | 6.486 | 6.4921 | 6.4877 | 6.1191 | 6.0703 | 5.9961 | 5.797 | 5.4798 | 4.8218 | 4.5172 | 4.2233 | 2.1049 | 0.52263 | 0.42621
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | WPD Best View | Thermal headroom (MW) | 6.0442 | 5.8975 | 5.877 | 5.6651 | 5.1304 | 4.6766 | 4.0572 | 3.5093 | 2.9167 | 2.2955 | 1.6232 | 0.39504 | -0.45944 | -1.1835 | -2.3534 | -3.0932 | -6.7205 | -8.0632 | -7.8933
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Consumer Transformation | Thermal headroom (MW) | 4.6751 | 3.9805 | 3.785 | 3.4539 | 3.1728 | 2.8158 | 2.1991 | 1.6702 | 1.149 | 0.19941 | -0.4081 | -1.1285 | -2.2006 | -2.8705 | -3.9445 | -4.5866 | -7.8837 | -9.0173 | -8.838
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Leading the Way | Thermal headroom (MW) | 4.5667 | 3.779 | 3.57 | 3.1959 | 2.9261 | 2.5517 | 1.9417 | 1.4123 | 0.53077 | -0.066524 | -0.62508 | -1.5734 | -2.1588 | -3.0752 | -3.6679 | -4.4837 | -5.9205 | -5.9373 | -4.9173
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Steady Progression | Thermal headroom (MW) | 4.8083 | 4.7841 | 4.8978 | 4.8532 | 4.8639 | 4.8708 | 4.8581 | 4.8965 | 4.5379 | 4.4653 | 4.4625 | 4.3863 | 4.2357 | 4.112 | 3.9598 | 3.4138 | 1.2603 | -1.1119 | -1.6044
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | System Transformation | Thermal headroom (MW) | 4.6821 | 4.5425 | 4.5622 | 4.4791 | 4.4488 | 4.0714 | 4.0204 | 3.9228 | 3.8195 | 3.7208 | 3.5584 | 2.9862 | 2.7397 | 2.4577 | 1.7806 | 1.0406 | -1.9972 | -3.8696 | -3.6984
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | WPD Best View | Thermal headroom (MW) | 4.6751 | 3.9805 | 3.785 | 3.4539 | 3.1728 | 2.8158 | 2.1991 | 1.6702 | 1.149 | 0.19941 | -0.4081 | -1.1285 | -2.2006 | -2.8705 | -3.9445 | -4.5866 | -7.8837 | -9.0173 | -8.838
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Consumer Transformation | Thermal headroom (MW) | 12.7584 | 12.6259 | 12.6343 | 12.5366 | 12.4175 | 12.1915 | 11.8954 | 11.5807 | 11.2477 | 10.927 | 10.5312 | 10.1951 | 9.9262 | 9.7299 | 9.597 | 9.4818 | 8.934 | 8.6164 | 8.6726
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Leading the Way | Thermal headroom (MW) | 12.7437 | 12.5671 | 12.5892 | 12.4842 | 12.3588 | 12.1297 | 11.8258 | 11.5225 | 11.1816 | 10.8546 | 10.4366 | 10.2071 | 10.0694 | 10.0521 | 10.0493 | 10.0397 | 9.869 | 9.8576 | 10.5439
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Steady Progression | Thermal headroom (MW) | 12.7926 | 12.7933 | 12.9522 | 12.9959 | 13.0358 | 13.0464 | 13.0516 | 13.0356 | 12.9985 | 12.9377 | 12.801 | 12.6778 | 12.5363 | 12.3851 | 12.1886 | 11.9945 | 10.8737 | 10.0186 | 9.8898
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | System Transformation | Thermal headroom (MW) | 12.7759 | 12.737 | 12.8576 | 12.8944 | 12.909 | 12.8882 | 12.8575 | 12.7871 | 12.687 | 12.5508 | 12.2842 | 12.078 | 11.8297 | 11.559 | 11.2707 | 11.0077 | 10.1185 | 9.8422 | 10.0983
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | WPD Best View | Thermal headroom (MW) | 12.7584 | 12.6259 | 12.6343 | 12.5366 | 12.4175 | 12.1915 | 11.8954 | 11.5807 | 11.2477 | 10.927 | 10.5312 | 10.1951 | 9.9262 | 9.7299 | 9.597 | 9.4818 | 8.8425 | 8.5521 | 8.6726
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Consumer Transformation | Thermal headroom (MW) | 16.7445 | 16.2628 | 15.7662 | 15.3454 | 14.9272 | 14.2792 | 13.7603 | 13.2732 | 12.7496 | 12.1626 | 11.6724 | 11.1376 | 10.5893 | 10.1028 | 9.5906 | 9.1166 | 7.4604 | 7.1442 | 7.4233
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Leading the Way | Thermal headroom (MW) | 16.7369 | 16.1325 | 15.4949 | 14.9827 | 14.4647 | 13.7443 | 13.1946 | 12.6812 | 12.178 | 11.5961 | 11.1393 | 10.7952 | 10.4337 | 10.0677 | 9.7119 | 9.4232 | 8.5279 | 8.6811 | 9.3842
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Steady Progression | Thermal headroom (MW) | 16.7675 | 16.5323 | 16.2794 | 16.0955 | 15.8756 | 15.6385 | 15.5536 | 15.4327 | 15.3063 | 15.1801 | 15.0272 | 14.8765 | 14.675 | 14.4201 | 14.1502 | 13.8671 | 12.4761 | 11.4252 | 11.2168
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | System Transformation | Thermal headroom (MW) | 16.754 | 16.4006 | 16.0096 | 15.7333 | 15.4391 | 15.0796 | 14.9121 | 14.7483 | 14.5663 | 14.333 | 14.1454 | 13.894 | 13.5596 | 13.1973 | 12.8704 | 12.556 | 11.3291 | 10.7391 | 10.9376
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | WPD Best View | Thermal headroom (MW) | 16.7445 | 16.2628 | 15.7662 | 15.3454 | 14.9272 | 14.2792 | 13.7603 | 13.2732 | 12.7496 | 12.1626 | 11.6724 | 11.1376 | 10.5893 | 10.1028 | 9.5906 | 9.1166 | 7.4604 | 7.1442 | 7.4233
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Consumer Transformation | Thermal headroom (MW) | 19.0484 | 18.9427 | 18.8525 | 18.7239 | 18.5701 | 18.3274 | 17.9852 | 17.7134 | 16.8948 | 16.4436 | 16.1318 | 15.7928 | 15.3917 | 14.9885 | 14.5596 | 14.1583 | 12.156 | 11.7136 | 11.7279
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Leading the Way | Thermal headroom (MW) | 19.0236 | 18.9222 | 18.8452 | 18.6813 | 18.5367 | 18.2986 | 17.9617 | 17.6947 | 16.5575 | 15.9851 | 15.605 | 15.2774 | 14.8854 | 14.5283 | 14.2056 | 13.9207 | 13.1475 | 13.0374 | 13.4939
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Steady Progression | Thermal headroom (MW) | 19.0777 | 19.0867 | 19.1188 | 19.097 | 19.1068 | 19.0754 | 19.0259 | 18.9648 | 18.5832 | 18.4162 | 18.2794 | 18.1172 | 17.945 | 17.7451 | 17.5524 | 17.3479 | 15.8346 | 14.7453 | 14.404
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | System Transformation | Thermal headroom (MW) | 19.0539 | 19.0493 | 19.0565 | 19.0261 | 18.9948 | 18.9412 | 18.8435 | 18.7443 | 18.0507 | 17.7887 | 17.6352 | 17.4179 | 17.1571 | 16.8374 | 16.5516 | 16.2818 | 14.7262 | 14.2125 | 14.2959
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | WPD Best View | Thermal headroom (MW) | 19.0484 | 18.9427 | 18.8525 | 18.7163 | 18.5701 | 18.3274 | 17.9852 | 17.7134 | 16.8948 | 16.4436 | 16.1318 | 15.7928 | 15.3917 | 14.9885 | 14.5596 | 14.1583 | 12.156 | 11.7136 | 11.7279
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Consumer Transformation | Thermal headroom (MW) | 47.4678 | 45.2114 | 42.5267 | 40.1143 | 37.2038 | 33.3274 | 27.6123 | 21.2262 | 15.0665 | 5.5639 | -1.7678 | -9.47 | -18.6245 | -25.7073 | -33.4264 | -40.4133 | -74.9469 | -91.8548 | -95.1551
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Leading the Way | Thermal headroom (MW) | 47.3834 | 45.0544 | 42.4235 | 39.9319 | 37.0369 | 33.0349 | 26.5187 | 20.7345 | 11.3044 | 3.8196 | -3.1801 | -10.4238 | -18.0003 | -24.7205 | -30.5392 | -38.5494 | -59.6181 | -65.058 | -58.4553
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Steady Progression | Thermal headroom (MW) | 47.9582 | 47.9248 | 47.8101 | 47.5541 | 47.2199 | 46.7135 | 45.9144 | 44.862 | 43.2915 | 41.5867 | 39.6302 | 37.0554 | 33.5057 | 29.4501 | 25.6524 | 18.3765 | -10.4808 | -33.0918 | -39.7105
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | System Transformation | Thermal headroom (MW) | 47.7537 | 47.5054 | 46.6628 | 46.2564 | 45.5997 | 44.2664 | 42.7768 | 41.0077 | 38.769 | 35.9339 | 31.8321 | 24.6339 | 18.28 | 12.8305 | 5.9056 | -0.95436 | -35.1689 | -49.8973 | -53.9848
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | WPD Best View | Thermal headroom (MW) | 47.4687 | 45.2135 | 42.5311 | 40.1214 | 37.2145 | 33.343 | 27.6341 | 21.338 | 15.2109 | 5.7315 | -1.5833 | -9.2758 | -18.523 | -25.5863 | -33.2869 | -40.2925 | -74.8449 | -91.7375 | -95.0497
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Consumer Transformation | Thermal headroom (MW) | -0.047599 | -0.49161 | -0.51645 | -0.61188 | -0.75918 | -0.95025 | -1.3038 | -1.7416 | -2.2836 | -3.1922 | -3.7432 | -4.3362 | -5.192 | -5.9175 | -7.0439 | -7.7973 | -11.6232 | -13.3707 | -13.7541
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Leading the Way | Thermal headroom (MW) | -0.03594 | -0.50216 | -0.4505 | -0.50988 | -0.62584 | -0.87415 | -1.2076 | -1.6965 | -2.6178 | -3.2038 | -3.7706 | -4.5581 | -5.2611 | -6.363 | -7.0598 | -8.0525 | -10.1428 | -10.6202 | -9.8373
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Steady Progression | Thermal headroom (MW) | 0.012913 | 0.106 | 0.3277 | 0.37227 | 0.45456 | 0.5312 | 0.57625 | 0.57557 | 0.20116 | 0.10972 | -0.074699 | -0.33845 | -0.65833 | -1.0062 | -1.3969 | -2.1816 | -5.3956 | -7.8933 | -8.7443
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | System Transformation | Thermal headroom (MW) | -0.0042754 | 0.05168 | 0.20827 | 0.2618 | 0.33102 | -0.026947 | -0.046554 | -0.086633 | -0.209 | -0.50492 | -0.85819 | -1.6638 | -2.1881 | -2.7478 | -3.685 | -4.6044 | -8.1226 | -9.8951 | -10.0687
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | WPD Best View | Thermal headroom (MW) | -0.046309 | -0.48875 | -0.51045 | -0.60214 | -0.74456 | -0.92894 | -1.274 | -1.5884 | -2.0857 | -2.9627 | -3.4904 | -4.0702 | -5.0529 | -5.7518 | -6.8528 | -7.5787 | -11.3687 | -13.21 | -13.6097
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Consumer Transformation | Thermal headroom (MW) | 9.6787 | 9.3221 | 8.9805 | 8.5569 | 8.1102 | 7.4576 | 6.3108 | 5.1998 | 4.0723 | 2.5993 | 1.529 | 0.31071 | -1.0111 | -1.9957 | -2.9845 | -3.8162 | -9.5714 | -12.5065 | -13.0644
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Leading the Way | Thermal headroom (MW) | 9.668 | 9.3683 | 9.0691 | 8.6715 | 8.2926 | 7.6403 | 6.4899 | 5.4142 | 3.8916 | 2.7569 | 1.6727 | 0.90347 | -0.067386 | -0.74057 | -1.1962 | -2.4966 | -6.0726 | -7.6012 | -6.7982
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Steady Progression | Thermal headroom (MW) | 9.7427 | 9.8102 | 9.9465 | 9.9734 | 9.9908 | 9.9702 | 9.9231 | 9.789 | 9.6348 | 9.3986 | 9.1159 | 8.7615 | 8.2237 | 7.7542 | 7.2491 | 6.3638 | 3.5213 | 1.2383 | 0.42627
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | System Transformation | Thermal headroom (MW) | 9.7176 | 9.7671 | 9.855 | 9.827 | 9.8242 | 9.7415 | 9.5484 | 9.3023 | 8.9713 | 8.5703 | 8.0911 | 7.1742 | 6.3512 | 5.6659 | 4.9706 | 4.3131 | 1.1552 | -0.35644 | -0.72389
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | WPD Best View | Thermal headroom (MW) | 9.6787 | 9.3221 | 8.9805 | 8.5569 | 8.1102 | 7.4576 | 6.3108 | 5.1998 | 4.0723 | 2.5993 | 1.529 | 0.31071 | -1.0111 | -1.9957 | -2.9845 | -3.8738 | -9.5714 | -12.5065 | -13.0644
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Consumer Transformation | Thermal headroom (MW) | 12.8497 | 12.8686 | 13.0629 | 13.0885 | 13.093 | 13.0408 | 12.7775 | 12.529 | 12.2785 | 11.9753 | 11.6324 | 11.1603 | 10.5594 | 10.0572 | 9.5538 | 9.0362 | 7.2212 | 6.8314 | 7.211
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Leading the Way | Thermal headroom (MW) | 12.8244 | 12.8569 | 13.0816 | 13.1129 | 13.13 | 13.0144 | 12.7668 | 12.5097 | 12.2152 | 11.8787 | 11.423 | 11.0231 | 10.3832 | 9.8906 | 9.3872 | 8.9706 | 8.1104 | 8.4997 | 9.9444
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Steady Progression | Thermal headroom (MW) | 12.8975 | 13.0615 | 13.4636 | 13.6462 | 13.8386 | 14.0219 | 14.1794 | 14.3221 | 14.3879 | 14.4796 | 14.5785 | 14.607 | 14.5102 | 14.4843 | 14.4024 | 14.2954 | 13.1155 | 11.6102 | 11.4928
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | System Transformation | Thermal headroom (MW) | 12.8623 | 13.0397 | 13.3957 | 13.5661 | 13.7538 | 13.9 | 13.9537 | 13.9988 | 14.0606 | 14.0631 | 14.0521 | 13.9475 | 13.707 | 13.4931 | 13.2265 | 12.9458 | 11.1701 | 10.3986 | 10.987
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | WPD Best View | Thermal headroom (MW) | 12.8497 | 12.8686 | 13.0629 | 13.0885 | 13.093 | 13.0408 | 12.7775 | 12.529 | 12.2785 | 11.9753 | 11.6324 | 11.1603 | 10.5594 | 10.0572 | 9.5538 | 9.0362 | 7.2212 | 6.8314 | 7.211
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Consumer Transformation | Thermal headroom (MW) | 2.6785 | 2.5558 | 2.4185 | 2.2326 | 1.9963 | 1.7116 | 1.3315 | 0.92061 | 0.46805 | -0.38122 | -0.90681 | -1.4588 | -1.9758 | -2.4105 | -2.7613 | -3.0357 | -4.3848 | -5.5107 | -5.616
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Leading the Way | Thermal headroom (MW) | 2.6796 | 2.5689 | 2.4524 | 2.2583 | 2.0196 | 1.7367 | 1.347 | 0.92883 | 0.083486 | -0.4968 | -1.0498 | -1.5538 | -1.9896 | -2.3088 | -2.4869 | -2.9269 | -4.1002 | -4.1829 | -3.8015
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Steady Progression | Thermal headroom (MW) | 2.7181 | 2.6971 | 2.6936 | 2.6529 | 2.5935 | 2.5153 | 2.4119 | 2.2575 | 2.0896 | 1.8725 | 1.6417 | 1.3581 | 1.048 | 0.69092 | 0.29577 | -0.51738 | -2.8935 | -4.2363 | -4.6583
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | System Transformation | Thermal headroom (MW) | 2.7079 | 2.6833 | 2.6613 | 2.6012 | 2.5184 | 2.3899 | 2.2264 | 2.0213 | 1.7516 | 1.448 | 1.092 | 0.31526 | -0.18778 | -0.77018 | -1.3937 | -1.9967 | -4.4445 | -5.1754 | -5.5245
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | WPD Best View | Thermal headroom (MW) | 2.6785 | 2.5558 | 2.4185 | 2.2326 | 1.9963 | 1.7116 | 1.3315 | 0.92061 | 0.46805 | -0.38122 | -0.90681 | -1.4588 | -1.9758 | -2.4105 | -2.7613 | -3.0357 | -4.4155 | -5.5107 | -5.616
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Consumer Transformation | Thermal headroom (MW) | 5.4996 | 5.1284 | 4.4114 | 4.0622 | 3.7208 | 3.163 | 2.2848 | 1.0989 | 0.16538 | -0.79863 | -2.1956 | -3.4966 | -5.5126 | -6.8139 | -8.519 | -10.1586 | -15.9559 | -18.4855 | -19.4871
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Leading the Way | Thermal headroom (MW) | 5.4833 | 5.0573 | 4.2742 | 3.9058 | 3.5576 | 3.0054 | 1.7362 | 0.87327 | -0.044056 | -1.3633 | -2.476 | -3.9373 | -5.6081 | -7.1679 | -8.7055 | -9.7276 | -13.3707 | -14.6597 | -13.1423
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Steady Progression | Thermal headroom (MW) | 5.5629 | 5.5232 | 5.2694 | 5.2255 | 5.2016 | 5.1555 | 5.0236 | 4.9225 | 4.7726 | 4.6076 | 4.4422 | 4.1773 | 3.6411 | 2.9409 | 2.5047 | 2.0515 | -2.1549 | -6.5752 | -7.9336
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | System Transformation | Thermal headroom (MW) | 5.5272 | 5.4349 | 4.965 | 4.9383 | 4.8779 | 4.7515 | 4.5513 | 4.3446 | 4.1217 | 3.8166 | 3.0966 | 2.6532 | 1.4259 | 0.77686 | -0.29496 | -1.384 | -7.216 | -10.4505 | -11.1668
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | WPD Best View | Thermal headroom (MW) | 5.4996 | 5.1284 | 4.4114 | 4.0622 | 3.7208 | 3.163 | 2.2848 | 1.0989 | 0.16538 | -0.79863 | -2.1956 | -3.4966 | -5.5126 | -6.8139 | -8.519 | -10.1586 | -15.9559 | -18.4855 | -19.4871
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Consumer Transformation | Thermal headroom (MW) | 5.8787 | 5.7511 | 5.6282 | 5.3982 | 5.1069 | 4.7757 | 4.2816 | 3.7593 | 3.2131 | 1.9278 | 1.3515 | 0.65471 | 0.0072559 | -0.567 | -1.0268 | -1.4215 | -3.8313 | -5.6926 | -5.8948
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Leading the Way | Thermal headroom (MW) | 5.8769 | 5.7633 | 5.6703 | 5.4247 | 5.1492 | 4.7997 | 4.3033 | 3.7701 | 2.4813 | 1.8779 | 1.1854 | 0.57473 | 0.038539 | -0.36477 | -0.61579 | -1.4957 | -3.2715 | -3.5688 | -3.4257
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Steady Progression | Thermal headroom (MW) | 5.9178 | 5.9299 | 5.9862 | 5.9823 | 5.9622 | 5.8858 | 5.7777 | 5.6539 | 5.4942 | 5.2901 | 5.0414 | 4.7505 | 4.4045 | 4.0037 | 3.5982 | 2.4197 | -0.29293 | -2.4636 | -3.0014
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | System Transformation | Thermal headroom (MW) | 5.9076 | 5.9107 | 5.9482 | 5.9205 | 5.8659 | 5.7337 | 5.5802 | 5.3744 | 5.1011 | 4.7803 | 4.3996 | 3.2262 | 2.6938 | 2.1027 | 1.4132 | 0.73714 | -2.4325 | -3.7606 | -4.4995
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | WPD Best View | Thermal headroom (MW) | 5.8787 | 5.7511 | 5.6282 | 5.3982 | 5.1069 | 4.7757 | 4.2816 | 3.7593 | 3.2131 | 1.9278 | 1.3515 | 0.65471 | 0.0072559 | -0.567 | -1.0268 | -1.4215 | -3.8313 | -5.6926 | -5.8948
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Consumer Transformation | Thermal headroom (MW) | 3.4522 | 3.1902 | 2.8777 | 2.5613 | 2.1077 | 1.5652 | 0.9267 | 0.35389 | -0.2471 | -1.208 | -1.8017 | -2.4768 | -3.0693 | -3.701 | -4.2858 | -4.9178 | -9.9472 | -11.5274 | -11.6433
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Leading the Way | Thermal headroom (MW) | 3.4257 | 3.1377 | 2.8188 | 2.4774 | 1.9865 | 1.4147 | 0.77585 | 0.2046 | -0.7491 | -1.3759 | -1.9268 | -2.3964 | -2.8887 | -3.2887 | -3.8055 | -4.8369 | -7.0552 | -7.6387 | -7.2697
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Steady Progression | Thermal headroom (MW) | 3.5077 | 3.4514 | 3.397 | 3.2907 | 3.1425 | 3.0188 | 2.9241 | 2.7953 | 2.6587 | 2.4818 | 2.2733 | 2.0178 | 1.7257 | 1.4216 | 1.0646 | 0.33402 | -2.8217 | -4.577 | -5.0169
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | System Transformation | Thermal headroom (MW) | 3.4795 | 3.3913 | 3.2666 | 3.1225 | 2.9072 | 2.7399 | 2.5624 | 2.3715 | 2.1498 | 1.8849 | 1.5598 | 0.82117 | 0.40051 | -0.042473 | -0.52318 | -1.0094 | -4.4933 | -5.4913 | -5.7723
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | WPD Best View | Thermal headroom (MW) | 3.4522 | 3.1902 | 2.8777 | 2.5613 | 2.1077 | 1.5652 | 0.9267 | 0.35389 | -0.2471 | -1.208 | -1.8017 | -2.4768 | -3.0693 | -3.701 | -4.2858 | -4.9178 | -9.9472 | -11.5274 | -11.6433
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Consumer Transformation | Thermal headroom (MW) | 42.9462 | 42.223 | 41.9874 | 41.29 | 40.1222 | 38.8325 | 36.6585 | 34.6468 | 32.295 | 28.5139 | 25.8963 | 23.0273 | 20.3186 | 17.6353 | 14.2918 | 11.0391 | -4.502 | -12.1037 | -12.7934
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Leading the Way | Thermal headroom (MW) | 42.8415 | 41.8952 | 41.94 | 41.1201 | 40.0485 | 38.7454 | 36.5318 | 34.3805 | 30.5842 | 28.0343 | 25.5132 | 23.4519 | 21.4722 | 18.9081 | 16.4129 | 12.4116 | 3.128 | 1.2277 | 4.9996
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Steady Progression | Thermal headroom (MW) | 43.2092 | 43.5304 | 44.581 | 44.7988 | 44.9346 | 45.111 | 45.2788 | 45.3646 | 45.4037 | 45.317 | 44.9268 | 44.1523 | 43.3505 | 42.4302 | 41.2475 | 38.5566 | 31.3248 | 23.0848 | 21.0063
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | System Transformation | Thermal headroom (MW) | 43.0643 | 43.2149 | 43.9329 | 44.158 | 44.0818 | 44.075 | 43.9262 | 43.7099 | 43.2154 | 42.6526 | 41.5885 | 38.647 | 37.079 | 35.3603 | 33.5673 | 31.7551 | 22.2873 | 15.7702 | 14.7541
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | WPD Best View | Thermal headroom (MW) | 42.9462 | 42.223 | 41.9874 | 41.29 | 40.1222 | 38.8325 | 36.6585 | 34.6468 | 32.295 | 28.5139 | 25.8963 | 23.0273 | 20.3186 | 17.6353 | 14.2918 | 11.0391 | -4.502 | -12.1037 | -12.7934
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Consumer Transformation | Thermal headroom (MW) | 0.66575 | 0.55231 | 0.61578 | 0.47698 | 0.21691 | -0.15239 | -0.60837 | -1.0158 | -1.5337 | -2.774 | -3.3583 | -3.9144 | -4.4671 | -4.8645 | -5.1338 | -5.3614 | -8.5738 | -10.3274 | -10.2145
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Leading the Way | Thermal headroom (MW) | 0.64044 | 0.53139 | 0.63298 | 0.49881 | 0.22827 | -0.1837 | -0.63156 | -1.034 | -2.3054 | -2.8771 | -3.4489 | -3.8508 | -4.179 | -4.3094 | -4.2513 | -5.2162 | -6.8989 | -6.9934 | -6.3516
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Steady Progression | Thermal headroom (MW) | 0.7344 | 0.88442 | 1.2412 | 1.3837 | 1.4322 | 1.4636 | 1.559 | 1.6253 | 1.6449 | 1.6719 | 1.6103 | 1.4842 | 1.252 | 1.0425 | 0.80451 | -0.18999 | -1.8701 | -3.8445 | -4.0844
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | System Transformation | Thermal headroom (MW) | 0.69206 | 0.81341 | 1.1187 | 1.2167 | 1.2128 | 1.1748 | 1.1768 | 1.1493 | 1.088 | 0.98157 | 0.71251 | -0.3157 | -0.72777 | -1.1136 | -1.5044 | -1.9032 | -3.9131 | -5.0977 | -5.3212
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | WPD Best View | Thermal headroom (MW) | 0.66575 | 0.55231 | 0.61578 | 0.47698 | 0.21691 | -0.15239 | -0.60837 | -1.0158 | -1.5337 | -2.774 | -3.3583 | -3.9144 | -4.4671 | -4.8645 | -5.1338 | -5.3614 | -8.5738 | -10.3274 | -10.2145
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Consumer Transformation | Thermal headroom (MW) | 16.0791 | 15.7255 | 15.4869 | 15.1323 | 14.7395 | 14.1031 | 13.0358 | 12.039 | 11.088 | 9.7592 | 8.7943 | 7.6521 | 6.3502 | 4.3721 | 2.3292 | 0.27581 | -6.843 | -10.1487 | -10.5981
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Leading the Way | Thermal headroom (MW) | 16.0378 | 15.6078 | 15.4715 | 15.1508 | 14.7562 | 14.1272 | 12.9924 | 11.9609 | 10.6141 | 9.5844 | 8.6368 | 7.8948 | 6.5892 | 4.6823 | 2.7611 | 0.63735 | -4.1835 | -5.1091 | -3.2107
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Steady Progression | Thermal headroom (MW) | 16.1838 | 16.2391 | 16.5002 | 16.5126 | 16.5542 | 16.5587 | 16.4596 | 16.351 | 16.2702 | 16.166 | 16.0044 | 15.7393 | 15.3889 | 14.8763 | 14.3176 | 13.3528 | 10.5088 | 6.4316 | 4.7505
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | System Transformation | Thermal headroom (MW) | 16.1258 | 16.1125 | 16.2464 | 16.2555 | 16.2136 | 16.1588 | 15.9033 | 15.605 | 15.3873 | 15.116 | 14.7593 | 13.8808 | 13.3025 | 12.4752 | 11.6415 | 10.7989 | 6.2152 | 2.4712 | 1.9411
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | WPD Best View | Thermal headroom (MW) | 16.0791 | 15.7255 | 15.4869 | 15.1323 | 14.7395 | 14.1031 | 13.0358 | 12.039 | 11.088 | 9.7592 | 8.7943 | 7.6521 | 6.3502 | 4.3721 | 2.3292 | 0.27581 | -6.843 | -10.1487 | -10.5981
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Consumer Transformation | Thermal headroom (MW) | 9.6375 | 8.994 | 8.7212 | 8.2414 | 7.4075 | 6.6941 | 5.4445 | 4.254 | 2.6599 | 1.416 | -0.36128 | -2.3789 | -4.0707 | -5.5817 | -8.2602 | -10.6081 | -19.8387 | -24.0278 | -25.2757
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Leading the Way | Thermal headroom (MW) | 9.5617 | 8.777 | 8.6394 | 7.7955 | 7.3323 | 6.6408 | 5.3872 | 3.8884 | 2.6563 | 1.0249 | -0.4573 | -2.0481 | -3.3191 | -5.3246 | -7.308 | -8.9968 | -14.7548 | -16.8922 | -15.0712
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Steady Progression | Thermal headroom (MW) | 9.7885 | 9.7232 | 10.0598 | 10.0727 | 10.135 | 10.1434 | 10.142 | 10.094 | 10.0323 | 9.9097 | 9.578 | 8.7302 | 8.3021 | 7.8301 | 6.9788 | 6.4262 | 1.9073 | -2.0581 | -3.9074
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | System Transformation | Thermal headroom (MW) | 9.7008 | 9.4994 | 9.7439 | 9.7466 | 9.761 | 9.675 | 9.5282 | 9.354 | 8.7676 | 8.417 | 7.7348 | 6.5848 | 5.5296 | 4.4875 | 3.3801 | 2.2949 | -3.3599 | -7.2366 | -8.3014
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | WPD Best View | Thermal headroom (MW) | 9.6375 | 8.994 | 8.7212 | 8.2414 | 7.4075 | 6.6941 | 5.4445 | 4.254 | 2.6599 | 1.416 | -0.36128 | -2.3789 | -4.0707 | -5.5817 | -8.2602 | -10.6081 | -19.8387 | -24.0278 | -25.2757
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Consumer Transformation | Thermal headroom (MW) | 2.4342 | 2.2939 | 2.076 | 1.9123 | 1.6276 | 1.3906 | 0.91082 | 0.45872 | -0.050723 | -0.9389 | -1.4651 | -2.1066 | -2.6766 | -3.1471 | -4.0915 | -5.0782 | -9.2595 | -11.1891 | -11.3978
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Leading the Way | Thermal headroom (MW) | 2.423 | 2.0973 | 2.0737 | 1.9228 | 1.6222 | 1.3827 | 0.90333 | 0.44608 | -0.45753 | -0.99509 | -1.5173 | -1.9669 | -2.3144 | -2.9677 | -3.8424 | -4.9739 | -7.4053 | -8.0254 | -7.041
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Steady Progression | Thermal headroom (MW) | 2.4836 | 2.5689 | 2.7813 | 2.681 | 2.6635 | 2.7239 | 2.768 | 2.7802 | 2.7912 | 2.7755 | 2.725 | 2.6109 | 2.4269 | 2.2406 | 2.0184 | 1.4186 | -0.041619 | -1.4192 | -1.6768
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | System Transformation | Thermal headroom (MW) | 2.4589 | 2.5122 | 2.5042 | 2.5345 | 2.4685 | 2.5067 | 2.4985 | 2.4676 | 2.4007 | 2.2966 | 2.1078 | 1.5012 | 1.1949 | 0.86957 | 0.52956 | 0.1966 | -1.332 | -2.9037 | -3.1426
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | WPD Best View | Thermal headroom (MW) | 2.4342 | 2.2939 | 2.076 | 1.9123 | 1.6276 | 1.3906 | 0.91082 | 0.45872 | -0.050723 | -0.9389 | -1.4651 | -2.1066 | -2.6766 | -3.1471 | -4.0915 | -5.0782 | -9.2595 | -11.1891 | -11.3978
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Consumer Transformation | Thermal headroom (MW) | 2.2047 | 2.0767 | 2.0311 | 1.8845 | 1.6978 | 1.4799 | 1.1125 | 0.77049 | 0.3962 | -0.33878 | -0.70081 | -1.1321 | -1.4978 | -1.8002 | -2.0448 | -2.3378 | -4.3882 | -5.7027 | -5.9018
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Leading the Way | Thermal headroom (MW) | 2.1924 | 2.0557 | 2.0149 | 1.8643 | 1.6696 | 1.4613 | 1.0878 | 0.75943 | 0.033023 | -0.38508 | -0.73251 | -1.012 | -1.1828 | -1.3411 | -1.4674 | -1.9208 | -3.2399 | -3.5596 | -3.1801
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Steady Progression | Thermal headroom (MW) | 2.2404 | 2.2807 | 2.4104 | 2.4459 | 2.4517 | 2.463 | 2.4918 | 2.4941 | 2.4898 | 2.4178 | 2.3372 | 2.1851 | 2.0245 | 1.8379 | 1.6163 | 1.0249 | -0.38327 | -2.0178 | -2.3213
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | System Transformation | Thermal headroom (MW) | 2.2257 | 2.2381 | 2.3417 | 2.3457 | 2.3041 | 2.2846 | 2.2544 | 2.2261 | 2.1186 | 1.9561 | 1.7822 | 1.1629 | 0.88133 | 0.57177 | 0.24757 | -0.078802 | -1.7912 | -2.6995 | -2.9072
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | WPD Best View | Thermal headroom (MW) | 2.2047 | 2.0767 | 2.0311 | 1.8845 | 1.6978 | 1.4799 | 1.1125 | 0.77049 | 0.3962 | -0.33878 | -0.70081 | -1.1321 | -1.4978 | -1.8002 | -2.0448 | -2.3378 | -4.3882 | -5.7027 | -5.9018
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Consumer Transformation | Thermal headroom (MW) | 11.2487 | 11.3288 | 11.5951 | 11.6858 | 11.7713 | 11.8259 | 11.756 | 11.6962 | 11.6251 | 11.157 | 11.0014 | 10.4548 | 10.2824 | 10.1743 | 10.174 | 9.9923 | 9.4358 | 8.2838 | 8.6272
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Leading the Way | Thermal headroom (MW) | 11.1488 | 11.1939 | 11.4943 | 11.6056 | 11.6899 | 11.7627 | 11.7151 | 11.6652 | 11.238 | 11.1131 | 10.9746 | 10.3903 | 10.3412 | 10.3763 | 10.538 | 10.0956 | 9.8484 | 10.1764 | 11.2282
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Steady Progression | Thermal headroom (MW) | 11.3464 | 11.5531 | 12.0083 | 12.1933 | 12.4113 | 12.6177 | 12.7926 | 12.9585 | 13.1243 | 13.258 | 13.3771 | 13.2348 | 13.2735 | 13.3092 | 13.2477 | 12.7168 | 11.9457 | 11.2906 | 11.5375
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | System Transformation | Thermal headroom (MW) | 11.2712 | 11.4515 | 11.8418 | 12.0559 | 12.2623 | 12.4646 | 12.6358 | 12.7712 | 12.898 | 12.9852 | 13.0291 | 12.3049 | 12.2156 | 12.0829 | 11.9193 | 11.5817 | 10.6536 | 10.471 | 10.8262
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | WPD Best View | Thermal headroom (MW) | 11.2487 | 11.3288 | 11.5951 | 11.6858 | 11.7713 | 11.8259 | 11.756 | 11.6962 | 11.6251 | 11.157 | 11.0014 | 10.4548 | 10.2824 | 10.1743 | 10.174 | 9.9923 | 9.0332 | 8.2838 | 8.6272
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Consumer Transformation | Thermal headroom (MW) | 79.6491 | 79.132 | 78.8659 | 78.0992 | 76.7892 | 75.8872 | 74.3081 | 72.3718 | 70.5481 | 68.559 | 66.6958 | 63.9206 | 61.395 | 59.1848 | 56.1358 | 53.7273 | 42.3974 | 37.5545 | 37.1386
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Leading the Way | Thermal headroom (MW) | 79.5969 | 79.0851 | 78.9178 | 77.5093 | 76.8363 | 75.9608 | 74.4239 | 72.2817 | 70.0429 | 68.1559 | 66.1493 | 63.857 | 61.4489 | 59.2237 | 56.6422 | 54.6138 | 47.8252 | 45.9931 | 48.9066
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Steady Progression | Thermal headroom (MW) | 79.8351 | 79.9979 | 80.485 | 80.5075 | 80.5884 | 80.7214 | 80.7467 | 80.4806 | 80.2589 | 80.0317 | 79.6613 | 78.3953 | 77.4319 | 76.502 | 75.486 | 74.1722 | 67.3424 | 60.8677 | 58.7586
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | System Transformation | Thermal headroom (MW) | 79.7405 | 79.831 | 80.228 | 80.0898 | 80.0587 | 80.0765 | 79.9605 | 79.2691 | 78.1329 | 77.557 | 76.6862 | 75.3251 | 73.7233 | 71.6377 | 70.1682 | 68.7735 | 60.4526 | 56.2912 | 55.7994
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | WPD Best View | Thermal headroom (MW) | 79.7118 | 79.3743 | 79.3174 | 78.7497 | 77.959 | 77.3289 | 76.1548 | 74.6353 | 73.2173 | 71.5834 | 70.0601 | 67.6235 | 65.4019 | 63.5648 | 61.3922 | 59.3434 | 49.3254 | 43.8087 | 42.8895
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Consumer Transformation | Thermal headroom (MW) | 2.0527 | 1.812 | 1.6396 | 1.2617 | 0.58682 | 0.1665 | -0.51365 | -1.5558 | -2.2949 | -3.0217 | -3.753 | -4.946 | -5.9315 | -6.8546 | -8.4562 | -9.6654 | -15.3656 | -17.7402 | -18.1373
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Leading the Way | Thermal headroom (MW) | 2.0159 | 1.7922 | 1.6586 | 0.88463 | 0.61186 | 0.1978 | -0.47867 | -1.6373 | -2.4355 | -3.2107 | -3.9869 | -4.9727 | -6.1236 | -7.3693 | -8.7795 | -9.7442 | -13.2234 | -14.2843 | -12.9942
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Steady Progression | Thermal headroom (MW) | 2.1303 | 2.1562 | 2.2845 | 2.2175 | 2.2174 | 2.217 | 2.1703 | 1.8702 | 1.7251 | 1.5026 | 1.2849 | 0.5788 | 0.086328 | -0.33541 | -0.80142 | -1.2956 | -4.7258 | -7.8293 | -8.9772
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | System Transformation | Thermal headroom (MW) | 2.0899 | 2.093 | 2.1766 | 2.056 | 2.0315 | 1.9636 | 1.8515 | 1.3093 | 0.67103 | 0.32688 | -0.085712 | -0.582 | -1.3895 | -2.4262 | -3.084 | -3.7177 | -7.9565 | -9.7853 | -10.1924
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | WPD Best View | Thermal headroom (MW) | 2.072 | 1.9037 | 1.8231 | 1.5329 | 0.95814 | 0.69501 | 0.19797 | -0.65115 | -1.1896 | -1.7543 | -2.3061 | -3.3411 | -4.1821 | -4.7984 | -5.7891 | -6.703 | -11.7079 | -14.3352 | -14.8348
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Consumer Transformation | Thermal headroom (MW) | 10.6005 | 10.3481 | 10.1582 | 9.8683 | 9.5704 | 9.1172 | 8.3446 | 7.5254 | 6.799 | 5.7084 | 4.9268 | 3.8874 | 2.5338 | 1.4638 | 0.35592 | -0.71129 | -5.1098 | -7.1526 | -7.3752
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Leading the Way | Thermal headroom (MW) | 10.6068 | 10.3489 | 10.2314 | 9.9893 | 9.6981 | 9.2574 | 8.5339 | 7.5692 | 6.48 | 5.6642 | 4.8244 | 4.0589 | 2.8602 | 1.9257 | 1.0331 | -0.13245 | -2.5906 | -3.3809 | -2.6373
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Steady Progression | Thermal headroom (MW) | 10.6786 | 10.7586 | 10.9355 | 10.9907 | 11.0464 | 11.0999 | 11.1308 | 11.0346 | 11.0009 | 10.976 | 10.9327 | 10.7205 | 10.3667 | 10.0476 | 9.7031 | 8.998 | 7.0318 | 5.0199 | 4.3347
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | System Transformation | Thermal headroom (MW) | 10.647 | 10.6834 | 10.8229 | 10.8309 | 10.8579 | 10.8592 | 10.7981 | 10.511 | 10.4609 | 10.3017 | 10.068 | 9.3445 | 8.774 | 8.2645 | 7.763 | 7.3003 | 4.8501 | 2.9173 | 2.5887
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | WPD Best View | Thermal headroom (MW) | 10.6005 | 10.3481 | 10.1582 | 9.8683 | 9.5704 | 9.1172 | 8.3446 | 7.5254 | 6.799 | 5.7084 | 4.9268 | 3.8874 | 2.5338 | 1.4638 | 0.35592 | -0.71129 | -5.1098 | -7.1526 | -7.3752
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Consumer Transformation | Thermal headroom (MW) | 44.5687 | 43.4474 | 41.8174 | 39.8586 | 37.9531 | 36.4205 | 34.364 | 32.3285 | 30.1549 | 27.5631 | 25.43 | 22.72 | 20.2212 | 18.0153 | 15.7212 | 13.7173 | 4.1996 | 0.56286 | 0.76388
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Leading the Way | Thermal headroom (MW) | 44.3819 | 42.9556 | 41.0013 | 38.395 | 36.3534 | 34.7394 | 32.5564 | 30.4376 | 27.7519 | 25.5923 | 23.4644 | 21.3133 | 19.5018 | 17.8846 | 16.3459 | 14.2183 | 8.9578 | 8.4481 | 11.3142
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Steady Progression | Thermal headroom (MW) | 44.8163 | 44.4469 | 43.9254 | 42.8933 | 42.1674 | 41.7759 | 41.339 | 40.8631 | 40.3888 | 39.8952 | 39.2778 | 38.2341 | 37.3208 | 36.3122 | 35.1525 | 33.4332 | 26.1292 | 19.4536 | 17.99
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | System Transformation | Thermal headroom (MW) | 44.6481 | 44.0421 | 42.9982 | 41.6131 | 40.5682 | 39.9824 | 39.3262 | 38.5743 | 37.5142 | 36.6267 | 35.5509 | 33.8556 | 32.4381 | 30.6797 | 28.9495 | 27.2245 | 19.3449 | 15.972 | 16.1009
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | WPD Best View | Thermal headroom (MW) | 44.5978 | 43.55 | 42.003 | 40.1236 | 38.4839 | 37.0431 | 35.1468 | 33.2758 | 31.2595 | 28.8157 | 26.8156 | 24.2525 | 21.8883 | 19.7798 | 17.7337 | 15.8258 | 6.7848 | 2.782 | 2.7172
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Consumer Transformation | Thermal headroom (MW) | -0.89762 | -2.0194 | -3.0857 | -3.6589 | -3.9316 | -4.5634 | -5.3926 | -6.1238 | -6.8338 | -7.9044 | -8.6247 | -9.4959 | -10.415 | -11.1502 | -11.9209 | -12.657 | -15.5567 | -16.6881 | -16.52
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Leading the Way | Thermal headroom (MW) | -1.1075 | -2.5392 | -3.9333 | -4.598 | -4.8883 | -5.5006 | -6.3508 | -7.067 | -8.0434 | -8.6606 | -9.2632 | -9.8934 | -10.483 | -10.9926 | -11.5299 | -12.3333 | -13.7892 | -13.8836 | -13.3319
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Steady Progression | Thermal headroom (MW) | -0.71011 | -1.3793 | -1.9497 | -2.2474 | -2.3319 | -2.524 | -2.7081 | -2.8836 | -3.0085 | -3.1702 | -3.326 | -3.5894 | -3.8066 | -3.9857 | -4.2912 | -5.0207 | -6.9187 | -8.9227 | -9.2637
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | System Transformation | Thermal headroom (MW) | -0.87265 | -1.8141 | -2.6623 | -3.0403 | -3.0786 | -3.3513 | -3.6306 | -3.8808 | -4.0923 | -4.3099 | -4.5687 | -5.1691 | -5.496 | -5.8711 | -6.3319 | -6.7754 | -8.9413 | -10.3057 | -10.4312
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | WPD Best View | Thermal headroom (MW) | -0.89762 | -2.0194 | -3.0857 | -3.6589 | -3.9316 | -4.5634 | -5.3926 | -6.1238 | -6.8338 | -7.9044 | -8.6247 | -9.4959 | -10.415 | -11.1502 | -11.9209 | -12.657 | -15.5567 | -16.6881 | -16.52
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Consumer Transformation | Thermal headroom (MW) | 4.5109 | 4.4809 | 4.5746 | 4.5351 | 4.2072 | 4.0048 | 3.689 | 2.9922 | 2.5889 | 2.1734 | 1.7658 | 1.1847 | 0.57402 | 0.042416 | -0.50901 | -1.0489 | -3.0856 | -3.6542 | -3.3882
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Leading the Way | Thermal headroom (MW) | 4.492 | 4.4302 | 4.6063 | 4.5946 | 4.1718 | 3.9784 | 3.6167 | 2.8011 | 2.3637 | 1.8902 | 1.4323 | 0.93658 | 0.48482 | 0.038541 | -0.37866 | -0.78406 | -1.7327 | -1.6433 | -0.52239
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Steady Progression | Thermal headroom (MW) | 4.5624 | 4.7023 | 5.0367 | 5.1344 | 5.0951 | 5.1816 | 5.3054 | 5.1565 | 5.2048 | 5.2717 | 5.2914 | 5.2514 | 5.1794 | 5.0092 | 4.7752 | 4.4964 | 2.9247 | 1.8052 | 1.6177
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | System Transformation | Thermal headroom (MW) | 4.5343 | 4.6489 | 4.9124 | 5.0405 | 4.8998 | 4.9478 | 4.9795 | 4.6619 | 4.6291 | 4.5958 | 4.5125 | 4.3989 | 4.0565 | 3.6832 | 3.3178 | 2.9524 | 1.8335 | 1.0807 | 1.5114
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | WPD Best View | Thermal headroom (MW) | 4.5122 | 4.4837 | 4.5806 | 4.5449 | 4.2218 | 4.0261 | 3.7188 | 3.0326 | 2.6434 | 2.2443 | 1.8557 | 1.2982 | 0.71311 | 0.20817 | -0.31798 | -0.83028 | -2.8311 | -3.4935 | -3.2439
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Consumer Transformation | Thermal headroom (MW) | 2.6582 | 2.5459 | 2.5016 | 2.4109 | 1.9517 | 1.8216 | 1.55 | 1.257 | 0.95692 | 0.64957 | 0.35936 | -0.33155 | -0.62573 | -0.86125 | -1.3853 | -1.6055 | -3.6519 | -4.672 | -4.683
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Leading the Way | Thermal headroom (MW) | 2.6288 | 2.5072 | 2.474 | 2.0239 | 1.9422 | 1.8077 | 1.5478 | 1.2627 | 0.95607 | 0.64017 | 0.34068 | -0.23411 | -0.40414 | -0.50725 | -0.96602 | -1.0322 | -2.4637 | -2.93 | -2.2329
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Steady Progression | Thermal headroom (MW) | 2.7155 | 2.7463 | 2.8641 | 2.9282 | 2.984 | 3.0297 | 3.0634 | 3.0782 | 3.0979 | 3.0718 | 3.0035 | 2.5336 | 2.41 | 2.2485 | 2.0721 | 1.888 | 0.44489 | -1.1261 | -1.6663
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | System Transformation | Thermal headroom (MW) | 2.6739 | 2.679 | 2.7736 | 2.8188 | 2.8617 | 2.8868 | 2.8747 | 2.8511 | 2.4123 | 2.2903 | 2.1507 | 1.9471 | 1.695 | 1.0821 | 0.80039 | 0.54084 | -1.5419 | -2.5666 | -2.714
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | WPD Best View | Thermal headroom (MW) | 2.7105 | 2.7352 | 2.8415 | 2.8926 | 2.9325 | 2.9583 | 2.9695 | 2.9606 | 2.9193 | 2.8423 | 2.7507 | 2.2676 | 2.1511 | 2.0176 | 1.8918 | 1.7676 | 0.52809 | -0.89607 | -1.369
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Consumer Transformation | Thermal headroom (MW) | 4.6671 | 4.5666 | 3.4354 | 1.6863 | 0.1865 | -0.57245 | -1.3815 | -2.0517 | -2.8266 | -3.9603 | -4.6848 | -5.4935 | -6.3182 | -7.0818 | -7.8976 | -8.6802 | -11.3773 | -12.0425 | -11.5385
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Leading the Way | Thermal headroom (MW) | 4.6524 | 4.4524 | 3.0265 | 0.67228 | -1.289 | -2.2116 | -3.1407 | -3.9076 | -5.061 | -5.8403 | -6.4538 | -6.9951 | -7.5618 | -8.1491 | -8.687 | -9.467 | -10.3503 | -9.933 | -9.0722
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Steady Progression | Thermal headroom (MW) | 4.6962 | 4.7082 | 4.0699 | 2.7916 | 1.8028 | 1.404 | 1.0119 | 0.72608 | 0.4494 | 0.19327 | -0.059251 | -0.35497 | -0.67578 | -0.98589 | -1.3464 | -2.0371 | -3.7186 | -6.1576 | -6.3263
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | System Transformation | Thermal headroom (MW) | 4.6825 | 4.6758 | 3.6532 | 1.988 | 0.62274 | 0.12517 | -0.34426 | -0.70315 | -1.1063 | -1.5305 | -1.9155 | -2.667 | -3.0276 | -3.4498 | -3.904 | -4.3759 | -6.8605 | -7.7608 | -7.5794
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | WPD Best View | Thermal headroom (MW) | 4.6684 | 4.5695 | 3.4414 | 1.696 | 0.20111 | -0.55115 | -1.3517 | -2.0112 | -2.7721 | -3.8894 | -4.5948 | -5.38 | -6.1791 | -6.916 | -7.7065 | -8.4616 | -11.1229 | -11.8818 | -11.3941
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Consumer Transformation | Thermal headroom (MW) | 1.9393 | 1.7853 | 1.6245 | 1.4086 | 1.153 | 0.83594 | 0.37843 | -0.086362 | -0.58706 | -1.0822 | -1.568 | -2.177 | -2.727 | -3.2233 | -3.6236 | -3.9719 | -6.3521 | -7.4314 | -7.6993
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Leading the Way | Thermal headroom (MW) | 1.9292 | 1.7611 | 1.6422 | 1.4306 | 1.1892 | 0.87251 | 0.39693 | -0.063662 | -0.57693 | -1.1114 | -1.6673 | -2.1779 | -2.6013 | -2.9416 | -3.1254 | -3.6757 | -5.2913 | -5.6733 | -5.0483
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Steady Progression | Thermal headroom (MW) | 1.9751 | 1.9656 | 1.9874 | 1.9431 | 1.9085 | 1.8437 | 1.7535 | 1.633 | 1.4985 | 1.3311 | 1.1362 | 0.87678 | 0.60732 | 0.28504 | -0.03415 | -0.38272 | -2.5922 | -4.0602 | -4.5638
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | System Transformation | Thermal headroom (MW) | 1.9616 | 1.9377 | 1.9211 | 1.87 | 1.8076 | 1.7038 | 1.5638 | 1.385 | 1.1568 | 0.89261 | 0.5827 | 0.19442 | -0.22072 | -0.67817 | -1.1917 | -1.7136 | -3.7144 | -4.392 | -4.4478
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | WPD Best View | Thermal headroom (MW) | 1.9393 | 1.7853 | 1.6245 | 1.4086 | 1.153 | 0.83594 | 0.37843 | -0.086362 | -0.58706 | -1.0822 | -1.568 | -2.177 | -2.727 | -3.2233 | -3.6236 | -3.9719 | -6.3521 | -7.4314 | -7.6993
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Consumer Transformation | Thermal headroom (MW) | -1.0138 | -1.0765 | -0.99441 | -1.2618 | -1.4904 | -1.6747 | -2.0337 | -2.4055 | -3.0917 | -3.6255 | -4.3344 | -5.0434 | -5.8077 | -6.5601 | -7.3218 | -8.0407 | -10.7365 | -11.581 | -11.4518
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Leading the Way | Thermal headroom (MW) | -1.016 | -1.073 | -0.98334 | -1.3168 | -1.5832 | -1.7417 | -2.1112 | -2.5011 | -3.3423 | -3.9567 | -4.7554 | -5.4426 | -6.154 | -6.8478 | -7.4538 | -7.9844 | -9.4393 | -9.4152 | -8.2784
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Steady Progression | Thermal headroom (MW) | -0.98825 | -0.89762 | -0.65607 | -0.68494 | -0.6971 | -0.6094 | -0.59039 | -0.53109 | -0.68295 | -0.68942 | -0.85111 | -1.0535 | -1.3654 | -1.7046 | -2.0729 | -2.4507 | -4.5893 | -6.36 | -6.6838
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | System Transformation | Thermal headroom (MW) | -0.99238 | -0.9013 | -0.66951 | -0.8039 | -0.91172 | -0.83062 | -0.78146 | -0.80965 | -1.1247 | -1.2405 | -1.6263 | -2.0284 | -2.5183 | -3.0537 | -3.5674 | -4.069 | -6.0861 | -6.6788 | -6.3471
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | WPD Best View | Thermal headroom (MW) | -1.0112 | -1.0708 | -0.9824 | -1.2424 | -1.4612 | -1.6321 | -1.974 | -2.3246 | -2.9827 | -3.4792 | -4.1545 | -4.8163 | -5.5295 | -6.2286 | -6.9398 | -7.6035 | -10.2275 | -11.2596 | -11.163
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Consumer Transformation | Thermal headroom (MW) | 45.5821 | 42.3806 | 37.9429 | 32.5663 | 26.0472 | 19.7814 | 11.8463 | 5.1403 | -2.4621 | -10.6704 | -18.6726 | -29.536 | -39.3664 | -48.2826 | -59.0355 | -68.0618 | -114.7317 | -128.3753 | -129.2708
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Leading the Way | Thermal headroom (MW) | 45.2875 | 41.4939 | 36.2178 | 29.3557 | 23.634 | 16.3757 | 6.9312 | -0.26552 | -8.7964 | -17.1004 | -25.3899 | -34.78 | -42.6961 | -50.4015 | -58.8169 | -65.7535 | -101.8662 | -106.1759 | -95.2503
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Steady Progression | Thermal headroom (MW) | 46.2414 | 45.6175 | 44.5205 | 42.3828 | 39.7607 | 37.6463 | 35.6712 | 34.0111 | 31.7504 | 29.6674 | 27.2789 | 22.9711 | 19.6255 | 15.7895 | 11.6766 | 6.6527 | -26.4663 | -51.6755 | -59.7254
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | System Transformation | Thermal headroom (MW) | 45.8458 | 44.6924 | 42.2614 | 38.8453 | 35.9682 | 32.8886 | 29.5667 | 26.8964 | 22.2336 | 18.8421 | 15.0878 | 9.48 | 4.1186 | -2.8867 | -8.9653 | -15.2218 | -57.0073 | -73.7398 | -74.5359
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | WPD Best View | Thermal headroom (MW) | 45.4011 | 42.0705 | 37.1271 | 30.2521 | 23.9145 | 17.3717 | 8.5412 | 1.8019 | -5.4398 | -13.3665 | -20.8988 | -29.6467 | -37.4389 | -44.6348 | -53.4095 | -60.3123 | -102.6721 | -113.1014 | -108.2686
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Consumer Transformation | Thermal headroom (MW) | 12.4665 | 12.3624 | 12.2555 | 11.619 | 11.3446 | 10.9319 | 10.45 | 9.9589 | 9.4489 | 8.9271 | 8.4181 | 7.9166 | 7.5402 | 7.1575 | 6.8339 | 6.5801 | 5.9357 | 5.7031 | 5.8866
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Leading the Way | Thermal headroom (MW) | 12.4519 | 12.3419 | 11.854 | 11.6005 | 11.3128 | 10.8976 | 10.3924 | 9.8784 | 9.3478 | 8.8009 | 8.3139 | 7.9454 | 7.6288 | 7.3756 | 7.2721 | 7.2557 | 6.7867 | 6.9906 | 7.9012
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Steady Progression | Thermal headroom (MW) | 12.5213 | 12.5565 | 12.6641 | 12.6234 | 12.157 | 12.0954 | 12.0152 | 11.8934 | 11.7482 | 11.5699 | 11.3535 | 11.0856 | 10.7912 | 10.4651 | 10.1156 | 9.7458 | 7.7324 | 6.545 | 6.2478
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | System Transformation | Thermal headroom (MW) | 12.493 | 12.509 | 12.5728 | 12.0872 | 11.9816 | 11.8748 | 11.6943 | 11.4905 | 11.2443 | 10.9364 | 10.5745 | 10.1447 | 9.6816 | 9.1982 | 8.7081 | 8.2485 | 6.3981 | 6.0894 | 6.3383
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | WPD Best View | Thermal headroom (MW) | 12.5063 | 12.5034 | 12.5398 | 12.4173 | 11.8584 | 11.6679 | 11.4369 | 11.1782 | 10.8988 | 10.6136 | 10.3218 | 10.0362 | 9.7902 | 9.5824 | 9.3488 | 9.0999 | 7.918 | 7.3962 | 7.4846
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Consumer Transformation | Thermal headroom (MW) | 10.7884 | 10.1148 | 9.8717 | 9.529 | 9.1493 | 8.8502 | 8.4267 | 8.0048 | 7.4997 | 6.6306 | 6.1352 | 5.4144 | 4.552 | 3.6859 | 2.7513 | 1.9201 | -1.539 | -2.934 | -2.8767
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Leading the Way | Thermal headroom (MW) | 10.7792 | 9.8805 | 9.5826 | 9.1565 | 8.7002 | 8.4119 | 7.9425 | 7.5322 | 6.7005 | 6.1717 | 5.4939 | 4.7093 | 3.9225 | 3.0935 | 2.3163 | 1.2811 | -0.49893 | -0.50561 | 0.53024
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Steady Progression | Thermal headroom (MW) | 10.8394 | 10.4851 | 10.4889 | 10.3693 | 10.1986 | 10.1515 | 10.1036 | 10.0403 | 9.9631 | 9.8538 | 9.6969 | 9.5079 | 9.2647 | 8.9721 | 8.6812 | 8.0033 | 6.3416 | 3.5768 | 3.0286
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | System Transformation | Thermal headroom (MW) | 10.819 | 10.2852 | 10.176 | 9.9561 | 9.7493 | 9.6812 | 9.5623 | 9.4242 | 9.2233 | 9.0087 | 8.7666 | 8.0514 | 7.6601 | 7.2409 | 6.8159 | 6.406 | 3.3785 | 1.6434 | 1.5479
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | WPD Best View | Thermal headroom (MW) | 10.7793 | 9.8853 | 9.5907 | 9.1506 | 8.6633 | 8.3715 | 7.9059 | 7.4969 | 7.0762 | 6.2651 | 5.6427 | 4.84 | 4.0803 | 3.2682 | 2.46 | 1.769 | -0.78653 | -1.5751 | -0.61578
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Consumer Transformation | Thermal headroom (MW) | 3.0287 | 2.8474 | 2.7973 | 2.5773 | 2.3341 | 1.9068 | 1.2176 | 0.60385 | -0.042605 | -0.74094 | -1.5073 | -2.5925 | -3.6045 | -4.5945 | -5.5997 | -6.6456 | -10.5619 | -11.9195 | -11.8948
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Leading the Way | Thermal headroom (MW) | 2.9823 | 2.7594 | 2.7373 | 2.528 | 2.2846 | 1.8814 | 1.1768 | 0.59702 | -0.096691 | -0.83908 | -1.6755 | -2.6735 | -3.5868 | -4.513 | -5.4228 | -6.3011 | -8.5561 | -8.7425 | -7.0366
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Steady Progression | Thermal headroom (MW) | 3.1267 | 3.207 | 3.4765 | 3.5541 | 3.6228 | 3.6644 | 3.7316 | 3.8122 | 3.819 | 3.8487 | 3.8301 | 3.6403 | 3.4747 | 3.2916 | 3.0508 | 2.7469 | 0.3247 | -2.3631 | -2.9166
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | System Transformation | Thermal headroom (MW) | 3.0626 | 3.0785 | 3.2653 | 3.2786 | 3.3005 | 3.3902 | 3.3566 | 3.3029 | 3.2246 | 3.0984 | 2.9157 | 2.5228 | 2.1792 | 1.7541 | 1.2479 | 0.65886 | -2.6593 | -4.2835 | -3.9544
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | WPD Best View | Thermal headroom (MW) | 3.0075 | 2.7948 | 2.7483 | 2.5243 | 2.2897 | 1.8789 | 1.1804 | 0.60122 | -0.032742 | -0.68571 | -1.4003 | -2.3334 | -3.1912 | -4.0803 | -4.9829 | -5.8642 | -9.1283 | -10.2728 | -9.7821
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Consumer Transformation | Thermal headroom (MW) | 17.5509 | 17.0697 | 16.0384 | 15.0548 | 13.6623 | 12.4454 | 10.9291 | 9.7282 | 8.4794 | 7.2886 | 6.0384 | 4.2295 | 2.7482 | 1.4504 | -0.26114 | -1.6271 | -10.0357 | -12.1259 | -12.3173
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Leading the Way | Thermal headroom (MW) | 17.4952 | 16.9419 | 15.8302 | 14.3311 | 13.1758 | 11.6915 | 9.8026 | 8.4883 | 7.1928 | 5.8779 | 4.668 | 3.2597 | 2.1713 | 1.1839 | -0.12971 | -1.0176 | -8.2478 | -9.2895 | -8.0206
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Steady Progression | Thermal headroom (MW) | 17.6557 | 17.5444 | 17.1105 | 16.5772 | 16.0986 | 15.5708 | 15.083 | 14.6972 | 14.2461 | 13.8096 | 13.3377 | 12.4383 | 11.8445 | 11.241 | 10.6125 | 9.9539 | 4.527 | 1.2205 | -0.07183
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | System Transformation | Thermal headroom (MW) | 17.5879 | 17.417 | 16.7145 | 16.0584 | 15.402 | 14.7098 | 13.966 | 13.4173 | 12.3948 | 11.7519 | 11.0666 | 10.2897 | 9.4756 | 8.3027 | 7.4978 | 6.6709 | -0.063285 | -2.4697 | -2.7847
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | WPD Best View | Thermal headroom (MW) | 17.4936 | 17.0098 | 15.803 | 14.252 | 13.044 | 11.6485 | 9.799 | 8.4872 | 7.2031 | 5.9545 | 4.7566 | 3.4005 | 2.3353 | 1.38 | 0.090581 | -0.79646 | -8.2491 | -9.5758 | -8.5645
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Consumer Transformation | Thermal headroom (MW) | 13.1862 | 12.6502 | 12.5802 | 12.3338 | 11.9827 | 11.3404 | 10.5236 | 9.6876 | 7.9116 | 5.5419 | 3.2301 | 0.47231 | -2.7613 | -5.642 | -8.9526 | -11.9036 | -23.5944 | -28.256 | -29.1152
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Leading the Way | Thermal headroom (MW) | 13.1559 | 12.579 | 12.6323 | 12.3831 | 12.0336 | 11.3925 | 10.586 | 9.6483 | 7.3505 | 5.075 | 2.4038 | -0.74357 | -3.6867 | -6.9774 | -9.8714 | -12.7636 | -19.8951 | -20.7365 | -16.7749
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Steady Progression | Thermal headroom (MW) | 13.2755 | 13.4337 | 13.7746 | 13.8343 | 13.8948 | 13.914 | 13.9287 | 13.9383 | 13.5327 | 13.4441 | 13.3115 | 13.0772 | 12.6495 | 11.6626 | 10.4951 | 8.8607 | -0.92639 | -10.6267 | -13.4118
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | System Transformation | Thermal headroom (MW) | 13.2283 | 13.3439 | 13.5842 | 13.6523 | 13.6499 | 13.2033 | 13.0963 | 12.9546 | 12.7511 | 12.4907 | 12.1459 | 10.6084 | 9.1281 | 7.3838 | 4.9756 | 2.403 | -10.293 | -16.9402 | -17.0756
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | WPD Best View | Thermal headroom (MW) | 13.1913 | 12.6612 | 12.6027 | 12.381 | 12.0568 | 11.5052 | 10.7817 | 9.9571 | 8.2632 | 5.9836 | 3.768 | 1.1116 | -2.0586 | -4.8949 | -8.1666 | -11.0839 | -22.7919 | -27.62 | -28.5722
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Consumer Transformation | Thermal headroom (MW) | 11.0104 | 10.8467 | 10.8441 | 10.6751 | 10.109 | 9.708 | 9.1291 | 8.5256 | 7.8695 | 7.0312 | 6.0349 | 4.4969 | 3.2703 | 2.0684 | 0.47989 | -0.81768 | -6.2932 | -8.3889 | -8.6581
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Leading the Way | Thermal headroom (MW) | 10.969 | 10.8015 | 10.7775 | 10.2971 | 10.1016 | 9.6909 | 9.1207 | 8.5096 | 7.7602 | 6.8496 | 5.6836 | 4.1163 | 2.887 | 1.6335 | 0.090566 | -0.99861 | -4.3721 | -4.9989 | -2.9632
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Steady Progression | Thermal headroom (MW) | 11.0973 | 11.1823 | 11.3849 | 11.4819 | 11.5762 | 11.6008 | 11.6306 | 11.6303 | 11.648 | 11.5174 | 11.394 | 10.8264 | 10.5744 | 10.2185 | 9.8285 | 9.367 | 5.4863 | 0.81937 | -0.73582
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | System Transformation | Thermal headroom (MW) | 11.0486 | 11.0572 | 11.2644 | 11.334 | 11.3761 | 11.3599 | 11.2558 | 11.1592 | 10.6289 | 10.3891 | 10.0309 | 9.58 | 9.0385 | 7.994 | 7.2326 | 6.3651 | 0.62745 | -2.5477 | -2.7481
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | WPD Best View | Thermal headroom (MW) | 11.0104 | 10.8467 | 10.8441 | 10.6751 | 10.109 | 9.708 | 9.1291 | 8.5256 | 7.8695 | 7.0312 | 6.0349 | 4.4969 | 3.2703 | 2.0684 | 0.47989 | -0.81768 | -6.2932 | -8.3889 | -8.6581
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Consumer Transformation | Thermal headroom (MW) | 38.3848 | 36.0617 | 33.3561 | 30.3145 | 27.0609 | 22.8538 | 17.4958 | 12.3654 | 7.0465 | -1.1363 | -6.8331 | -12.9854 | -19.0777 | -24.9672 | -30.4655 | -35.8712 | -60.3363 | -70.1946 | -68.4491
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Leading the Way | Thermal headroom (MW) | 38.1536 | 35.4315 | 33.028 | 30.0683 | 26.7523 | 22.375 | 16.6764 | 11.1768 | 2.7171 | -3.2665 | -9.4158 | -15.1992 | -20.6615 | -25.6546 | -29.7408 | -36.4429 | -53.7071 | -51.9727 | -45.3382
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Steady Progression | Thermal headroom (MW) | 39.0981 | 39.1366 | 39.5283 | 38.8842 | 38.2546 | 37.6457 | 36.636 | 35.405 | 34.0618 | 32.3614 | 30.4065 | 27.8194 | 24.9204 | 21.6451 | 18.1268 | 11.4679 | -11.9495 | -33.7106 | -40.9511
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | System Transformation | Thermal headroom (MW) | 38.6832 | 38.3005 | 37.7512 | 36.7804 | 35.7886 | 34.4303 | 32.0431 | 29.4786 | 26.7609 | 23.5886 | 20.0797 | 13.0503 | 8.2539 | 3.132 | -2.124 | -7.8021 | -36.9727 | -49.4396 | -51.0771
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | WPD Best View | Thermal headroom (MW) | 38.6089 | 37.9419 | 37.1561 | 35.9369 | 34.6515 | 32.9555 | 30.2044 | 27.3571 | 24.3164 | 20.9326 | 17.3796 | 10.6285 | 6.1476 | 1.5266 | -3.0481 | -7.7432 | -31.6141 | -43.7809 | -44.8146
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Consumer Transformation | Thermal headroom (MW) | 2.8019 | 2.3089 | 1.575 | 0.95393 | 0.32402 | -0.79308 | -2.2585 | -3.4695 | -4.4604 | -5.879 | -6.9977 | -8.3854 | -9.6291 | -10.9233 | -12.1121 | -13.2535 | -17.1835 | -18.1546 | -17.4388
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Leading the Way | Thermal headroom (MW) | 2.7768 | 2.1284 | 0.96173 | 0.57393 | -0.16517 | -1.4042 | -3.0976 | -4.5953 | -6.0195 | -7.1369 | -8.2938 | -9.4177 | -10.319 | -11.3874 | -12.303 | -13.361 | -15.0193 | -14.3949 | -12.596
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Steady Progression | Thermal headroom (MW) | 2.8573 | 2.7294 | 2.5449 | 2.4856 | 1.9812 | 1.7288 | 1.3134 | 0.97425 | 0.79425 | 0.57367 | 0.33587 | 0.024847 | -0.29959 | -0.7361 | -1.1565 | -1.9666 | -4.8126 | -8.3614 | -8.733
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | System Transformation | Thermal headroom (MW) | 2.8287 | 2.5687 | 2.0823 | 1.7295 | 1.3753 | 0.9775 | 0.17237 | -0.42354 | -0.69477 | -1.0853 | -1.4797 | -2.4637 | -3.0601 | -3.7894 | -4.4949 | -5.259 | -9.227 | -10.9488 | -10.5459
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | WPD Best View | Thermal headroom (MW) | 2.8286 | 2.5697 | 2.0835 | 1.7324 | 1.3792 | 0.98417 | 0.1818 | -0.41047 | -0.67531 | -1.0576 | -1.442 | -2.4113 | -2.9887 | -3.695 | -4.3732 | -5.1033 | -8.9442 | -10.8019 | -10.4805
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Consumer Transformation | Thermal headroom (MW) | 16.2971 | 16.0862 | 15.7009 | 14.9081 | 14.2863 | 13.2674 | 11.737 | 10.1874 | 8.5265 | 6.8175 | 5.0778 | 3.255 | 1.3348 | -0.4928 | -2.4542 | -4.3323 | -13.0534 | -14.3716 | -12.7841
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Leading the Way | Thermal headroom (MW) | 16.2413 | 15.9551 | 15.4843 | 14.5422 | 13.7705 | 12.644 | 10.7784 | 8.793 | 6.6795 | 4.4958 | 2.347 | 0.32759 | -1.6551 | -3.6683 | -5.5909 | -7.3631 | -14.4926 | -13.0099 | -10.3932
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Steady Progression | Thermal headroom (MW) | 16.4029 | 16.4942 | 16.5454 | 16.213 | 15.9424 | 15.7206 | 15.2221 | 14.6292 | 13.9982 | 13.29 | 12.5282 | 11.6982 | 10.8121 | 9.855 | 8.8554 | 7.7665 | 1.7017 | -2.5496 | -4.4472
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | System Transformation | Thermal headroom (MW) | 16.3229 | 16.3416 | 16.1856 | 15.6498 | 15.2588 | 14.814 | 13.8654 | 12.8044 | 11.6572 | 10.4541 | 9.2147 | 7.8175 | 6.3659 | 4.8571 | 3.2479 | 1.6151 | -6.7076 | -8.8987 | -8.0726
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | WPD Best View | Thermal headroom (MW) | 16.3493 | 16.3964 | 16.3415 | 15.968 | 15.7081 | 15.3744 | 14.4389 | 13.4166 | 12.3161 | 11.1845 | 10.0007 | 8.6469 | 7.2331 | 5.7384 | 4.1377 | 2.4931 | -3.9075 | -6.7316 | -6.3064
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Consumer Transformation | Thermal headroom (MW) | 15.0502 | 14.6486 | 14.2148 | 13.7578 | 13.247 | 12.4355 | 11.4933 | 10.6007 | 9.6504 | 8.3129 | 7.0799 | 5.4014 | 3.6952 | 2.02 | 0.35341 | -1.7119 | -9.3362 | -12.5688 | -13.2616
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Leading the Way | Thermal headroom (MW) | 14.9943 | 14.4617 | 14.088 | 13.5625 | 12.9915 | 12.1442 | 11.1938 | 10.2727 | 8.938 | 7.9592 | 6.4762 | 5.0238 | 3.546 | 2.1014 | 0.64507 | -1.5525 | -6.7531 | -7.2906 | -5.8592
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Steady Progression | Thermal headroom (MW) | 15.149 | 15.0745 | 15.0815 | 14.9115 | 14.7831 | 14.6646 | 14.5651 | 14.4404 | 14.2526 | 14.0358 | 13.7351 | 13.3645 | 12.9445 | 12.4571 | 11.9238 | 10.7726 | 5.5757 | -0.85985 | -3.4205
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | System Transformation | Thermal headroom (MW) | 15.0925 | 14.9699 | 14.8458 | 14.6759 | 14.4785 | 14.2404 | 13.9669 | 13.6878 | 13.3518 | 12.9601 | 12.4591 | 11.5257 | 10.8797 | 10.1743 | 9.4321 | 8.3444 | 0.52407 | -4.4532 | -5.5572
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | WPD Best View | Thermal headroom (MW) | 15.0925 | 14.9699 | 14.8458 | 14.6759 | 14.4785 | 14.2404 | 13.9669 | 13.6878 | 13.3518 | 12.9601 | 12.4591 | 11.5257 | 10.8797 | 10.1743 | 9.4321 | 8.3444 | 0.52407 | -4.4532 | -5.5572
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Consumer Transformation | Thermal headroom (MW) | 0.33244 | 0.13134 | -0.062295 | -0.31721 | -0.62507 | -0.979 | -1.421 | -1.8795 | -2.3709 | -3.2384 | -3.7298 | -4.2422 | -4.7814 | -5.2429 | -5.6125 | -5.9211 | -7.5116 | -8.5211 | -8.4235
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Leading the Way | Thermal headroom (MW) | 0.32437 | 0.14144 | -0.010056 | -0.25829 | -0.55524 | -0.91048 | -1.3548 | -1.8127 | -2.7032 | -3.2401 | -3.7476 | -4.2835 | -4.7472 | -5.0818 | -5.2921 | -5.7491 | -7.0861 | -6.9667 | -6.3883
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Steady Progression | Thermal headroom (MW) | 0.39553 | 0.41336 | 0.46105 | 0.45148 | 0.42488 | 0.36648 | 0.27902 | 0.15826 | 0.022449 | -0.1706 | -0.3862 | -0.67426 | -0.98579 | -1.3496 | -1.7431 | -2.5263 | -4.9096 | -6.5389 | -7.0284
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | System Transformation | Thermal headroom (MW) | 0.36414 | 0.35529 | 0.36822 | 0.32017 | 0.25036 | 0.12821 | -0.050978 | -0.28464 | -0.55059 | -0.87106 | -1.2476 | -2.0534 | -2.5762 | -3.1341 | -3.7049 | -4.3353 | -6.9216 | -7.7087 | -7.9379
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | WPD Best View | Thermal headroom (MW) | 0.34496 | 0.27791 | 0.22492 | 0.093726 | -0.065976 | -0.29103 | -0.57668 | -0.90718 | -1.3 | -1.7045 | -2.1105 | -2.8802 | -3.3872 | -3.8292 | -4.2351 | -4.5709 | -5.9685 | -6.4504 | -6.3663
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Consumer Transformation | Thermal headroom (MW) | 8.1372 | 7.9129 | 7.7045 | 7.4527 | 7.1809 | 6.8894 | 6.4991 | 6.1297 | 5.7435 | 4.9821 | 4.595 | 4.2283 | 3.9119 | 3.5654 | 3.2717 | 3.0414 | 1.5707 | 0.72505 | 0.85991
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Leading the Way | Thermal headroom (MW) | 8.1165 | 7.8832 | 7.7228 | 7.4958 | 7.2347 | 6.9485 | 6.558 | 6.2045 | 5.4476 | 5.0141 | 4.6518 | 4.3348 | 4.0377 | 3.7888 | 3.6646 | 3.2176 | 2.2381 | 2.3033 | 2.5576
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Steady Progression | Thermal headroom (MW) | 8.2094 | 8.2219 | 8.2928 | 8.2772 | 8.27 | 8.2486 | 8.2096 | 8.1405 | 8.0553 | 7.9348 | 7.8048 | 7.6139 | 7.3817 | 7.1319 | 6.8562 | 6.2149 | 4.5454 | 2.9476 | 2.4659
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | System Transformation | Thermal headroom (MW) | 8.167 | 8.1389 | 8.1543 | 8.1114 | 8.0674 | 8.0016 | 7.8514 | 7.6753 | 7.4801 | 7.2379 | 6.9871 | 6.287 | 5.9157 | 5.5144 | 5.114 | 4.7279 | 2.791 | 1.9496 | 1.7043
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | WPD Best View | Thermal headroom (MW) | 8.1669 | 8.1409 | 8.1573 | 8.1189 | 8.0772 | 8.018 | 7.874 | 7.7056 | 7.5237 | 7.2977 | 7.0638 | 6.3874 | 6.0429 | 5.6664 | 5.2866 | 4.9161 | 2.9534 | 1.9267 | 1.6065
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Consumer Transformation | Thermal headroom (MW) | 2.2734 | 1.9798 | 1.6995 | 1.3694 | 1.0018 | 0.63438 | 0.20698 | -0.19032 | -0.621 | -1.4102 | -1.8328 | -2.1824 | -2.4674 | -2.7648 | -3.0326 | -3.2499 | -4.5357 | -5.0819 | -4.7048
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Leading the Way | Thermal headroom (MW) | 2.2478 | 1.9656 | 1.7408 | 1.4377 | 1.1142 | 0.72113 | 0.28145 | -0.10037 | -0.89762 | -1.3545 | -1.7657 | -2.0705 | -2.3496 | -2.5984 | -2.7325 | -3.2153 | -4.0539 | -3.6527 | -3.3181
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Steady Progression | Thermal headroom (MW) | 2.3796 | 2.4134 | 2.51 | 2.5138 | 2.5206 | 2.5012 | 2.451 | 2.3868 | 2.3032 | 2.1859 | 2.046 | 1.8195 | 1.5584 | 1.2675 | 0.96577 | 0.2831 | -1.5431 | -3.3474 | -3.9129
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | System Transformation | Thermal headroom (MW) | 2.3143 | 2.2924 | 2.318 | 2.2685 | 2.2108 | 2.1082 | 1.9127 | 1.6948 | 1.4439 | 1.1533 | 0.83851 | 0.085951 | -0.37079 | -0.83517 | -1.3002 | -1.7448 | -3.7939 | -4.6396 | -4.7831
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | WPD Best View | Thermal headroom (MW) | 2.3143 | 2.2924 | 2.318 | 2.2685 | 2.2108 | 2.1082 | 1.9127 | 1.6948 | 1.4439 | 1.1533 | 0.83851 | 0.085951 | -0.37079 | -0.83517 | -1.3002 | -1.7448 | -3.7939 | -4.6396 | -4.7831
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Consumer Transformation | Thermal headroom (MW) | 1.9807 | 1.6317 | 1.1114 | 0.69037 | 0.2066 | -0.33584 | -1.0074 | -1.677 | -2.3938 | -3.4775 | -4.1917 | -4.8437 | -5.561 | -6.2008 | -6.742 | -7.1678 | -9.7482 | -11.0325 | -10.8351
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Leading the Way | Thermal headroom (MW) | 1.9402 | 1.4281 | 1.167 | 0.7592 | 0.30871 | -0.21526 | -0.8899 | -1.5579 | -2.6497 | -3.4395 | -4.1449 | -4.7941 | -5.4335 | -5.8974 | -6.1894 | -6.8416 | -8.7171 | -8.5276 | -7.7168
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Steady Progression | Thermal headroom (MW) | 2.107 | 2.1321 | 2.2303 | 2.0265 | 1.9931 | 1.9303 | 1.8181 | 1.6566 | 1.4668 | 1.227 | 0.94671 | 0.5482 | 0.092998 | -0.40448 | -0.96684 | -1.9017 | -5.3082 | -7.9892 | -8.8587
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | System Transformation | Thermal headroom (MW) | 2.0373 | 2.0028 | 1.8478 | 1.7667 | 1.6655 | 1.4912 | 1.2099 | 0.88423 | 0.48135 | 0.01331 | -0.50942 | -1.5165 | -2.2681 | -3.0566 | -3.8756 | -4.6838 | -8.2442 | -9.4869 | -9.6562
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | WPD Best View | Thermal headroom (MW) | 1.9861 | 1.7642 | 1.4428 | 1.1742 | 0.87443 | 0.48409 | 0.019053 | -0.44702 | -0.99435 | -1.59 | -2.1672 | -3.0434 | -3.6015 | -4.1717 | -4.6764 | -5.0835 | -6.6573 | -7.4201 | -7.1657
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Consumer Transformation | Thermal headroom (MW) | 49.8654 | 48.7897 | 48.1612 | 47.1494 | 46.0008 | 44.7193 | 42.3872 | 40.1962 | 37.5743 | 33.4321 | 30.3362 | 26.4023 | 22.1925 | 18.0934 | 14.0059 | 9.9883 | -7.9653 | -14.5479 | -14.0835
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Leading the Way | Thermal headroom (MW) | 49.7797 | 48.7515 | 48.2749 | 47.2981 | 46.246 | 44.9778 | 42.6089 | 40.4296 | 36.7859 | 33.366 | 29.9667 | 26.4147 | 23.0235 | 19.1848 | 15.672 | 11.4168 | 0.48376 | -0.88629 | 2.9124
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Steady Progression | Thermal headroom (MW) | 50.0887 | 50.2288 | 50.726 | 50.7709 | 50.8078 | 50.8168 | 50.7562 | 50.619 | 50.1533 | 49.5905 | 48.9302 | 47.9067 | 46.8162 | 45.3242 | 43.8518 | 41.3259 | 31.0952 | 22.396 | 19.7069
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | System Transformation | Thermal headroom (MW) | 49.9527 | 49.9725 | 50.3255 | 50.2714 | 50.0735 | 49.7036 | 49.3559 | 48.9178 | 48.263 | 47.028 | 45.72 | 43.1622 | 41.3322 | 38.9363 | 36.4419 | 33.945 | 22.1696 | 15.132 | 14.7471
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | WPD Best View | Thermal headroom (MW) | 49.9526 | 49.9737 | 50.3269 | 50.2748 | 50.0794 | 49.7136 | 49.3696 | 48.9362 | 48.2896 | 47.0645 | 45.7668 | 43.2235 | 41.4098 | 39.0291 | 36.5472 | 34.0599 | 22.2684 | 15.1177 | 14.6869
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Consumer Transformation | Thermal headroom (MW) | 1.9593 | 1.678 | 1.4522 | 1.1531 | 0.80773 | 0.42335 | -0.33719 | -1.0038 | -1.8934 | -3.3064 | -4.4218 | -5.8586 | -7.3437 | -8.7703 | -10.2569 | -11.716 | -18.0683 | -20.2126 | -19.8204
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Leading the Way | Thermal headroom (MW) | 1.9398 | 1.657 | 1.4819 | 1.1977 | 0.8956 | 0.52093 | -0.26261 | -0.93501 | -2.1826 | -3.27 | -4.5176 | -5.784 | -7.0501 | -8.3145 | -9.5311 | -11.0245 | -15.0574 | -15.4398 | -14.4451
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Steady Progression | Thermal headroom (MW) | 2.018 | 2.0497 | 2.174 | 2.1597 | 2.1688 | 2.15 | 2.1626 | 2.1235 | 2.0776 | 1.9005 | 1.6178 | 1.2066 | 0.76607 | 0.26628 | -0.28306 | -1.2222 | -4.6444 | -6.9579 | -7.7808
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | System Transformation | Thermal headroom (MW) | 1.9646 | 1.9743 | 2.0403 | 2.0268 | 1.9611 | 1.91 | 1.8189 | 1.7086 | 1.5066 | 1.0976 | 0.59517 | -0.38047 | -1.0538 | -1.792 | -2.5452 | -3.285 | -6.812 | -9.2582 | -9.535
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | WPD Best View | Thermal headroom (MW) | 1.9646 | 1.9743 | 2.0403 | 2.0268 | 1.9611 | 1.91 | 1.8189 | 1.7086 | 1.5066 | 1.0976 | 0.59517 | -0.38047 | -1.0538 | -1.792 | -2.5452 | -3.285 | -6.812 | -9.2582 | -9.535
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Consumer Transformation | Thermal headroom (MW) | 5.0472 | 4.7112 | 4.4616 | 4.031 | 3.5758 | 2.9627 | 1.8945 | 0.82706 | -0.37199 | -2.4004 | -3.9055 | -5.8519 | -7.9002 | -10.2745 | -12.3606 | -14.3899 | -22.3146 | -25.3279 | -25.2363
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Leading the Way | Thermal headroom (MW) | 5.0227 | 4.7459 | 4.5642 | 4.1651 | 3.7596 | 3.1291 | 2.0489 | 0.95949 | -0.67004 | -2.5708 | -4.2946 | -6.019 | -7.9507 | -10.3474 | -12.2033 | -14.138 | -18.9011 | -19.4893 | -17.4027
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Steady Progression | Thermal headroom (MW) | 5.1278 | 5.2171 | 5.4623 | 5.5247 | 5.5777 | 5.6017 | 5.5118 | 5.4532 | 5.2861 | 4.968 | 4.7441 | 4.3507 | 3.9394 | 3.1599 | 2.5377 | 1.4901 | -3.3805 | -8.6984 | -10.1384
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | System Transformation | Thermal headroom (MW) | 5.1042 | 5.1375 | 5.3392 | 5.3449 | 5.2949 | 5.2337 | 5.0261 | 4.806 | 4.521 | 3.8839 | 3.3445 | 2.362 | 1.5829 | 0.2319 | -0.91484 | -2.1162 | -8.714 | -12.2925 | -12.4062
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | WPD Best View | Thermal headroom (MW) | 5.1042 | 5.1375 | 5.3392 | 5.3449 | 5.2949 | 5.2337 | 5.0261 | 4.806 | 4.521 | 3.8839 | 3.3445 | 2.362 | 1.5829 | 0.2319 | -0.91484 | -2.1162 | -8.714 | -12.2925 | -12.4062
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Consumer Transformation | Thermal headroom (MW) | 35.3406 | 32.8301 | 31.0544 | 28.5116 | 24.7225 | 20.9273 | 16.5803 | 12.4946 | 8.1467 | 2.9539 | -1.345 | -6.8465 | -12.4068 | -17.483 | -22.9726 | -27.3609 | -50.9899 | -60.4108 | -60.8165
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Leading the Way | Thermal headroom (MW) | 34.8718 | 31.9402 | 30.1218 | 26.8607 | 22.8678 | 18.9119 | 14.5798 | 10.6185 | 5.488 | 1.1388 | -2.7084 | -7.205 | -11.0205 | -14.978 | -18.3787 | -22.5242 | -38.896 | -41.6721 | -34.9345
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Steady Progression | Thermal headroom (MW) | 35.9798 | 35.5062 | 35.7497 | 34.9601 | 33.6819 | 32.8936 | 32.4843 | 31.8603 | 30.8826 | 29.9448 | 28.8904 | 27.0453 | 25.4454 | 23.4387 | 21.3544 | 18.1806 | 4.6059 | -7.9358 | -11.8784
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | System Transformation | Thermal headroom (MW) | 35.5184 | 34.5736 | 34.2254 | 33.0326 | 31.1067 | 29.5252 | 28.6231 | 27.5481 | 25.7272 | 24.0389 | 22.1592 | 18.9561 | 16.3932 | 13.0845 | 9.6453 | 6.3421 | -10.3031 | -18.8349 | -18.7841
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | WPD Best View | Thermal headroom (MW) | 34.9184 | 32.0269 | 30.2027 | 26.9762 | 23.011 | 19.1328 | 14.9828 | 11.1573 | 6.1969 | 2.0796 | -1.8704 | -6.599 | -10.6469 | -14.9138 | -18.9193 | -23.0786 | -39.8416 | -45.4016 | -41.3651
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Consumer Transformation | Thermal headroom (MW) | 4.8916 | 4.7842 | 4.6917 | 4.5515 | 4.3933 | 4.186 | 3.8884 | 3.5839 | 3.2762 | 2.9657 | 2.6638 | 2.326 | 2.0279 | 1.7146 | 1.4538 | 1.2357 | -0.072132 | -0.75443 | -0.88018
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Leading the Way | Thermal headroom (MW) | 4.8838 | 4.7865 | 4.7066 | 4.5717 | 4.4252 | 4.2268 | 3.9227 | 3.616 | 3.3016 | 2.9753 | 2.6785 | 2.4215 | 2.1572 | 1.946 | 1.8309 | 1.7235 | 0.67684 | 0.45697 | 0.96578
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Steady Progression | Thermal headroom (MW) | 4.9254 | 4.9369 | 4.9806 | 4.9853 | 4.9751 | 4.9495 | 4.9088 | 4.8417 | 4.7802 | 4.6827 | 4.5701 | 4.4228 | 4.2518 | 4.054 | 3.851 | 3.618 | 2.295 | 1.3278 | 1.027
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | System Transformation | Thermal headroom (MW) | 4.9096 | 4.9053 | 4.9328 | 4.9144 | 4.8875 | 4.8172 | 4.7393 | 4.6281 | 4.4977 | 4.3265 | 4.1425 | 3.9 | 3.6253 | 3.3328 | 3.0167 | 2.7274 | 1.4365 | 1.0309 | 1.0617
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | WPD Best View | Thermal headroom (MW) | 4.8916 | 4.7851 | 4.6943 | 4.551 | 4.3923 | 4.1834 | 3.8854 | 3.5754 | 3.2644 | 2.9485 | 2.6488 | 2.3217 | 2.0169 | 1.7226 | 1.4866 | 1.2966 | -0.059277 | -0.66261 | -0.7165
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Consumer Transformation | Thermal headroom (MW) | 5.6996 | 5.593 | 5.6514 | 5.569 | 4.6186 | 4.4191 | 4.156 | 3.9273 | 3.6111 | 3.2922 | 2.9735 | 2.6004 | 1.9525 | 1.1652 | 0.31826 | -0.63637 | -4.1669 | -5.331 | -5.4721
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Leading the Way | Thermal headroom (MW) | 5.6659 | 5.5541 | 5.6473 | 5.5964 | 4.3488 | 4.1247 | 3.8671 | 3.6473 | 3.363 | 2.9661 | 2.6642 | 2.3174 | 1.5423 | 0.79196 | 0.045393 | -0.71528 | -3.0248 | -3.2723 | -1.8316
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Steady Progression | Thermal headroom (MW) | 5.7653 | 5.8672 | 6.1404 | 6.2715 | 5.7529 | 5.806 | 5.9026 | 5.9287 | 5.9645 | 5.9661 | 5.9821 | 5.9341 | 5.8732 | 5.7872 | 5.6892 | 5.5256 | 4.2942 | 1.8287 | 1.0826
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | System Transformation | Thermal headroom (MW) | 5.7178 | 5.7887 | 6.0381 | 6.1264 | 5.3561 | 5.3664 | 5.3831 | 5.4283 | 5.3419 | 5.2422 | 5.1602 | 5.0147 | 4.8776 | 4.7083 | 4.4672 | 4.1347 | 1.5194 | 0.067874 | 0.27824
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | WPD Best View | Thermal headroom (MW) | 5.6659 | 5.5541 | 5.6473 | 5.5964 | 4.3488 | 4.1247 | 3.8671 | 3.6473 | 3.363 | 2.9661 | 2.6642 | 2.3174 | 1.5423 | 0.79196 | 0.045393 | -0.71528 | -3.0248 | -3.2723 | -1.8316
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Consumer Transformation | Thermal headroom (MW) | 10.4915 | 9.8193 | 9.2125 | 8.535 | 7.489 | 6.6842 | 5.8131 | 4.997 | 4.1634 | 3.3938 | 2.6651 | 1.2541 | -0.046275 | -1.211 | -2.8006 | -3.9526 | -8.8153 | -10.6273 | -10.5839
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Leading the Way | Thermal headroom (MW) | 10.3432 | 9.5151 | 8.8291 | 7.6748 | 6.8755 | 6.0759 | 5.2246 | 4.4612 | 3.7091 | 2.9992 | 2.4103 | 1.1646 | 0.24266 | -0.71408 | -2.0014 | -2.8514 | -5.6993 | -6.5627 | -5.0629
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Steady Progression | Thermal headroom (MW) | 10.6554 | 10.3629 | 10.1995 | 9.8937 | 9.5938 | 9.4158 | 9.2778 | 9.1051 | 8.9494 | 8.7736 | 8.5913 | 7.9962 | 7.7131 | 7.381 | 7.0439 | 6.6768 | 4.5684 | 1.7519 | 0.76413
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | System Transformation | Thermal headroom (MW) | 10.5227 | 10.0824 | 9.7535 | 9.337 | 8.9288 | 8.6849 | 8.4718 | 8.2295 | 7.5896 | 7.3294 | 7.0394 | 6.6423 | 6.2027 | 5.4034 | 4.9454 | 4.5198 | 1.2515 | -1.1373 | -1.3121
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | WPD Best View | Thermal headroom (MW) | 10.3483 | 9.5434 | 8.8678 | 7.7108 | 6.9243 | 6.1427 | 5.3106 | 4.5717 | 3.8603 | 3.2425 | 2.5223 | 1.3054 | 0.41662 | -0.50588 | -1.7626 | -2.5827 | -5.4577 | -6.4938 | -5.0822
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Consumer Transformation | Thermal headroom (MW) | 4.4597 | 3.9954 | 3.6384 | 3.1541 | 2.6121 | 1.494 | 0.0991 | -1.2204 | -2.5258 | -4.2059 | -5.5001 | -6.9222 | -8.0781 | -9.3039 | -10.351 | -11.1173 | -18.0133 | -20.597 | -20.3173
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Leading the Way | Thermal headroom (MW) | 4.3348 | 3.7459 | 3.4382 | 2.8872 | 2.3057 | 1.1665 | -0.21132 | -1.5 | -3.1871 | -4.4975 | -5.6209 | -6.5379 | -7.1273 | -7.8348 | -8.4494 | -9.7508 | -16.8048 | -16.7931 | -15.1506
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Steady Progression | Thermal headroom (MW) | 4.605 | 4.4815 | 4.5531 | 4.3831 | 4.2549 | 4.0344 | 3.8599 | 3.6551 | 3.4037 | 3.0479 | 2.611 | 2.0952 | 1.5673 | 0.78227 | -0.10454 | -1.3581 | -5.9457 | -8.0978 | -8.9503
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | System Transformation | Thermal headroom (MW) | 4.5054 | 4.2788 | 4.2212 | 4.0115 | 3.7962 | 3.4564 | 3.1428 | 2.7805 | 2.321 | 1.7461 | 1.0881 | -0.054346 | -0.86418 | -2.0057 | -3.2018 | -4.2937 | -9.1184 | -10.7826 | -10.7784
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | WPD Best View | Thermal headroom (MW) | 4.3557 | 3.8025 | 3.5394 | 3.0682 | 2.554 | 1.5198 | 0.34285 | -0.79174 | -2.3211 | -3.4971 | -4.5528 | -5.4845 | -6.1753 | -6.9511 | -7.6413 | -8.5455 | -14.8241 | -16.8015 | -16.5663
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Consumer Transformation | Thermal headroom (MW) | 8.391 | 7.5608 | 7.1702 | 6.3853 | 5.4525 | 4.3556 | 3.6094 | 2.8838 | 2.0166 | 0.73908 | -0.2375 | -1.3292 | -2.7719 | -3.6829 | -4.9394 | -5.8193 | -9.9479 | -11.4405 | -11.4855
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Leading the Way | Thermal headroom (MW) | 8.2556 | 7.3162 | 6.7939 | 5.7999 | 4.578 | 3.2997 | 2.5321 | 1.811 | 0.54942 | -0.37482 | -1.2469 | -2.4236 | -3.2216 | -4.2705 | -4.8726 | -5.7338 | -7.557 | -7.9 | -6.8442
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Steady Progression | Thermal headroom (MW) | 8.5457 | 8.3744 | 8.331 | 7.9085 | 7.4 | 6.9407 | 6.8498 | 6.7146 | 6.218 | 6.0118 | 5.8017 | 5.5611 | 5.328 | 5.0319 | 4.7935 | 4.1396 | 1.6979 | -0.9565 | -1.6581
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | System Transformation | Thermal headroom (MW) | 8.4255 | 8.133 | 7.9357 | 7.3263 | 6.606 | 5.65 | 5.4778 | 5.2674 | 4.9798 | 4.6483 | 4.2975 | 3.5855 | 3.1977 | 2.8067 | 2.0223 | 1.2391 | -2.0572 | -4.0713 | -4.0003
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | WPD Best View | Thermal headroom (MW) | 8.2556 | 7.3162 | 6.7939 | 5.7999 | 4.578 | 3.2997 | 2.5321 | 1.811 | 0.54942 | -0.37482 | -1.2469 | -2.4236 | -3.2216 | -4.2705 | -4.8726 | -5.7338 | -7.557 | -7.9 | -6.8442
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Consumer Transformation | Thermal headroom (MW) | 5.52 | 5.0872 | 4.6814 | 4.2662 | 3.8932 | 3.3273 | 2.3318 | 1.497 | 0.59698 | -0.65117 | -1.5327 | -2.5838 | -3.5594 | -4.4794 | -5.2013 | -5.8594 | -10.6171 | -12.7313 | -12.9696
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Leading the Way | Thermal headroom (MW) | 5.456 | 4.9111 | 4.5996 | 4.1894 | 3.8353 | 3.2843 | 2.3065 | 1.5248 | 0.3004 | -0.5614 | -1.3687 | -2.0023 | -2.5193 | -2.9641 | -3.1582 | -4.0234 | -6.8368 | -7.8649 | -7.1219
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Steady Progression | Thermal headroom (MW) | 5.6234 | 5.6027 | 5.7252 | 5.6488 | 5.6806 | 5.6963 | 5.6727 | 5.6583 | 5.606 | 5.5376 | 5.4434 | 5.1916 | 4.9101 | 4.5973 | 4.2441 | 3.5091 | 1.641 | 0.13077 | -0.23131
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | System Transformation | Thermal headroom (MW) | 5.5453 | 5.4435 | 5.4089 | 5.3457 | 5.3236 | 5.2975 | 5.167 | 5.0274 | 4.8571 | 4.6296 | 4.3192 | 3.5693 | 3.1244 | 2.621 | 2.1349 | 1.6819 | -0.045501 | -1.0393 | -1.1259
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | WPD Best View | Thermal headroom (MW) | 5.4638 | 4.9363 | 4.5977 | 4.1908 | 3.8334 | 3.2962 | 2.3212 | 1.55 | 0.33117 | -0.51899 | -1.3267 | -2.0548 | -2.6937 | -3.2482 | -3.8028 | -4.8219 | -7.784 | -9.0551 | -8.5003
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Consumer Transformation | Thermal headroom (MW) | 80.2932 | 79.8051 | 79.5276 | 79.0611 | 78.4791 | 77.5914 | 75.7767 | 74.0169 | 71.5722 | 69.3353 | 67.1019 | 64.8498 | 62.4378 | 60.2507 | 57.9405 | 55.0163 | 43.4924 | 39.4364 | 39.7872
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Leading the Way | Thermal headroom (MW) | 80.2445 | 79.7119 | 79.529 | 79.059 | 78.4952 | 77.6243 | 75.5673 | 73.5321 | 70.4476 | 67.8649 | 65.2572 | 62.8936 | 60.6857 | 58.5406 | 56.0321 | 52.3735 | 43.1917 | 43.7511 | 47.8723
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Steady Progression | Thermal headroom (MW) | 80.4649 | 80.6049 | 81.0063 | 81.1137 | 81.1847 | 81.246 | 80.8931 | 80.52 | 79.5708 | 78.9878 | 78.207 | 77.3644 | 76.4196 | 75.3423 | 74.1314 | 72.2825 | 63.6052 | 56.8428 | 54.1558
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | System Transformation | Thermal headroom (MW) | 80.3807 | 80.4363 | 80.6885 | 80.73 | 80.7081 | 80.4965 | 79.7175 | 78.8783 | 77.4481 | 76.3478 | 75.0038 | 73.4035 | 71.7534 | 69.9196 | 67.8742 | 65.0517 | 53.913 | 49.3716 | 49.7172
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | WPD Best View | Thermal headroom (MW) | 80.3877 | 80.4488 | 80.71 | 80.7642 | 80.7564 | 80.563 | 79.8136 | 79.0066 | 77.6223 | 76.5796 | 75.3019 | 73.7707 | 72.1888 | 70.4401 | 68.4715 | 65.6807 | 54.4925 | 49.8493 | 49.9432
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Consumer Transformation | Thermal headroom (MW) | 3.5409 | 3.2961 | 3.0238 | 2.7413 | 2.3971 | 1.7034 | 0.37201 | -0.87332 | -2.8426 | -4.4134 | -6.1631 | -7.8633 | -9.6737 | -11.4115 | -13.1872 | -15.4832 | -25.1235 | -26.8782 | -26.0513
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Leading the Way | Thermal headroom (MW) | 3.5162 | 3.2145 | 3.0128 | 2.7392 | 2.4124 | 1.7308 | 0.21897 | -1.2472 | -3.6449 | -5.5904 | -7.6595 | -9.4105 | -11.1779 | -12.8729 | -14.5045 | -16.7976 | -25.3387 | -24.2944 | -21.2598
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Steady Progression | Thermal headroom (MW) | 3.6512 | 3.7219 | 3.9207 | 3.9766 | 4.0279 | 4.0586 | 3.7939 | 3.5569 | 2.8556 | 2.4705 | 1.9136 | 1.3785 | 0.78214 | 0.083153 | -0.71484 | -1.9344 | -9.4163 | -14.3418 | -16.1141
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | System Transformation | Thermal headroom (MW) | 3.5981 | 3.6147 | 3.6774 | 3.7173 | 3.7216 | 3.6617 | 3.0832 | 2.509 | 1.3312 | 0.60614 | -0.33108 | -1.2772 | -2.363 | -3.5951 | -4.8756 | -6.8889 | -17.1831 | -20.1404 | -19.4843
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | WPD Best View | Thermal headroom (MW) | 3.5981 | 3.6147 | 3.6774 | 3.7173 | 3.7216 | 3.6617 | 3.0832 | 2.509 | 1.3312 | 0.60614 | -0.33108 | -1.2772 | -2.363 | -3.5951 | -4.8756 | -6.8889 | -17.1831 | -20.1404 | -19.4843
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Consumer Transformation | Thermal headroom (MW) | 13.3661 | 13.3816 | 13.4393 | 13.3999 | 13.3319 | 13.2309 | 12.8563 | 12.4452 | 11.9969 | 11.5432 | 11.081 | 10.6095 | 10.1627 | 9.6917 | 9.215 | 8.5567 | 7.5743 | 5.7589 | 5.4234
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Leading the Way | Thermal headroom (MW) | 13.3652 | 13.3834 | 13.4547 | 13.4086 | 13.3423 | 13.2381 | 12.7631 | 12.2285 | 11.6388 | 11.0099 | 10.409 | 9.8665 | 9.2842 | 8.7683 | 7.8855 | 6.5779 | 6.0243 | 5.9415 | 6.9954
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Steady Progression | Thermal headroom (MW) | 13.391 | 13.4592 | 13.6143 | 13.6708 | 13.7129 | 13.742 | 13.6052 | 13.4427 | 13.2525 | 13.031 | 12.7783 | 12.482 | 12.1405 | 11.7789 | 11.39 | 10.851 | 9.8269 | 8.1367 | 7.1916
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | System Transformation | Thermal headroom (MW) | 13.3832 | 13.4438 | 13.5885 | 13.6267 | 13.6521 | 13.6567 | 13.3882 | 13.0875 | 12.7427 | 12.3583 | 11.9254 | 11.4263 | 10.8754 | 10.2885 | 9.6805 | 8.8912 | 7.8866 | 6.435 | 6.1383
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | WPD Best View | Thermal headroom (MW) | 13.3912 | 13.4571 | 13.6121 | 13.6633 | 13.7031 | 13.7256 | 13.4882 | 13.2211 | 12.9228 | 12.5973 | 12.2327 | 11.8022 | 11.3175 | 10.817 | 10.288 | 9.5279 | 8.4783 | 6.9928 | 6.4412
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Consumer Transformation | Thermal headroom (MW) | 1.8527 | 1.1083 | 0.87039 | 0.38785 | -0.19014 | -0.70391 | -1.57 | -2.4041 | -3.3074 | -4.5492 | -5.3658 | -6.3196 | -7.4948 | -8.1993 | -9.123 | -10.0621 | -16.0607 | -18.513 | -18.6948
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Leading the Way | Thermal headroom (MW) | 1.7846 | 1.046 | 0.86405 | 0.36774 | -0.20613 | -0.6965 | -1.5593 | -2.3341 | -3.6126 | -4.5184 | -5.2768 | -6.2451 | -6.688 | -7.2794 | -8.1219 | -9.4979 | -12.8831 | -13.5774 | -12.0905
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Steady Progression | Thermal headroom (MW) | 1.993 | 2.0429 | 2.285 | 2.3099 | 2.2841 | 2.308 | 2.2958 | 2.2279 | 1.773 | 1.6267 | 1.4239 | 1.1115 | 0.77384 | 0.36922 | -0.098086 | -0.93156 | -4.3172 | -6.9644 | -7.8136
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | System Transformation | Thermal headroom (MW) | 1.9124 | 1.8825 | 2.0666 | 1.999 | 1.8764 | 1.4556 | 1.3406 | 1.1336 | 0.84734 | 0.49209 | 0.090737 | -0.8005 | -1.3936 | -2.0535 | -3.1018 | -4.1133 | -7.6233 | -9.4695 | -9.3727
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | WPD Best View | Thermal headroom (MW) | 1.9123 | 1.8845 | 2.0688 | 2.0046 | 1.8861 | 1.472 | 1.3631 | 1.1639 | 0.89098 | 0.55184 | 0.1674 | -0.70001 | -1.2665 | -1.9014 | -2.9293 | -3.9251 | -7.4614 | -9.4929 | -9.4713
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Consumer Transformation | Thermal headroom (MW) | 43.443 | 41.7169 | 39.8998 | 37.325 | 34.9563 | 31.2454 | 26.1266 | 20.8661 | 15.7602 | 10.4596 | 5.3412 | -0.091501 | -5.9569 | -10.9734 | -16.3283 | -22.1053 | -47.0401 | -53.1143 | -50.4587
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Leading the Way | Thermal headroom (MW) | 43.1725 | 41.0703 | 39.2221 | 36.345 | 33.7019 | 29.7759 | 23.8413 | 18.2108 | 12.0494 | 6.0766 | 0.67478 | -4.3909 | -8.7943 | -13.3461 | -18.0218 | -22.7235 | -40.1794 | -39.4577 | -32.312
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Steady Progression | Thermal headroom (MW) | 43.9512 | 43.8559 | 44.0773 | 43.2454 | 42.6057 | 41.935 | 40.8755 | 39.6114 | 38.1969 | 36.6808 | 34.9817 | 32.945 | 30.7508 | 28.0485 | 25.491 | 22.2879 | 6.1674 | -5.5471 | -9.7274
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | System Transformation | Thermal headroom (MW) | 43.5943 | 43.1192 | 42.6307 | 41.3547 | 40.2958 | 38.9818 | 36.8384 | 34.3743 | 31.6776 | 28.9029 | 25.7414 | 22.075 | 18.2261 | 14.463 | 10.3126 | 6.0195 | -13.2468 | -19.6204 | -18.301
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | WPD Best View | Thermal headroom (MW) | 43.8593 | 43.6891 | 43.7426 | 42.8307 | 42.1843 | 41.3226 | 39.5866 | 37.634 | 35.445 | 33.2185 | 30.8 | 27.878 | 24.7969 | 21.1851 | 17.6427 | 13.5623 | -2.8863 | -11.9204 | -12.3366
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Consumer Transformation | Thermal headroom (MW) | 3.6997 | 3.1729 | 2.8018 | 2.2329 | 1.6691 | 0.80596 | -0.41512 | -1.5784 | -2.7767 | -4.3421 | -5.4261 | -6.5795 | -7.5975 | -8.4438 | -9.2004 | -10.0106 | -14.5741 | -16.5219 | -16.2943
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Leading the Way | Thermal headroom (MW) | 3.619 | 3.0555 | 2.7194 | 2.1304 | 1.5817 | 0.7447 | -0.49238 | -1.6072 | -3.185 | -4.4313 | -5.4096 | -6.1055 | -6.6225 | -7.0794 | -7.3892 | -8.2709 | -11.2456 | -11.7324 | -10.6674
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Steady Progression | Thermal headroom (MW) | 3.8512 | 3.7945 | 3.9285 | 3.8429 | 3.7806 | 3.6875 | 3.5728 | 3.4439 | 3.2133 | 2.9097 | 2.5745 | 2.1551 | 1.6692 | 1.1252 | 0.56172 | -0.47466 | -3.5475 | -5.9819 | -6.6338
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | System Transformation | Thermal headroom (MW) | 3.7506 | 3.6044 | 3.6537 | 3.4621 | 3.3181 | 3.1389 | 2.8877 | 2.5461 | 2.0842 | 1.5456 | 0.97192 | -0.059296 | -0.80281 | -1.5923 | -2.3721 | -3.1962 | -6.3759 | -7.5823 | -7.5768
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | WPD Best View | Thermal headroom (MW) | 3.8348 | 3.7678 | 3.8858 | 3.7797 | 3.6935 | 3.5717 | 3.4117 | 3.2122 | 2.8828 | 2.4929 | 2.0495 | 1.507 | 0.90512 | 0.23392 | -0.44138 | -1.5462 | -4.5351 | -6.3591 | -6.6225
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Consumer Transformation | Thermal headroom (MW) | 4.1915 | 3.3713 | 2.446 | 1.6614 | 0.83929 | -0.46222 | -1.9734 | -3.3887 | -4.6974 | -5.7611 | -6.7239 | -8.1349 | -9.7858 | -11.1742 | -12.6354 | -14.1084 | -19.2404 | -20.2264 | -19.4617
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Leading the Way | Thermal headroom (MW) | 4.082 | 2.9775 | 2.0711 | 1.1867 | 0.25297 | -1.1542 | -2.7284 | -4.2412 | -5.6364 | -6.6742 | -7.7406 | -8.7659 | -9.6918 | -10.5889 | -11.4474 | -12.3039 | -14.6756 | -14.8587 | -13.2456
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Steady Progression | Thermal headroom (MW) | 4.3406 | 4.0667 | 3.8783 | 3.4835 | 3.1948 | 2.8263 | 2.5395 | 2.1802 | 1.8349 | 1.6056 | 1.3723 | 1.0531 | 0.72512 | 0.36786 | -0.04145 | -0.53988 | -3.0076 | -4.3563 | -4.4299
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | System Transformation | Thermal headroom (MW) | 4.2234 | 3.7835 | 3.255 | 2.843 | 2.4029 | 1.8484 | 1.3076 | 0.67821 | 0.085092 | -0.3265 | -0.70685 | -1.1724 | -1.6687 | -2.2227 | -2.7409 | -3.3488 | -5.1782 | -5.9147 | -5.4108
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | WPD Best View | Thermal headroom (MW) | 4.3406 | 4.0667 | 3.8783 | 3.4835 | 3.1948 | 2.8263 | 2.5395 | 2.1802 | 1.8349 | 1.6056 | 1.3723 | 1.0531 | 0.72512 | 0.36786 | -0.04145 | -0.53988 | -3.0076 | -4.3563 | -4.4299
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Consumer Transformation | Thermal headroom (MW) | 1.823 | 1.4434 | 1.2074 | 0.83151 | 0.43489 | -0.11076 | -0.89324 | -1.9888 | -2.7487 | -3.5123 | -4.6327 | -5.4548 | -6.5547 | -7.2009 | -8.0583 | -9.5443 | -14.8885 | -17.0329 | -17.6341
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Leading the Way | Thermal headroom (MW) | 1.784 | 1.3996 | 1.224 | 0.86437 | 0.49421 | -0.046484 | -1.1713 | -1.8812 | -2.6378 | -3.7686 | -4.4997 | -5.4009 | -5.8217 | -6.475 | -7.6648 | -8.5262 | -11.8794 | -12.9814 | -11.545
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Steady Progression | Thermal headroom (MW) | 1.9539 | 2.0111 | 2.2476 | 2.3064 | 2.3597 | 2.4005 | 2.3957 | 2.3953 | 2.3723 | 2.3232 | 2.1779 | 1.9094 | 1.6268 | 0.91727 | 0.55075 | 0.14524 | -3.2649 | -6.2737 | -7.3075
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | System Transformation | Thermal headroom (MW) | 1.8791 | 1.8572 | 2.017 | 2.0204 | 2.0089 | 1.9285 | 1.7869 | 1.6364 | 1.4446 | 1.1531 | 0.43648 | -0.030883 | -0.92463 | -1.488 | -2.4122 | -3.3325 | -7.1278 | -9.1236 | -9.5008
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | WPD Best View | Thermal headroom (MW) | 1.954 | 2.0091 | 2.2454 | 2.3008 | 2.3525 | 2.3884 | 2.379 | 2.373 | 2.3401 | 2.2634 | 2.1012 | 1.8089 | 1.4997 | 0.7652 | 0.37819 | -0.042943 | -3.3429 | -6.2508 | -7.2098
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | 52.3884 | -1.2626 | Consumer Transformation | Thermal headroom (MW) | 10.314 | 10.1139 | 10.1205 | 9.8795 | 9.6498 | 9.1311 | 8.3628 | 7.7112 | 6.9518 | 5.7827 | 5.0345 | 4.1299 | 3.2085 | 2.4187 | 1.5686 | 0.58927 | -2.3782 | -3.16 | -2.387
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | 52.3884 | -1.2626 | Leading the Way | Thermal headroom (MW) | 10.1722 | 9.9456 | 9.9495 | 9.7745 | 9.5391 | 9.0655 | 8.3409 | 7.6738 | 6.5309 | 5.6733 | 4.935 | 4.2869 | 3.6511 | 2.9709 | 2.3224 | 1.2169 | -0.056309 | 0.44944 | 1.9973
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | 52.3884 | -1.2626 | Steady Progression | Thermal headroom (MW) | 10.5185 | 10.6906 | 11.1003 | 11.2596 | 11.365 | 11.4984 | 11.6486 | 11.748 | 11.8302 | 11.8708 | 11.9403 | 11.8721 | 11.7566 | 11.4566 | 11.1399 | 10.3697 | 8.6706 | 7.76 | 7.5975
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | 52.3884 | -1.2626 | System Transformation | Thermal headroom (MW) | 10.3659 | 10.4482 | 10.7939 | 10.8595 | 10.9841 | 11.0834 | 11.1122 | 11.0344 | 11.0269 | 10.9595 | 10.8043 | 10.0804 | 9.6193 | 9.139 | 8.642 | 8.1132 | 6.6654 | 5.4563 | 5.8127
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | 52.3884 | -1.2626 | WPD Best View | Thermal headroom (MW) | 10.5155 | 10.6833 | 11.0889 | 11.2462 | 11.3493 | 11.4754 | 11.6153 | 11.702 | 11.7695 | 11.7946 | 11.7717 | 11.562 | 11.2774 | 10.8868 | 10.4836 | 9.6633 | 8.3256 | 7.3678 | 7.358
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Consumer Transformation | Thermal headroom (MW) | 36.952 | 35.7233 | 33.7921 | 31.6711 | 27.787 | 23.5238 | 17.3981 | 10.244 | 3.2327 | -5.6856 | -14.6519 | -25.5605 | -38.6958 | -49.875 | -61.6994 | -73.3565 | -119.1109 | -136.0941 | -138.0083
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Leading the Way | Thermal headroom (MW) | 36.3285 | 34.4508 | 33.4414 | 30.7814 | 26.7775 | 21.9323 | 15.1825 | 7.2086 | -1.5798 | -10.7597 | -21.5069 | -32.6236 | -46.6405 | -58.5346 | -70.1717 | -81.4858 | -111.2756 | -112.7859 | -96.1806
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Steady Progression | Thermal headroom (MW) | 37.6915 | 37.7487 | 38.3184 | 36.922 | 35.5287 | 34.2532 | 32.8565 | 31.2852 | 30.0783 | 28.6159 | 26.4575 | 22.9364 | 18.2377 | 13.902 | 9.0435 | 2.4847 | -36.1227 | -74.2129 | -85.2692
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | System Transformation | Thermal headroom (MW) | 37.1927 | 37.1268 | 36.6253 | 35.6411 | 33.7213 | 31.6687 | 28.9528 | 26.1076 | 23.9232 | 20.6364 | 16.0672 | 9.8132 | 1.6875 | -5.6522 | -13.8576 | -22.7291 | -73.197 | -96.8794 | -97.3729
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | WPD Best View | Thermal headroom (MW) | 37.0005 | 35.8902 | 34.3054 | 32.0762 | 28.3248 | 24.2209 | 18.345 | 11.3999 | 4.726 | -3.6275 | -12.4706 | -23.0333 | -35.782 | -46.6493 | -58.1276 | -69.6035 | -114.4172 | -131.9846 | -134.1656
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Consumer Transformation | Thermal headroom (MW) | 6.0872 | 5.8699 | 5.8024 | 5.5864 | 4.9464 | 4.6167 | 4.003 | 3.3953 | 2.6502 | 1.5853 | 0.68384 | -1.3458 | -3.1369 | -4.9 | -7.1043 | -8.958 | -17.0532 | -20.765 | -21.5289
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Leading the Way | Thermal headroom (MW) | 6.0705 | 5.8532 | 5.8443 | 5.2845 | 5.0256 | 4.7148 | 4.0982 | 3.5113 | 2.3721 | 1.5942 | 0.23075 | -1.7665 | -3.4689 | -5.2122 | -7.2278 | -9.1771 | -14.1931 | -15.603 | -13.6338
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Steady Progression | Thermal headroom (MW) | 6.1549 | 6.2483 | 6.501 | 6.5992 | 6.666 | 6.6935 | 6.7514 | 6.7735 | 6.7209 | 6.678 | 6.5659 | 5.9593 | 5.6762 | 5.3602 | 4.9796 | 4.2256 | 0.18452 | -5.7052 | -7.4586
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | System Transformation | Thermal headroom (MW) | 6.1194 | 6.1804 | 6.3896 | 6.4374 | 6.4757 | 6.4884 | 6.4417 | 6.3585 | 5.827 | 5.601 | 5.2902 | 4.4985 | 4.0152 | 3.0951 | 2.4896 | 1.7645 | -5.8672 | -10.1929 | -10.9487
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | WPD Best View | Thermal headroom (MW) | 6.1094 | 5.9569 | 5.9539 | 5.805 | 5.2355 | 4.9764 | 4.4896 | 4.023 | 3.4502 | 2.8894 | 1.8614 | -0.06273 | -1.7061 | -3.3249 | -5.3765 | -7.4386 | -14.8853 | -18.7962 | -19.6698
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Consumer Transformation | Thermal headroom (MW) | -0.52789 | -0.7141 | -0.86349 | -1.4474 | -2.3355 | -3.424 | -4.7095 | -5.9427 | -7.0102 | -8.1423 | -9.297 | -10.5201 | -11.5958 | -12.3841 | -13.3558 | -14.6895 | -19.2248 | -20.5084 | -20.156
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Leading the Way | Thermal headroom (MW) | -0.56148 | -0.82288 | -0.80697 | -1.4576 | -2.5297 | -3.8391 | -5.3611 | -6.7827 | -7.9571 | -9.1883 | -10.372 | -11.1268 | -11.7143 | -12.3433 | -13.3013 | -14.0789 | -16.4324 | -16.7176 | -14.8508
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Steady Progression | Thermal headroom (MW) | -0.44194 | -0.31819 | -0.012525 | -0.25494 | -0.62753 | -1.0145 | -1.321 | -1.6431 | -1.8524 | -2.1097 | -2.3986 | -2.76 | -3.2318 | -3.7087 | -4.2165 | -4.7749 | -7.4718 | -8.7928 | -9.0946
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | System Transformation | Thermal headroom (MW) | -0.49329 | -0.39218 | -0.23521 | -0.53254 | -1.1075 | -1.6634 | -2.2649 | -2.824 | -3.1638 | -3.595 | -4.0997 | -4.7512 | -5.463 | -6.1168 | -6.8015 | -7.4236 | -9.2196 | -9.5065 | -8.7776
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | WPD Best View | Thermal headroom (MW) | -0.52789 | -0.7141 | -0.86349 | -1.4474 | -2.3355 | -3.424 | -4.7095 | -5.9867 | -7.0102 | -8.1423 | -9.297 | -10.5201 | -11.5958 | -12.511 | -13.5176 | -14.6895 | -19.2248 | -20.5084 | -20.156
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Consumer Transformation | Thermal headroom (MW) | 13.5548 | 13.4275 | 13.3128 | 13.1445 | 12.9615 | 12.7262 | 12.1947 | 11.3343 | 10.3365 | 8.811 | 7.4755 | 5.875 | 4.166 | 2.4215 | 0.63362 | -1.1479 | -8.3724 | -11.554 | -12.2683
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Leading the Way | Thermal headroom (MW) | 13.4698 | 13.3044 | 13.2638 | 13.0834 | 12.926 | 12.7017 | 12.13 | 11.2177 | 9.7797 | 8.4234 | 6.8408 | 5.118 | 3.285 | 1.3906 | -0.37747 | -2.4206 | -6.9734 | -7.5791 | -5.4569
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Steady Progression | Thermal headroom (MW) | 13.658 | 13.6707 | 13.7584 | 13.7106 | 13.7071 | 13.7179 | 13.7032 | 13.6806 | 13.6417 | 13.5926 | 13.4028 | 12.9373 | 12.3944 | 11.7768 | 11.0433 | 9.8644 | 4.1213 | -2.0003 | -3.6936
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | System Transformation | Thermal headroom (MW) | 13.5822 | 13.5703 | 13.6101 | 13.5685 | 13.5629 | 13.5442 | 13.4659 | 13.3796 | 13.2712 | 12.9032 | 12.2727 | 11.1509 | 10.2101 | 9.1325 | 7.8565 | 6.464 | -1.2732 | -5.3256 | -5.7628
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | WPD Best View | Thermal headroom (MW) | 13.5548 | 13.4275 | 13.3128 | 13.1445 | 12.9615 | 12.7262 | 12.1947 | 11.3343 | 10.3365 | 8.811 | 7.4755 | 5.875 | 4.166 | 2.4215 | 0.63362 | -1.1479 | -8.3724 | -11.554 | -12.2683
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Consumer Transformation | Thermal headroom (MW) | 18.9271 | 18.7608 | 18.4581 | 18.2101 | 17.9208 | 17.536 | 17.0261 | 16.4136 | 15.7297 | 14.9225 | 14.0316 | 13.0877 | 11.5462 | 10.4635 | 9.3496 | 8.2786 | 4.5448 | 3.2295 | 3.2494
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Leading the Way | Thermal headroom (MW) | 18.833 | 18.5971 | 18.4136 | 18.1262 | 17.8778 | 17.4755 | 16.9986 | 16.4091 | 15.6478 | 14.7327 | 13.6695 | 12.588 | 10.7062 | 9.4404 | 8.2548 | 7.1885 | 4.854 | 5.0921 | 6.7257
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Steady Progression | Thermal headroom (MW) | 19.0185 | 18.9595 | 18.9377 | 18.6982 | 18.6037 | 18.5398 | 18.4167 | 18.2737 | 18.0921 | 17.8573 | 17.5781 | 17.2278 | 16.5731 | 16.0918 | 15.5655 | 14.9665 | 11.0676 | 7.1059 | 5.8406
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | System Transformation | Thermal headroom (MW) | 18.9579 | 18.898 | 18.7498 | 18.5856 | 18.4913 | 18.3598 | 18.1411 | 17.8709 | 17.5993 | 17.2284 | 16.7184 | 16.1916 | 15.0493 | 14.2731 | 13.3619 | 12.3987 | 7.4816 | 5.1377 | 5.2127
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | WPD Best View | Thermal headroom (MW) | 18.9271 | 18.7608 | 18.4581 | 18.2101 | 17.9208 | 17.536 | 17.0261 | 16.4136 | 15.7297 | 14.9225 | 14.0316 | 13.0877 | 11.5462 | 10.4635 | 9.3496 | 8.2786 | 4.5448 | 3.2295 | 3.2494
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Consumer Transformation | Thermal headroom (MW) | 11.7244 | 11.7091 | 11.6036 | 11.5902 | 10.4607 | 9.3075 | 8.1581 | 6.9559 | 6.4263 | 5.806 | 5.1478 | 4.2953 | 3.419 | 2.6608 | 1.8801 | 1.0421 | -1.4848 | -1.7701 | -1.2844
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Leading the Way | Thermal headroom (MW) | 11.7136 | 11.4847 | 11.6093 | 11.6025 | 10.0715 | 8.5373 | 7.0189 | 5.2205 | 4.5095 | 3.6776 | 2.8045 | 2.121 | 1.4765 | 0.82751 | 0.23331 | -0.29814 | -1.3028 | -0.73374 | 0.76753
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Steady Progression | Thermal headroom (MW) | 11.7578 | 11.8301 | 12.0089 | 11.8932 | 11.1701 | 10.4427 | 9.9008 | 9.234 | 9.041 | 8.8402 | 8.6536 | 8.3917 | 8.0965 | 7.7821 | 7.4349 | 6.9104 | 4.2742 | 2.4945 | 2.1856
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | System Transformation | Thermal headroom (MW) | 11.7422 | 11.7987 | 11.7558 | 11.8467 | 10.8131 | 9.7703 | 8.7989 | 7.7589 | 7.5297 | 7.1928 | 6.8081 | 6.296 | 5.7519 | 5.2891 | 4.7402 | 4.0799 | 1.3355 | 0.64218 | 1.2691
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | WPD Best View | Thermal headroom (MW) | 11.7505 | 11.7957 | 11.9483 | 11.7913 | 10.7266 | 9.6594 | 8.6676 | 7.5769 | 7.2057 | 6.7542 | 6.2761 | 5.6498 | 5.0079 | 4.484 | 3.9166 | 3.2763 | 1.148 | 0.51791 | 0.84615
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Consumer Transformation | Thermal headroom (MW) | 12.545 | 12.2574 | 11.5032 | 10.6196 | 10.0547 | 9.4285 | 7.5044 | 5.2782 | 2.7433 | -0.43601 | -3.7444 | -7.6287 | -11.6568 | -15.7325 | -19.8442 | -23.921 | -44.0377 | -51.5375 | -53.8485
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Leading the Way | Thermal headroom (MW) | 12.3322 | 11.9482 | 11.1423 | 10.0716 | 9.4633 | 8.8655 | 6.6819 | 4.3368 | 1.1886 | -2.0059 | -5.6938 | -9.5892 | -13.7029 | -17.8758 | -21.8493 | -25.736 | -42.4166 | -44.3879 | -37.9165
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Steady Progression | Thermal headroom (MW) | 12.7726 | 12.8477 | 12.7809 | 12.3201 | 12.2265 | 12.183 | 11.8574 | 11.7049 | 11.515 | 11.3006 | 10.5387 | 9.3409 | 8.0161 | 6.4371 | 4.6829 | 2.3462 | -14.2314 | -29.1252 | -33.3291
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | System Transformation | Thermal headroom (MW) | 12.5914 | 12.6072 | 12.2209 | 11.6722 | 11.5118 | 11.4357 | 10.8385 | 10.5432 | 10.1949 | 9.0431 | 7.4334 | 5.1372 | 2.8741 | 0.22594 | -2.7995 | -6.0795 | -28.6036 | -38.6334 | -40.0818
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | WPD Best View | Thermal headroom (MW) | 12.5501 | 12.2684 | 11.5257 | 10.6552 | 10.1062 | 9.4999 | 7.5342 | 5.3186 | 2.7978 | -0.36516 | -3.6545 | -7.5151 | -11.5177 | -15.5668 | -19.6532 | -23.7024 | -43.7832 | -51.3768 | -53.7042
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Consumer Transformation | Thermal headroom (MW) | 36.479 | 35.8862 | 35.6665 | 35.0225 | 34.3825 | 33.4047 | 31.7134 | 30.1956 | 28.4233 | 26.1425 | 24.0454 | 21.5003 | 18.9487 | 16.6806 | 14.3234 | 12.0019 | 3.448 | 0.45336 | 0.7949
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Leading the Way | Thermal headroom (MW) | 36.4443 | 35.8578 | 35.7025 | 35.1571 | 34.5187 | 33.591 | 31.873 | 30.3318 | 28.1688 | 26.1518 | 24.0558 | 22.0604 | 20.0434 | 18.1949 | 16.3922 | 14.508 | 9.5 | 8.7192 | 11.7296
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Steady Progression | Thermal headroom (MW) | 36.6586 | 36.8653 | 37.4693 | 37.7226 | 37.8823 | 38.0745 | 38.2342 | 38.2834 | 38.3334 | 38.3339 | 38.2349 | 37.9879 | 37.6914 | 37.3152 | 36.8492 | 35.9424 | 31.841 | 26.9697 | 25.855
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | System Transformation | Thermal headroom (MW) | 36.5529 | 36.6227 | 37.1425 | 37.2263 | 37.3361 | 37.3703 | 37.2899 | 37.1464 | 36.8968 | 36.5645 | 36.1288 | 35.1796 | 34.4703 | 33.6502 | 32.7315 | 31.7139 | 25.7575 | 22.4502 | 22.7077
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | WPD Best View | Thermal headroom (MW) | 36.5497 | 36.6002 | 37.1002 | 37.1605 | 37.2315 | 37.2323 | 37.0877 | 36.8913 | 36.6004 | 36.1999 | 35.6603 | 34.6242 | 33.8444 | 32.9449 | 31.9402 | 30.8455 | 24.9816 | 21.7522 | 21.9969
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Consumer Transformation | Thermal headroom (MW) | 56.6969 | 53.3036 | 52.1491 | 50.7316 | 48.5657 | 46.2929 | 42.9062 | 39.85 | 36.7013 | 31.953 | 29.0552 | 25.3435 | 21.8033 | 18.7619 | 15.2538 | 12.1982 | -2.5299 | -8.7213 | -7.9763
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Leading the Way | Thermal headroom (MW) | 56.5798 | 52.0625 | 51.2051 | 49.2297 | 47.2573 | 44.9809 | 41.271 | 38.2567 | 33.3051 | 30.0871 | 27.2588 | 24.1866 | 21.6436 | 19.3985 | 16.6104 | 12.9203 | 5.0723 | 4.1738 | 8.0019
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Steady Progression | Thermal headroom (MW) | 56.9547 | 55.488 | 55.9222 | 55.4995 | 55.0435 | 54.6871 | 54.1511 | 53.6814 | 52.9216 | 52.2086 | 51.362 | 49.8096 | 48.5531 | 47.2058 | 45.6937 | 42.4322 | 32.7927 | 23.1577 | 21.0822
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | System Transformation | Thermal headroom (MW) | 56.8126 | 54.5143 | 54.3853 | 53.9633 | 53.341 | 52.4849 | 51.3297 | 50.2983 | 48.5428 | 47.2201 | 45.7888 | 42.2929 | 40.2512 | 37.6879 | 35.3761 | 33.0388 | 20.9963 | 15.1372 | 14.3666
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | WPD Best View | Thermal headroom (MW) | 56.7311 | 53.673 | 52.7733 | 51.6129 | 49.8694 | 47.9271 | 45.2473 | 42.888 | 40.3172 | 36.793 | 34.5451 | 31.0197 | 28.0938 | 25.3011 | 22.2806 | 19.7427 | 5.7793 | -1.3181 | -1.164
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Consumer Transformation | Thermal headroom (MW) | 1.2846 | 1.094 | 0.98303 | 0.78717 | 0.21364 | -0.025792 | -0.56165 | -1.0654 | -1.5756 | -2.4506 | -2.954 | -3.9336 | -4.4908 | -4.9943 | -5.8414 | -6.693 | -11.3134 | -13.6129 | -13.9841
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Leading the Way | Thermal headroom (MW) | 1.2763 | 1.1074 | 1.0389 | 0.5057 | 0.32655 | 0.069984 | -0.45027 | -0.94456 | -1.8217 | -2.366 | -2.9123 | -3.7026 | -4.0626 | -4.4142 | -5.5157 | -6.5664 | -9.2638 | -10.4535 | -9.9795
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Steady Progression | Thermal headroom (MW) | 1.3289 | 1.4007 | 1.5682 | 1.6378 | 1.6605 | 1.7045 | 1.7393 | 1.7456 | 1.7402 | 1.6718 | 1.5708 | 1.0491 | 0.8532 | 0.63923 | 0.3965 | -0.23133 | -2.1639 | -4.6697 | -5.5301
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | System Transformation | Thermal headroom (MW) | 1.3114 | 1.3615 | 1.4844 | 1.503 | 1.5299 | 1.5558 | 1.5231 | 1.4855 | 0.98104 | 0.81019 | 0.59585 | -0.024465 | -0.34839 | -1.0577 | -1.4498 | -1.8122 | -4.8769 | -6.7138 | -7.4084
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | WPD Best View | Thermal headroom (MW) | 1.2934 | 1.1599 | 1.1021 | 0.94481 | 0.43166 | 0.26462 | -0.14267 | -0.54039 | -0.95404 | -1.3962 | -1.8432 | -3.1182 | -3.6577 | -4.162 | -4.9729 | -5.3929 | -9.6034 | -11.8615 | -12.5002
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Consumer Transformation | Thermal headroom (MW) | 12.5237 | 9.2096 | 9.0019 | 8.6045 | 8.2257 | 7.3767 | 6.3278 | 5.4776 | 4.605 | 3.1142 | 2.3659 | 1.4938 | 0.74883 | 0.15912 | -0.24193 | -0.70056 | -4.6524 | -5.9725 | -5.2388
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Leading the Way | Thermal headroom (MW) | 12.4695 | 8.053 | 7.8972 | 7.4966 | 7.0505 | 6.3466 | 5.143 | 4.4923 | 3.0623 | 2.3568 | 1.757 | 1.3013 | 1.0376 | 0.98287 | 0.66079 | -0.66937 | -2.2457 | -1.9754 | -0.81602
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Steady Progression | Thermal headroom (MW) | 12.6289 | 10.5607 | 10.8165 | 10.8295 | 10.7375 | 10.6328 | 10.5119 | 10.4457 | 10.3268 | 10.1493 | 9.9258 | 9.5943 | 9.2334 | 8.8222 | 8.4072 | 7.2742 | 5.2605 | 3.3314 | 3.3161
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | System Transformation | Thermal headroom (MW) | 12.5687 | 9.5977 | 9.767 | 9.7311 | 9.7094 | 9.3833 | 9.0452 | 8.84 | 8.5281 | 8.2152 | 7.8479 | 6.5992 | 6.0214 | 5.4261 | 4.8393 | 4.2729 | 2.3269 | 1.5044 | 1.661
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | WPD Best View | Thermal headroom (MW) | 12.5367 | 9.2923 | 9.2162 | 8.9425 | 8.6761 | 7.9546 | 7.1724 | 6.5917 | 5.9194 | 4.9553 | 4.3298 | 3.2223 | 2.5391 | 1.9431 | 1.4578 | 1.05 | -1.32 | -2.6624 | -2.2555
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Consumer Transformation | Thermal headroom (MW) | 6.3151 | 6.2085 | 6.1058 | 5.9826 | 5.8407 | 5.6778 | 5.3862 | 5.0829 | 4.808 | 4.1669 | 3.9007 | 3.6159 | 3.3111 | 3.0365 | 2.8013 | 2.6252 | 1.4862 | 0.64119 | 0.62063
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Leading the Way | Thermal headroom (MW) | 6.3043 | 6.1958 | 6.1172 | 6.003 | 5.8596 | 5.7015 | 5.4097 | 5.1231 | 4.4716 | 4.1753 | 3.9104 | 3.6772 | 3.444 | 3.2624 | 3.1672 | 2.7482 | 1.9897 | 1.8639 | 1.9449
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Steady Progression | Thermal headroom (MW) | 6.3351 | 6.343 | 6.3698 | 6.3517 | 6.3444 | 6.3238 | 6.276 | 6.2239 | 6.1578 | 6.0721 | 5.9725 | 5.8492 | 5.6974 | 5.5362 | 5.3447 | 4.8068 | 3.7253 | 2.7817 | 2.5681
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | System Transformation | Thermal headroom (MW) | 6.327 | 6.3191 | 6.3225 | 6.302 | 6.2754 | 6.2406 | 6.1542 | 6.0409 | 5.9266 | 5.7928 | 5.6215 | 5.0633 | 4.8327 | 4.5902 | 4.339 | 4.0776 | 2.7035 | 2.1011 | 1.7804
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | WPD Best View | Thermal headroom (MW) | 6.3151 | 6.2085 | 6.1058 | 5.9826 | 5.8407 | 5.6778 | 5.3862 | 5.0829 | 4.808 | 4.1669 | 3.9007 | 3.6159 | 3.3111 | 3.0365 | 2.8013 | 2.6252 | 1.4862 | 0.64119 | 0.62063
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Consumer Transformation | Thermal headroom (MW) | 13.4771 | 12.2867 | 12.0349 | 11.7325 | 11.4061 | 10.768 | 10.0832 | 9.4796 | 8.8605 | 8.2722 | 7.7136 | 7.1039 | 6.3385 | 5.5194 | 4.6443 | 3.7675 | 0.74623 | -0.29647 | -0.27476
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Leading the Way | Thermal headroom (MW) | 13.4628 | 11.8828 | 11.7092 | 11.403 | 11.0463 | 10.457 | 9.7148 | 9.2138 | 8.642 | 8.0682 | 7.553 | 7.0418 | 6.3523 | 5.6481 | 4.9012 | 4.3173 | 2.444 | 2.1935 | 3.2509
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Steady Progression | Thermal headroom (MW) | 13.5353 | 12.8683 | 12.9443 | 12.8751 | 12.7891 | 12.6874 | 12.6006 | 12.521 | 12.4072 | 12.2893 | 12.0781 | 11.8444 | 11.5695 | 11.2697 | 10.9639 | 10.6153 | 8.857 | 7.3453 | 6.8977
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | System Transformation | Thermal headroom (MW) | 13.5022 | 12.5332 | 12.5241 | 12.4442 | 12.3703 | 12.1634 | 11.96 | 11.7796 | 11.5612 | 11.3179 | 11.0162 | 10.6346 | 10.2094 | 9.7662 | 9.3312 | 8.8965 | 7.2271 | 6.1196 | 6.1855
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | WPD Best View | Thermal headroom (MW) | 13.4832 | 12.3048 | 12.0834 | 11.8057 | 11.5159 | 10.9191 | 10.2832 | 9.7809 | 9.2631 | 8.7222 | 8.186 | 7.569 | 6.7206 | 5.9706 | 5.1378 | 4.2784 | 1.2623 | 0.17163 | 0.216
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Consumer Transformation | Thermal headroom (MW) | 75.7186 | 73.7701 | 73.163 | 72.4795 | 71.255 | 70.1172 | 68.3368 | 66.7115 | 64.8854 | 62.7311 | 60.9498 | 58.5332 | 56.267 | 54.5061 | 52.2471 | 50.3547 | 42.6216 | 40.8896 | 42.1896
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Leading the Way | Thermal headroom (MW) | 75.6463 | 72.8241 | 72.4413 | 71.3068 | 70.1209 | 68.9536 | 66.8136 | 65.0569 | 62.7891 | 60.7562 | 58.9654 | 56.8833 | 55.2975 | 53.6321 | 51.7757 | 50.2191 | 46.7384 | 47.3258 | 50.755
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Steady Progression | Thermal headroom (MW) | 75.8616 | 74.9711 | 75.3118 | 74.9556 | 74.6431 | 74.4934 | 74.1996 | 73.9753 | 73.5425 | 73.2522 | 72.875 | 72.0417 | 71.4444 | 70.8271 | 70.1366 | 69.0784 | 63.7037 | 58.1356 | 57.3186
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | System Transformation | Thermal headroom (MW) | 75.7578 | 74.3584 | 74.1991 | 73.9905 | 73.5443 | 73.0149 | 72.2885 | 71.7603 | 70.7767 | 70.0313 | 69.3469 | 68.1514 | 67.1248 | 65.7537 | 64.4449 | 63.1234 | 56.1718 | 53.4515 | 54.2583
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | WPD Best View | Thermal headroom (MW) | 75.752 | 74.1743 | 73.8095 | 73.4097 | 72.7784 | 71.9924 | 70.8688 | 69.9905 | 68.5607 | 67.252 | 66.2087 | 64.7199 | 63.292 | 61.6327 | 60.0914 | 58.5481 | 51.0005 | 48.1327 | 49.0273
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Consumer Transformation | Thermal headroom (MW) | 8.4579 | 8.2646 | 8.2294 | 8.2172 | 8.1938 | 8.1012 | 7.9006 | 7.5176 | 7.104 | 6.6739 | 6.2602 | 5.8298 | 5.4783 | 5.1722 | 4.8559 | 4.3483 | 2.3353 | 1.8956 | 2.2141
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Leading the Way | Thermal headroom (MW) | 8.4565 | 8.1381 | 8.1872 | 8.1921 | 8.1702 | 8.1021 | 7.8503 | 7.4753 | 7.0271 | 6.5723 | 6.1713 | 5.8415 | 5.6005 | 5.1467 | 4.547 | 4.0317 | 2.8683 | 3.1704 | 4.3755
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Steady Progression | Thermal headroom (MW) | 8.4965 | 8.4745 | 8.693 | 8.7494 | 8.8492 | 8.9617 | 9.0405 | 9.1236 | 9.1696 | 9.1687 | 9.0174 | 8.8029 | 8.5386 | 8.2587 | 7.9486 | 7.6238 | 5.8415 | 4.7696 | 4.5957
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | System Transformation | Thermal headroom (MW) | 8.4804 | 8.397 | 8.5053 | 8.6248 | 8.723 | 8.8094 | 8.8209 | 8.8475 | 8.8012 | 8.5739 | 8.2871 | 7.9231 | 7.5091 | 7.055 | 6.5769 | 6.1381 | 4.4542 | 4.2611 | 4.6166
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | WPD Best View | Thermal headroom (MW) | 8.4792 | 8.3802 | 8.4662 | 8.5708 | 8.6497 | 8.7171 | 8.6856 | 8.651 | 8.4547 | 8.1941 | 7.9123 | 7.5706 | 7.2227 | 6.88 | 6.5508 | 6.2509 | 4.7152 | 4.2719 | 4.5402
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Consumer Transformation | Thermal headroom (MW) | -0.72718 | -0.65699 | -0.68981 | -0.68813 | -1.0408 | -1.1597 | -1.4582 | -1.7455 | -2.1433 | -2.6332 | -3.2088 | -4.1946 | -4.8912 | -5.5768 | -6.626 | -7.318 | -10.3891 | -11.0222 | -10.3914
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Leading the Way | Thermal headroom (MW) | -0.73 | -0.64727 | -0.77865 | -1.1338 | -1.1656 | -1.2988 | -1.603 | -1.9711 | -2.3997 | -2.9782 | -3.6233 | -4.6601 | -5.3594 | -6.0957 | -7.1586 | -7.7223 | -9.2203 | -8.7677 | -6.7468
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Steady Progression | Thermal headroom (MW) | -0.70293 | -0.50392 | -0.32259 | -0.15556 | -0.0074709 | 0.12008 | 0.22109 | 0.30563 | 0.35867 | 0.39032 | 0.35516 | -0.080046 | -0.17275 | -0.32359 | -0.55522 | -0.79803 | -3.3802 | -6.3134 | -6.7826
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | System Transformation | Thermal headroom (MW) | -0.70978 | -0.51348 | -0.44486 | -0.31213 | -0.1793 | -0.070357 | -0.060077 | -0.059748 | -0.47633 | -0.57603 | -0.72719 | -0.97568 | -1.2934 | -2.0486 | -2.5144 | -3.071 | -7.0638 | -8.786 | -8.3601
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | WPD Best View | Thermal headroom (MW) | -0.70978 | -0.51348 | -0.44486 | -0.31213 | -0.1793 | -0.070357 | -0.060077 | -0.059748 | -0.47633 | -0.57603 | -0.72719 | -0.97568 | -1.2934 | -2.0486 | -2.5144 | -3.071 | -7.0638 | -8.786 | -8.3601
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Consumer Transformation | Thermal headroom (MW) | 10.8652 | 9.6176 | 8.4527 | 7.234 | 5.4555 | 3.8613 | 1.4314 | -0.52645 | -2.7525 | -5.0539 | -6.7734 | -8.6968 | -11.0424 | -12.3775 | -14.0938 | -15.3203 | -19.6972 | -19.5924 | -17.9714
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Leading the Way | Thermal headroom (MW) | 10.7438 | 8.6169 | 7.8171 | 6.224 | 3.815 | 1.9343 | -1.0975 | -3.5137 | -6.4816 | -8.7607 | -10.3966 | -12.0764 | -13.4073 | -14.4605 | -15.0495 | -15.7624 | -16.2822 | -14.9116 | -12.6103
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Steady Progression | Thermal headroom (MW) | 11.0122 | 10.6084 | 10.5002 | 9.2859 | 8.1938 | 7.5131 | 6.5645 | 5.8461 | 4.6438 | 3.9796 | 3.5276 | 2.9626 | 2.401 | 1.8947 | 1.3437 | 0.42901 | -3.1904 | -6.85 | -7.0065
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | System Transformation | Thermal headroom (MW) | 10.8892 | 10.187 | 9.2625 | 8.3178 | 6.805 | 5.4466 | 3.9069 | 2.7354 | 1.4025 | 0.31779 | -0.38569 | -1.5929 | -2.5011 | -3.2536 | -4.3847 | -5.5036 | -9.5246 | -10.6344 | -9.4233
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | WPD Best View | Thermal headroom (MW) | 10.8878 | 10.1851 | 9.2577 | 8.311 | 6.7943 | 5.432 | 3.8865 | 2.7081 | 1.3674 | 0.27464 | -0.43796 | -1.6541 | -2.5688 | -3.325 | -4.454 | -5.5665 | -9.4963 | -10.6482 | -9.5023
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Consumer Transformation | Thermal headroom (MW) | 73.4464 | 70.6824 | 70.0335 | 68.7179 | 64.9412 | 62.0249 | 59.8937 | 58.0072 | 55.6887 | 52.5194 | 49.88 | 46.4297 | 43.2535 | 40.4243 | 37.235 | 34.3563 | 23.992 | 21.0419 | 22.5731
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Leading the Way | Thermal headroom (MW) | 73.3402 | 69.79 | 69.3114 | 67.5564 | 63.0888 | 59.8146 | 57.542 | 55.641 | 52.7705 | 49.8095 | 47.168 | 44.4971 | 42.0449 | 39.6771 | 37.1303 | 34.6564 | 29.3855 | 29.7569 | 33.5874
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Steady Progression | Thermal headroom (MW) | 73.7154 | 72.4521 | 72.9596 | 72.7213 | 70.8442 | 69.809 | 69.7548 | 69.438 | 69.0657 | 68.633 | 68.1719 | 67.2451 | 66.322 | 65.4022 | 64.3031 | 62.5198 | 56.1029 | 48.9755 | 47.1607
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | System Transformation | Thermal headroom (MW) | 73.5254 | 71.591 | 71.8324 | 71.3994 | 68.7551 | 67.0872 | 66.6129 | 66.1456 | 65.0896 | 64.101 | 63.0978 | 61.3596 | 60.0365 | 58.2751 | 56.6009 | 54.9724 | 46.8054 | 42.3534 | 42.8171
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | WPD Best View | Thermal headroom (MW) | 73.5067 | 71.2122 | 71.0252 | 70.2037 | 67.1592 | 64.9829 | 63.7823 | 62.66 | 60.8965 | 58.866 | 57.1332 | 54.7554 | 52.6011 | 50.3633 | 48.2335 | 46.1195 | 36.2803 | 32.0175 | 32.7654
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Consumer Transformation | Thermal headroom (MW) | 11.0103 | 10.8451 | 10.6334 | 10.1714 | 9.8414 | 7.5986 | 7.0976 | 6.5888 | 6.037 | 4.8816 | 4.1018 | 3.2922 | 2.4593 | 1.7764 | 1.1404 | 0.48654 | -1.5838 | -2.0141 | -1.3107
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Leading the Way | Thermal headroom (MW) | 10.9766 | 10.7892 | 10.5533 | 9.9502 | 9.5477 | 6.6259 | 6.1494 | 5.6302 | 4.6594 | 3.9397 | 3.0412 | 2.4398 | 1.8056 | 1.2732 | 0.75006 | 0.01257 | -0.66593 | 0.022719 | 0.92646
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Steady Progression | Thermal headroom (MW) | 11.0693 | 11.0733 | 11.133 | 10.9372 | 10.8369 | 9.4882 | 9.4654 | 9.3651 | 9.1838 | 9.0228 | 8.8541 | 8.6642 | 8.3614 | 8.1522 | 7.7771 | 6.9933 | 5.3372 | 3.8743 | 3.6422
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | System Transformation | Thermal headroom (MW) | 11.0297 | 11.0169 | 10.983 | 10.6547 | 10.4761 | 8.5618 | 8.4804 | 8.357 | 8.2151 | 7.8377 | 7.4918 | 6.771 | 6.3978 | 5.977 | 5.4823 | 5.0099 | 3.1108 | 2.1535 | 2.3337
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | WPD Best View | Thermal headroom (MW) | 11.0273 | 10.9976 | 10.9358 | 10.5894 | 10.3834 | 8.4451 | 8.3587 | 8.1936 | 8.0195 | 7.5872 | 7.2075 | 6.4558 | 6.0074 | 5.642 | 5.2122 | 4.7723 | 2.7272 | 1.9022 | 2.0654
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Consumer Transformation | Thermal headroom (MW) | 24.5494 | 21.6037 | 21.3562 | 20.9191 | 20.1324 | 19.2659 | 18.0497 | 17.0479 | 15.9896 | 14.394 | 13.1725 | 11.156 | 9.426 | 7.8574 | 5.8883 | 4.2654 | -2.7706 | -5.336 | -4.9811
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Leading the Way | Thermal headroom (MW) | 24.4997 | 20.5829 | 20.4747 | 19.6843 | 19.2099 | 18.4968 | 17.0941 | 16.259 | 14.9519 | 13.7247 | 12.4575 | 10.8521 | 9.5713 | 8.2529 | 6.6648 | 5.2281 | 1.3474 | 0.55823 | 2.2548
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Steady Progression | Thermal headroom (MW) | 24.6522 | 22.9017 | 23.2186 | 23.2252 | 23.173 | 23.1257 | 23.0701 | 22.9798 | 22.9341 | 22.8363 | 22.6706 | 22.0866 | 21.7673 | 21.4375 | 21.1105 | 20.325 | 16.9534 | 12.4065 | 11.4798
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | System Transformation | Thermal headroom (MW) | 24.5623 | 22.0567 | 22.2578 | 22.29 | 22.3203 | 22.0798 | 21.776 | 21.5769 | 21.0336 | 20.7839 | 20.4863 | 19.7172 | 19.2068 | 18.2925 | 17.5981 | 16.8902 | 11.6078 | 8.5641 | 8.3288
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | WPD Best View | Thermal headroom (MW) | 24.5529 | 21.6838 | 21.4753 | 21.1167 | 20.7777 | 20.0117 | 18.9157 | 18.0571 | 16.7858 | 15.369 | 14.2897 | 12.8545 | 11.3717 | 9.6572 | 8.2199 | 6.8042 | -0.086677 | -3.021 | -2.8723
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Consumer Transformation | Thermal headroom (MW) | 0.61925 | 0.42907 | 0.29066 | 0.10189 | -1.3809 | -1.6418 | -2.0236 | -2.3035 | -2.8222 | -3.3347 | -3.8138 | -4.3584 | -4.8607 | -5.3383 | -5.8522 | -6.3527 | -7.8702 | -8.0128 | -7.5231
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Leading the Way | Thermal headroom (MW) | 0.59266 | 0.38224 | 0.3112 | 0.14131 | -1.766 | -2.0246 | -2.3673 | -2.7293 | -3.1979 | -3.8202 | -4.3057 | -4.7786 | -5.2397 | -5.7008 | -6.1724 | -6.6109 | -7.421 | -6.963 | -5.9317
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Steady Progression | Thermal headroom (MW) | 0.71418 | 0.79419 | 0.96214 | 1.0421 | 0.20941 | 0.26232 | 0.33037 | 0.28719 | 0.25836 | 0.20281 | 0.17815 | 0.073096 | -0.13593 | -0.4271 | -0.76713 | -1.1148 | -2.7479 | -4.1743 | -4.6884
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | System Transformation | Thermal headroom (MW) | 0.65354 | 0.6842 | 0.7835 | 0.84031 | -0.39877 | -0.36677 | -0.45102 | -0.52719 | -0.74555 | -0.9456 | -1.1737 | -1.4474 | -1.7986 | -2.2635 | -2.7316 | -3.185 | -4.6698 | -5.3353 | -5.0248
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | WPD Best View | Thermal headroom (MW) | 0.64542 | 0.59591 | 0.5902 | 0.56339 | -0.77688 | -0.83766 | -1.0437 | -1.2271 | -1.5767 | -1.8841 | -2.2307 | -2.6391 | -3.0406 | -3.4139 | -3.8454 | -4.3071 | -6.0478 | -6.7289 | -6.4009
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Consumer Transformation | Thermal headroom (MW) | 5.0189 | 4.6946 | 4.3901 | 3.6164 | 0.7686 | 0.22127 | -0.60107 | -1.4159 | -2.5054 | -3.5623 | -4.7357 | -6.1015 | -7.4092 | -8.5737 | -9.8289 | -11.012 | -14.4774 | -15.3157 | -14.7647
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Leading the Way | Thermal headroom (MW) | 4.9846 | 4.6623 | 4.4031 | 3.5123 | -0.22252 | -0.71117 | -1.6071 | -2.5391 | -3.7571 | -5.3369 | -6.3023 | -7.2703 | -8.2675 | -9.2059 | -10.0927 | -10.8306 | -12.6238 | -12.4522 | -10.7969
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Steady Progression | Thermal headroom (MW) | 5.1329 | 5.1852 | 5.3229 | 5.0688 | 3.2695 | 3.2428 | 3.1674 | 2.9459 | 2.6601 | 2.3506 | 2.0513 | 1.6518 | 1.1948 | 0.74513 | 0.26671 | -0.23056 | -2.2822 | -4.5023 | -5.3406
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | System Transformation | Thermal headroom (MW) | 5.0635 | 5.0626 | 5.1167 | 4.7074 | 2.1711 | 2.0842 | 1.905 | 1.6468 | 1.0708 | 0.50099 | -0.035913 | -0.65136 | -1.2496 | -1.8476 | -2.4859 | -3.0796 | -5.4476 | -6.8088 | -6.3748
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | WPD Best View | Thermal headroom (MW) | 5.0583 | 5.0536 | 5.0964 | 4.6773 | 2.1193 | 2.0171 | 1.8187 | 1.5166 | 0.9166 | 0.33121 | -0.21204 | -0.81687 | -1.3813 | -1.9265 | -2.4937 | -3.0118 | -5.5607 | -6.8961 | -6.4865
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Consumer Transformation | Thermal headroom (MW) | 70.4519 | 68.4498 | 67.3793 | 65.7603 | 62.8745 | 58.5455 | 54.1393 | 49.7283 | 45.4851 | 39.8121 | 35.8363 | 31.1301 | 26.4912 | 22.3969 | 17.777 | 13.5069 | -2.4609 | -7.1089 | -3.3692
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Leading the Way | Thermal headroom (MW) | 70.0134 | 67.41 | 66.6797 | 64.5754 | 61.5708 | 56.8082 | 52.5102 | 48.3374 | 42.7487 | 38.7181 | 34.8945 | 32.1501 | 29.6205 | 26.5079 | 23.3174 | 19.245 | 12.4978 | 14.0257 | 21.6472
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Steady Progression | Thermal headroom (MW) | 71.1527 | 71.3156 | 72.8002 | 72.9408 | 72.7394 | 72.0382 | 72.175 | 72.0539 | 71.8381 | 71.4701 | 70.9876 | 69.8445 | 68.6816 | 67.2851 | 65.6163 | 62.3196 | 52.9925 | 45.5533 | 44.3626
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | System Transformation | Thermal headroom (MW) | 70.6394 | 70.2972 | 70.9537 | 70.9857 | 70.0316 | 68.5902 | 68.0699 | 67.209 | 66.0126 | 64.6895 | 63.1476 | 59.7331 | 57.4491 | 54.7922 | 52.4128 | 50.2249 | 41.1389 | 36.6008 | 38.6503
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | WPD Best View | Thermal headroom (MW) | 70.0134 | 67.41 | 66.6716 | 64.5754 | 61.5708 | 56.8082 | 52.5102 | 48.3374 | 42.7487 | 38.7181 | 34.8945 | 32.1501 | 29.6205 | 26.5079 | 23.3174 | 19.024 | 11.9797 | 13.9314 | 21.4639
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Consumer Transformation | Thermal headroom (MW) | 8.92 | 8.7856 | 8.9262 | 8.8208 | 8.7135 | 8.5846 | 8.142 | 7.7558 | 7.3802 | 7.0116 | 6.6768 | 6.1673 | 5.7007 | 5.2732 | 4.782 | 3.7383 | -0.23087 | -1.8277 | -1.9504
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Leading the Way | Thermal headroom (MW) | 8.9025 | 8.7886 | 8.995 | 8.9257 | 8.8747 | 8.7633 | 8.3273 | 7.9907 | 7.632 | 7.2486 | 6.8908 | 6.6336 | 6.4349 | 6.2768 | 5.6363 | 4.8709 | 2.4993 | 1.8053 | 3.4922
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Steady Progression | Thermal headroom (MW) | 8.9949 | 9.2201 | 9.7327 | 9.9933 | 10.2363 | 10.4691 | 10.7012 | 10.8917 | 11.0891 | 11.257 | 11.4013 | 11.4646 | 11.5305 | 11.5518 | 11.5673 | 11.5551 | 10.9736 | 10.5239 | 10.6613
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | System Transformation | Thermal headroom (MW) | 8.9454 | 9.1371 | 9.6125 | 9.8435 | 10.0587 | 10.251 | 10.3903 | 10.5133 | 10.6023 | 10.6751 | 10.7196 | 10.7094 | 10.6647 | 10.5846 | 10.4477 | 10.2845 | 9.7753 | 9.3781 | 9.7087
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | WPD Best View | Thermal headroom (MW) | 8.9025 | 8.7886 | 8.995 | 8.9257 | 8.8747 | 8.7633 | 8.3273 | 7.9907 | 7.632 | 7.2486 | 6.8908 | 6.6336 | 6.4349 | 6.2768 | 5.6363 | 4.8709 | 2.4993 | 1.8053 | 3.4922
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Consumer Transformation | Thermal headroom (MW) | 12.6755 | 12.7052 | 12.8492 | 12.9054 | 12.9522 | 12.9757 | 12.979 | 12.9712 | 12.9246 | 12.5192 | 12.468 | 12.435 | 12.4242 | 12.4419 | 12.5007 | 12.5726 | 12.3312 | 12.1237 | 12.4259
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Leading the Way | Thermal headroom (MW) | 12.6638 | 12.6819 | 12.8292 | 12.8805 | 12.927 | 12.9435 | 12.9555 | 12.9424 | 12.5377 | 12.4863 | 12.4405 | 12.4345 | 12.4704 | 12.5408 | 12.6664 | 12.3659 | 12.7537 | 13.1048 | 13.2355
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Steady Progression | Thermal headroom (MW) | 12.6943 | 12.745 | 12.9125 | 12.9951 | 13.0731 | 13.1431 | 13.203 | 13.2555 | 13.3047 | 13.3453 | 13.3675 | 13.3753 | 13.3539 | 13.3218 | 13.2794 | 12.8685 | 12.5316 | 12.0575 | 12.2062
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | System Transformation | Thermal headroom (MW) | 12.6859 | 12.7231 | 12.8925 | 12.9652 | 13.0403 | 13.1027 | 13.1524 | 13.1965 | 13.2272 | 13.236 | 13.2115 | 12.8004 | 12.7255 | 12.6382 | 12.5568 | 12.4694 | 11.9794 | 11.7353 | 11.6871
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | WPD Best View | Thermal headroom (MW) | 12.6638 | 12.6819 | 12.8292 | 12.8805 | 12.927 | 12.9435 | 12.9555 | 12.9424 | 12.5377 | 12.4863 | 12.4405 | 12.4345 | 12.4704 | 12.5408 | 12.6664 | 12.3659 | 12.7537 | 13.1048 | 13.2355
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Consumer Transformation | Thermal headroom (MW) | 1.079 | 0.71598 | 0.64409 | 0.48332 | 0.32254 | 0.089616 | -0.49326 | -1.0031 | -1.5278 | -2.0826 | -2.5825 | -3.2097 | -3.7617 | -4.23 | -4.58 | -4.8252 | -5.9832 | -6.676 | -6.3072
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Leading the Way | Thermal headroom (MW) | 0.97134 | 0.5584 | 0.53896 | 0.4182 | 0.30759 | 0.11267 | -0.40027 | -0.8317 | -1.3269 | -1.8764 | -2.3352 | -2.6598 | -2.8964 | -2.9985 | -2.9552 | -2.8564 | -3.4245 | -3.5582 | -2.4202
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Steady Progression | Thermal headroom (MW) | 1.2092 | 1.2 | 1.4893 | 1.6159 | 1.7632 | 1.8779 | 1.9707 | 2.055 | 2.1264 | 2.1725 | 2.1949 | 2.1477 | 2.0211 | 1.863 | 1.6727 | 1.4697 | 0.29673 | -0.017489 | 0.095664
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | System Transformation | Thermal headroom (MW) | 1.1103 | 1.023 | 1.2576 | 1.3642 | 1.4883 | 1.5903 | 1.6143 | 1.6133 | 1.5827 | 1.5338 | 1.4292 | 1.2176 | 0.9598 | 0.67017 | 0.37258 | 0.10893 | -0.58654 | -0.54173 | 0.067588
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | WPD Best View | Thermal headroom (MW) | 0.97134 | 0.5584 | 0.53896 | 0.4182 | 0.30759 | 0.11267 | -0.40027 | -0.8317 | -1.3269 | -1.8764 | -2.3352 | -2.6598 | -2.8964 | -2.9985 | -2.9552 | -3.1569 | -3.7984 | -3.5582 | -2.4202
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Consumer Transformation | Thermal headroom (MW) | 8.6624 | 8.5607 | 8.6106 | 8.5598 | 8.4942 | 8.4223 | 8.239 | 8.0784 | 7.8715 | 7.667 | 7.4701 | 7.256 | 7.0737 | 6.9476 | 6.8797 | 6.8641 | 6.712 | 6.8311 | 7.2248
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Leading the Way | Thermal headroom (MW) | 8.6124 | 8.498 | 8.5755 | 8.5409 | 8.4933 | 8.4366 | 8.2609 | 8.1349 | 7.9185 | 7.707 | 7.5212 | 7.3965 | 7.3337 | 7.3368 | 7.4306 | 7.528 | 7.6583 | 7.9615 | 8.792
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Steady Progression | Thermal headroom (MW) | 8.7316 | 8.807 | 9.0314 | 9.1383 | 9.2434 | 9.3166 | 9.3966 | 9.4769 | 9.54 | 9.5893 | 9.6163 | 9.6045 | 9.5426 | 9.4577 | 9.3714 | 9.2682 | 8.5725 | 8.558 | 8.6794
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | System Transformation | Thermal headroom (MW) | 8.6812 | 8.7279 | 8.9306 | 8.9994 | 9.086 | 9.1688 | 9.2082 | 9.2333 | 9.2419 | 9.2302 | 9.1805 | 9.0543 | 8.9083 | 8.7381 | 8.5706 | 8.4173 | 7.9973 | 8.1451 | 8.6009
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | WPD Best View | Thermal headroom (MW) | 8.6124 | 8.498 | 8.5755 | 8.5409 | 8.4933 | 8.4366 | 8.2609 | 8.1349 | 7.9185 | 7.707 | 7.5212 | 7.3965 | 7.3337 | 7.3368 | 7.4306 | 7.4811 | 7.5345 | 7.9615 | 8.7195
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Consumer Transformation | Thermal headroom (MW) | 11.0631 | 10.8119 | 10.6934 | 10.4073 | 10.1424 | 9.6047 | 8.684 | 7.9501 | 7.2333 | 6.4682 | 5.6849 | 4.6008 | 3.5089 | 2.4897 | 1.4105 | 0.38835 | -3.7826 | -5.1725 | -5.1026
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Leading the Way | Thermal headroom (MW) | 11.0116 | 10.7742 | 10.7509 | 10.5101 | 10.2574 | 9.7872 | 8.8728 | 8.1524 | 7.4157 | 6.6172 | 5.8108 | 5.0269 | 4.2091 | 3.3317 | 2.4614 | 1.7524 | -0.64002 | -1.1738 | 0.16488
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Steady Progression | Thermal headroom (MW) | 11.1546 | 11.2709 | 11.5405 | 11.6486 | 11.7429 | 11.8417 | 11.9501 | 12.0308 | 12.0308 | 12.0763 | 12.0087 | 11.7915 | 11.5145 | 11.2056 | 10.8571 | 10.4848 | 8.3342 | 7.0208 | 6.5893
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | System Transformation | Thermal headroom (MW) | 11.0875 | 11.1677 | 11.3861 | 11.4626 | 11.5463 | 11.608 | 11.5661 | 11.528 | 11.5267 | 11.3592 | 11.0663 | 10.671 | 10.2142 | 9.7097 | 9.1884 | 8.7038 | 6.6311 | 5.7058 | 5.9287
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | WPD Best View | Thermal headroom (MW) | 11.0116 | 10.7742 | 10.7509 | 10.5101 | 10.2574 | 9.7872 | 8.8728 | 8.1524 | 7.4157 | 6.6172 | 5.8108 | 5.0269 | 4.2091 | 3.3317 | 2.4614 | 1.7524 | -0.64002 | -1.1738 | 0.16488
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Consumer Transformation | Thermal headroom (MW) | 4.6955 | 4.7309 | 4.7485 | 4.7059 | 3.9088 | 3.8991 | 3.8334 | 3.5799 | 3.2784 | 2.6957 | 2.5618 | 2.4378 | 2.328 | 2.226 | 2.148 | 2.1046 | 1.8339 | 1.4927 | 1.6488
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Leading the Way | Thermal headroom (MW) | 4.6852 | 4.6436 | 4.7479 | 4.6767 | 3.5898 | 3.5859 | 3.5296 | 3.224 | 2.5674 | 2.2718 | 2.1977 | 2.166 | 2.1383 | 2.1401 | 2.1699 | 1.8515 | 2.0624 | 2.2208 | 2.2342
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Steady Progression | Thermal headroom (MW) | 4.7071 | 4.7699 | 4.9001 | 4.8321 | 4.2936 | 4.3448 | 4.3665 | 4.306 | 4.2408 | 4.1808 | 4.1647 | 4.1321 | 4.0893 | 4.0526 | 4.0127 | 3.5912 | 3.4096 | 2.8666 | 2.9463
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | System Transformation | Thermal headroom (MW) | 4.6995 | 4.7575 | 4.801 | 4.7939 | 4.0292 | 4.0567 | 4.0873 | 4.0219 | 3.884 | 3.7798 | 3.7127 | 3.295 | 3.2512 | 3.1932 | 3.1079 | 3.0424 | 2.6248 | 2.3902 | 2.2905
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | WPD Best View | Thermal headroom (MW) | 4.6852 | 4.6436 | 4.7479 | 4.6767 | 3.5898 | 3.5859 | 3.5296 | 3.224 | 2.5674 | 2.2718 | 2.1977 | 2.166 | 2.1383 | 2.1401 | 2.1699 | 1.8298 | 1.9091 | 2.1587 | 2.151
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Consumer Transformation | Thermal headroom (MW) | 9.9992 | 9.5856 | 9.2182 | 8.8006 | 8.121 | 5.1464 | 4.3308 | 3.5889 | 2.7875 | 1.7513 | 0.81206 | -0.85461 | -2.4276 | -3.8153 | -5.6272 | -7.0965 | -13.0907 | -15.0883 | -14.9197
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Leading the Way | Thermal headroom (MW) | 9.9124 | 9.3915 | 9.0932 | 8.2872 | 8.006 | 4.1686 | 3.4021 | 2.7913 | 1.9398 | 1.0033 | -0.53119 | -1.9893 | -3.1823 | -4.3724 | -5.8844 | -6.9457 | -10.0003 | -10.5081 | -8.3738
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Steady Progression | Thermal headroom (MW) | 10.1192 | 10.0652 | 10.1667 | 10.0482 | 10.0959 | 8.3162 | 8.2606 | 8.2203 | 8.0161 | 7.7767 | 7.5233 | 6.8056 | 6.3959 | 5.9463 | 5.4572 | 4.9405 | 1.7816 | -1.717 | -2.9395
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | System Transformation | Thermal headroom (MW) | 10.029 | 9.8977 | 9.8517 | 9.7427 | 9.751 | 7.2504 | 7.1463 | 7.0062 | 6.4698 | 5.9918 | 5.4358 | 4.8703 | 4.2213 | 3.2479 | 2.6258 | 1.9929 | -2.7094 | -5.3754 | -5.2283
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | WPD Best View | Thermal headroom (MW) | 9.9124 | 9.3915 | 9.0932 | 8.2872 | 8.006 | 4.1686 | 3.4021 | 2.7913 | 1.9398 | 1.0033 | -0.53119 | -1.9893 | -3.1823 | -4.3724 | -5.8844 | -6.9457 | -10.0003 | -10.5081 | -8.3738
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Consumer Transformation | Thermal headroom (MW) | 14.235 | 13.7399 | 13.4129 | 13.0874 | 12.7027 | 11.7141 | 10.453 | 9.1854 | 8.1018 | 6.7328 | 5.7121 | 4.6955 | 3.5609 | 2.6381 | 1.759 | 0.99066 | -1.32 | -1.5268 | -0.31861
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Leading the Way | Thermal headroom (MW) | 14.1313 | 13.468 | 13.1431 | 12.6371 | 12.2449 | 11.2533 | 10.017 | 8.8092 | 7.4304 | 6.5254 | 5.72 | 5.2801 | 4.7545 | 4.1423 | 3.5987 | 2.8573 | 2.0535 | 2.7983 | 3.9207
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Steady Progression | Thermal headroom (MW) | 14.3822 | 14.3087 | 14.4602 | 14.4239 | 14.491 | 14.4036 | 14.252 | 14.0547 | 13.8886 | 13.6648 | 13.4334 | 13.1744 | 12.8918 | 12.5705 | 12.1492 | 11.3795 | 9.707 | 8.7706 | 8.9568
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | System Transformation | Thermal headroom (MW) | 14.2697 | 14.0758 | 14.0184 | 13.9553 | 13.8522 | 13.6417 | 13.3211 | 12.9232 | 12.5425 | 12.1557 | 11.7462 | 10.9426 | 10.4127 | 9.866 | 9.4033 | 9.0108 | 7.9381 | 7.9163 | 8.4706
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | WPD Best View | Thermal headroom (MW) | 14.1313 | 13.468 | 13.138 | 12.6371 | 12.2449 | 11.2533 | 10.017 | 8.8092 | 7.4304 | 6.5254 | 5.72 | 5.2801 | 4.7545 | 4.1423 | 3.5987 | 2.8573 | 2.0535 | 2.7983 | 3.9207
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Consumer Transformation | Thermal headroom (MW) | 69.3885 | 68.0228 | 65.8454 | 63.4231 | 60.5087 | 56.6615 | 52.2124 | 48.6247 | 44.8768 | 40.3064 | 37.0834 | 33.3261 | 29.7326 | 26.1052 | 22.0691 | 18.5077 | 7.1121 | 5.081 | 7.6823
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Leading the Way | Thermal headroom (MW) | 69.1465 | 67.4499 | 64.9962 | 62.1519 | 58.961 | 54.2639 | 48.9404 | 44.4389 | 39.4119 | 34.3141 | 30.7642 | 27.7101 | 24.6317 | 21.6877 | 18.7329 | 16.3067 | 11.308 | 13.3895 | 19.2739
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Steady Progression | Thermal headroom (MW) | 69.836 | 69.7396 | 69.4032 | 68.4163 | 67.1845 | 65.3696 | 63.7649 | 62.4275 | 61.0674 | 59.6366 | 58.6692 | 57.1642 | 55.7924 | 54.2667 | 52.682 | 50.6663 | 41.2092 | 30.079 | 27.4346
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | System Transformation | Thermal headroom (MW) | 69.5206 | 69.1543 | 67.9783 | 66.5494 | 64.8746 | 62.2982 | 59.2903 | 56.9919 | 54.5338 | 51.9398 | 50.1211 | 47.6259 | 45.3153 | 42.5745 | 39.8985 | 37.2433 | 25.8749 | 21.0786 | 22.7297
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | WPD Best View | Thermal headroom (MW) | 69.1465 | 67.4499 | 64.9962 | 62.1346 | 58.8911 | 54.1463 | 48.7707 | 44.3978 | 39.4119 | 34.3141 | 30.7642 | 27.7101 | 24.6317 | 21.6877 | 18.6694 | 16.0987 | 11.3028 | 13.3895 | 19.2739
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Consumer Transformation | Thermal headroom (MW) | 7.5616 | 7.2819 | 6.9696 | 6.5006 | 5.7774 | 5.3098 | 4.6549 | 4.0722 | 3.3711 | 2.5406 | 1.6514 | 0.25442 | -0.83502 | -1.9225 | -3.4282 | -4.5538 | -9.0617 | -10.3596 | -9.9254
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Leading the Way | Thermal headroom (MW) | 7.5434 | 7.1418 | 6.8865 | 6.1616 | 5.7914 | 5.3096 | 4.655 | 4.0647 | 3.2626 | 2.4034 | 1.4233 | -0.023815 | -1.1765 | -2.3156 | -3.8109 | -4.8096 | -7.388 | -7.2464 | -5.2912
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Steady Progression | Thermal headroom (MW) | 7.6454 | 7.7339 | 7.8839 | 7.7576 | 7.7189 | 7.6828 | 7.6771 | 7.628 | 7.575 | 7.4882 | 7.3596 | 6.7438 | 6.4743 | 6.0808 | 5.6584 | 5.1729 | 1.2897 | -3.1297 | -4.4776
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | System Transformation | Thermal headroom (MW) | 7.5899 | 7.624 | 7.5494 | 7.3944 | 7.3405 | 7.2948 | 7.1311 | 6.9481 | 6.3794 | 6.0774 | 5.6998 | 5.194 | 4.6116 | 3.5716 | 2.7479 | 1.8366 | -3.8282 | -6.613 | -6.5913
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | WPD Best View | Thermal headroom (MW) | 7.5434 | 7.1418 | 6.8865 | 6.1616 | 5.7914 | 5.3096 | 4.655 | 4.0647 | 3.2626 | 2.4034 | 1.4233 | -0.023815 | -1.1765 | -2.3156 | -3.8109 | -4.8096 | -7.388 | -7.2464 | -5.2912
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Consumer Transformation | Thermal headroom (MW) | 10.3681 | 9.983 | 9.7711 | 9.6441 | 9.5377 | 9.3895 | 9.0985 | 8.8362 | 8.559 | 7.9108 | 7.6445 | 7.323 | 7.0388 | 6.8257 | 6.6635 | 6.5825 | 5.8119 | 5.2259 | 5.5437
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Leading the Way | Thermal headroom (MW) | 10.2601 | 9.6872 | 9.5546 | 9.4259 | 9.3249 | 9.2045 | 8.923 | 8.7287 | 8.1248 | 7.8679 | 7.6562 | 7.5172 | 7.4244 | 7.3983 | 7.4652 | 7.2124 | 6.8379 | 6.9477 | 7.3534
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Steady Progression | Thermal headroom (MW) | 10.4776 | 10.3343 | 10.4239 | 10.3635 | 10.4093 | 10.4496 | 10.4724 | 10.4848 | 10.5091 | 10.5194 | 10.5129 | 10.4702 | 10.4173 | 10.3116 | 10.2103 | 9.7382 | 9.143 | 8.6801 | 8.7813
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | System Transformation | Thermal headroom (MW) | 10.3856 | 10.1458 | 10.084 | 10.1097 | 10.1561 | 10.1836 | 10.1736 | 10.1619 | 10.1467 | 10.1186 | 10.0623 | 9.5633 | 9.4107 | 9.2444 | 9.0717 | 8.9316 | 8.2642 | 7.9838 | 8.0039
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | WPD Best View | Thermal headroom (MW) | 10.2601 | 9.6872 | 9.5546 | 9.4259 | 9.3249 | 9.2045 | 8.923 | 8.7287 | 8.1248 | 7.8679 | 7.6562 | 7.5172 | 7.4244 | 7.3983 | 7.3854 | 6.9506 | 6.8313 | 6.9477 | 7.3534
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Consumer Transformation | Thermal headroom (MW) | 29.4814 | 29.1797 | 28.4787 | 27.6517 | 26.582 | 24.8769 | 22.9983 | 21.7248 | 20.5619 | 19.2496 | 18.3811 | 17.424 | 16.4693 | 15.6474 | 14.7569 | 13.9144 | 11.939 | 12.0616 | 12.8796
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Leading the Way | Thermal headroom (MW) | 29.4116 | 29.0672 | 28.0972 | 27.1622 | 25.7825 | 23.563 | 21.1131 | 19.372 | 17.842 | 16.1411 | 15.0853 | 14.375 | 13.6782 | 13.134 | 12.6524 | 12.2746 | 11.8179 | 12.7312 | 14.1933
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Steady Progression | Thermal headroom (MW) | 29.5835 | 29.506 | 29.1917 | 28.7789 | 28.0335 | 26.9461 | 25.9646 | 25.2643 | 24.5774 | 23.9225 | 23.5175 | 23.0717 | 22.5955 | 22.1373 | 21.6711 | 21.1667 | 19.1726 | 16.2747 | 15.8346
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | System Transformation | Thermal headroom (MW) | 29.51 | 29.3815 | 28.8449 | 28.1639 | 27.2427 | 25.7709 | 24.0992 | 23.0286 | 22.093 | 21.0234 | 20.4295 | 19.7288 | 19.0755 | 18.383 | 17.6616 | 16.967 | 14.6853 | 14.235 | 14.977
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | WPD Best View | Thermal headroom (MW) | 29.4116 | 29.0672 | 28.0972 | 27.1622 | 25.7825 | 23.563 | 21.1131 | 19.372 | 17.842 | 16.1411 | 15.0853 | 14.375 | 13.6782 | 13.134 | 12.6524 | 12.2746 | 11.8179 | 12.7312 | 14.1933
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Consumer Transformation | Thermal headroom (MW) | 3.7208 | 3.4555 | 3.2103 | 2.9049 | 2.5799 | 2.225 | 1.7585 | 1.3123 | 0.84426 | 0.36754 | -0.091335 | -0.54108 | -0.99945 | -1.7331 | -2.5387 | -3.3056 | -5.9251 | -6.7314 | -6.533
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Leading the Way | Thermal headroom (MW) | 3.7017 | 3.4496 | 3.2686 | 2.9889 | 2.6973 | 2.3453 | 1.8783 | 1.4504 | 0.96995 | 0.46657 | 0.0047858 | -0.34796 | -0.97785 | -1.7524 | -2.558 | -3.1831 | -4.7514 | -4.6908 | -3.6941
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Steady Progression | Thermal headroom (MW) | 3.8129 | 3.857 | 3.9684 | 3.9841 | 3.9957 | 3.9884 | 3.9509 | 3.8966 | 3.8297 | 3.7212 | 3.5963 | 3.3872 | 3.1465 | 2.8804 | 2.6004 | 2.2931 | 0.5088 | -1.1573 | -2.0159
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | System Transformation | Thermal headroom (MW) | 3.7543 | 3.7508 | 3.804 | 3.7778 | 3.7368 | 3.6575 | 3.4893 | 3.3142 | 3.096 | 2.8421 | 2.5562 | 2.2017 | 1.7983 | 1.3534 | 0.91789 | 0.48693 | -1.3742 | -2.9094 | -2.8709
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | WPD Best View | Thermal headroom (MW) | 3.7017 | 3.4496 | 3.2686 | 2.9889 | 2.6973 | 2.3453 | 1.8783 | 1.4504 | 0.96995 | 0.46657 | 0.0047858 | -0.34796 | -0.97785 | -1.7524 | -2.558 | -3.1831 | -4.7514 | -4.6908 | -3.6941
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Consumer Transformation | Thermal headroom (MW) | 12.7568 | 12.4107 | 11.2177 | 10.0665 | 8.8971 | 7.3365 | 5.7511 | 4.1324 | 2.14 | -0.32424 | -1.8449 | -3.4926 | -5.2439 | -6.8759 | -8.5284 | -10.0598 | -14.494 | -14.399 | -12.8815
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Leading the Way | Thermal headroom (MW) | 12.6955 | 12.2229 | 10.831 | 9.3888 | 7.9447 | 5.9974 | 4.1398 | 1.7846 | -1.114 | -4.1324 | -5.7817 | -7.1278 | -8.3506 | -9.4844 | -10.431 | -11.1425 | -12.3609 | -11.0985 | -8.6607
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Steady Progression | Thermal headroom (MW) | 12.8859 | 12.9055 | 12.4644 | 11.7981 | 11.2335 | 10.4469 | 9.8616 | 9.1935 | 8.4621 | 7.6712 | 7.267 | 6.7678 | 6.2676 | 5.7146 | 5.1278 | 4.5123 | 0.93911 | -3.4251 | -3.9836
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | System Transformation | Thermal headroom (MW) | 12.803 | 12.7516 | 11.8818 | 11.0311 | 10.1869 | 9.0862 | 8.0595 | 6.9356 | 5.7385 | 4.3892 | 3.5575 | 2.6795 | 1.7119 | 0.68504 | -0.42023 | -1.5062 | -5.5946 | -6.402 | -5.2069
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | WPD Best View | Thermal headroom (MW) | 12.6955 | 12.2229 | 10.831 | 9.3551 | 7.8084 | 5.7679 | 3.8086 | 1.7043 | -1.114 | -4.1324 | -5.7817 | -7.1278 | -8.3506 | -9.4844 | -10.431 | -11.1425 | -12.3609 | -11.0985 | -8.6607
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Consumer Transformation | Thermal headroom (MW) | 42.6274 | 41.2834 | 40.6113 | 39.1181 | 38.0969 | 36.3271 | 33.315 | 30.1587 | 26.8303 | 23.0705 | 19.8431 | 16.2155 | 12.5794 | 8.9992 | 5.1313 | 1.0307 | -11.8929 | -17.1394 | -15.9155
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Leading the Way | Thermal headroom (MW) | 42.4756 | 40.8849 | 40.1998 | 38.6583 | 37.627 | 35.82 | 32.5523 | 29.113 | 25.0754 | 21.313 | 17.8798 | 15.0265 | 12.1813 | 8.9872 | 5.6594 | 2.0423 | -4.9754 | -5.1626 | 0.55033
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Steady Progression | Thermal headroom (MW) | 42.957 | 42.9093 | 43.6538 | 43.5615 | 43.6834 | 43.769 | 43.5083 | 43.1954 | 42.723 | 42.0858 | 41.3633 | 40.4124 | 39.2776 | 37.9201 | 36.2872 | 34.0803 | 27.1932 | 19.7366 | 17.2592
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | System Transformation | Thermal headroom (MW) | 42.7388 | 42.3583 | 42.7563 | 42.297 | 42.3351 | 42.1694 | 41.3553 | 40.3006 | 39.0434 | 37.6466 | 36.2156 | 34.0099 | 31.9833 | 29.7051 | 27.282 | 24.9568 | 17.6209 | 12.608 | 13.6692
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | WPD Best View | Thermal headroom (MW) | 42.4756 | 40.8849 | 40.1998 | 38.6583 | 37.627 | 35.7913 | 32.551 | 29.113 | 25.0754 | 21.313 | 17.8798 | 15.0265 | 12.1813 | 8.8671 | 5.5166 | 1.9 | -5.1524 | -5.1626 | 0.55033
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Consumer Transformation | Thermal headroom (MW) | 16.8755 | 16.3608 | 15.9233 | 15.4766 | 15.1458 | 14.7275 | 14.1389 | 13.6077 | 13.1298 | 12.6709 | 12.1992 | 11.717 | 11.298 | 10.8086 | 9.9213 | 9.0238 | 6.1727 | 5.6028 | 6.1945
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Leading the Way | Thermal headroom (MW) | 16.8199 | 16.1968 | 15.7832 | 15.3353 | 15.0304 | 14.6119 | 13.9972 | 13.5165 | 13.1085 | 12.6995 | 12.2836 | 12.0293 | 11.8126 | 11.0611 | 10.2543 | 9.5176 | 7.9214 | 8.3125 | 9.8048
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Steady Progression | Thermal headroom (MW) | 17.0092 | 16.9625 | 17.0654 | 17.0357 | 17.1129 | 17.1674 | 17.2015 | 17.214 | 17.2537 | 17.2645 | 17.2484 | 17.1363 | 17.0229 | 16.8445 | 16.638 | 16.4041 | 15.1156 | 13.9241 | 13.093
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | System Transformation | Thermal headroom (MW) | 16.912 | 16.7353 | 16.6717 | 16.571 | 16.5848 | 16.6038 | 16.4913 | 16.3621 | 16.2453 | 16.0915 | 15.9291 | 15.69 | 15.3656 | 15.0057 | 14.6531 | 14.321 | 13.2192 | 11.769 | 12.0925
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | WPD Best View | Thermal headroom (MW) | 16.8199 | 16.1968 | 15.7832 | 15.3353 | 15.0304 | 14.6119 | 13.9972 | 13.5165 | 13.1085 | 12.6995 | 12.2836 | 12.0293 | 11.8126 | 11.0611 | 10.2543 | 9.5176 | 7.9214 | 8.3125 | 9.8048
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Consumer Transformation | Thermal headroom (MW) | 2.0085 | 2.0008 | 2.0596 | 2.0319 | 2.0311 | 2.0108 | 1.8318 | 1.6011 | 1.3381 | 1.0722 | 0.83119 | 0.58013 | 0.36142 | 0.22768 | 0.063252 | -0.18542 | -1.3645 | -1.5897 | -1.3621
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Leading the Way | Thermal headroom (MW) | 2.0029 | 2.001 | 2.0611 | 2.038 | 2.0412 | 2.0002 | 1.7984 | 1.5664 | 1.2974 | 1.0371 | 0.80424 | 0.6347 | 0.54018 | 0.35422 | 0.0044636 | -0.30923 | -0.97612 | -0.75698 | 0.020747
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Steady Progression | Thermal headroom (MW) | 2.0236 | 2.1002 | 2.2553 | 2.3238 | 2.4152 | 2.4986 | 2.5559 | 2.6283 | 2.6594 | 2.6356 | 2.5489 | 2.4322 | 2.2855 | 2.1269 | 1.9419 | 1.7308 | 0.70951 | 0.098466 | 0.039271
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | System Transformation | Thermal headroom (MW) | 2.0152 | 2.0762 | 2.217 | 2.266 | 2.3452 | 2.424 | 2.4618 | 2.4701 | 2.4106 | 2.2818 | 2.1119 | 1.8977 | 1.6513 | 1.3793 | 1.0929 | 0.8232 | -0.10421 | -0.17177 | 0.083264
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | WPD Best View | Thermal headroom (MW) | 2.0029 | 2.001 | 2.0611 | 2.038 | 2.0412 | 1.9722 | 1.7971 | 1.5664 | 1.2974 | 1.0371 | 0.80424 | 0.6347 | 0.54018 | 0.35422 | 0.0044636 | -0.30923 | -0.97612 | -0.75698 | 0.020747
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Consumer Transformation | Thermal headroom (MW) | 5.7945 | 5.36 | 5.1381 | 4.8794 | 4.6721 | 4.4202 | 3.857 | 3.3584 | 2.8605 | 2.0098 | 1.5236 | 0.84336 | 0.059922 | -1.0172 | -2.1791 | -3.2996 | -7.8756 | -9.9392 | -10.1912
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Leading the Way | Thermal headroom (MW) | 5.7685 | 5.2653 | 5.0552 | 4.799 | 4.6268 | 4.4013 | 3.8464 | 3.3951 | 2.5765 | 2.0947 | 1.6041 | 1.2161 | 0.45877 | -0.49289 | -1.3797 | -2.5456 | -5.1848 | -5.962 | -4.9366
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Steady Progression | Thermal headroom (MW) | 5.8427 | 5.7823 | 5.9371 | 5.993 | 6.0854 | 6.1671 | 6.2232 | 6.2687 | 6.3086 | 6.3479 | 6.3419 | 6.2803 | 6.2089 | 6.0684 | 5.9199 | 5.3788 | 4.262 | 2.5185 | 1.9861
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | System Transformation | Thermal headroom (MW) | 5.8159 | 5.6641 | 5.735 | 5.7534 | 5.8313 | 5.8914 | 5.8684 | 5.8573 | 5.8105 | 5.7623 | 5.6876 | 5.1802 | 4.9543 | 4.6913 | 4.4184 | 4.1481 | 2.3176 | 0.43945 | 0.21424
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | WPD Best View | Thermal headroom (MW) | 5.7685 | 5.2653 | 5.0552 | 4.799 | 4.6268 | 4.4013 | 3.8464 | 3.3951 | 2.5765 | 2.0947 | 1.6041 | 1.2161 | 0.45877 | -0.49289 | -1.3797 | -2.5456 | -5.1848 | -5.962 | -4.9366
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Consumer Transformation | Thermal headroom (MW) | 5.9094 | 5.6332 | 5.5512 | 5.3511 | 5.1163 | 4.4112 | 2.7384 | 1.0222 | -0.7958 | -3.029 | -5.0037 | -6.9994 | -8.9843 | -10.8798 | -12.6485 | -14.9715 | -19.7177 | -22.9563 | -22.4511
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Leading the Way | Thermal headroom (MW) | 5.8765 | 5.5316 | 5.5033 | 5.3091 | 5.0773 | 4.3577 | 2.3816 | 0.32293 | -2.271 | -4.5979 | -6.908 | -8.8404 | -10.6306 | -12.2281 | -13.9462 | -16.262 | -18.5578 | -18.8061 | -17.1906
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Steady Progression | Thermal headroom (MW) | 5.9789 | 5.9932 | 6.2193 | 6.2659 | 6.2981 | 6.2534 | 5.7875 | 5.2273 | 4.5899 | 3.8754 | 3.0805 | 2.2297 | 1.3295 | 0.31154 | -0.75408 | -2.2397 | -4.425 | -8.3012 | -10.055
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | System Transformation | Thermal headroom (MW) | 5.9348 | 5.8835 | 6.0206 | 6.0493 | 6.0536 | 5.9325 | 5.0316 | 4.0472 | 2.9532 | 1.8117 | 0.56145 | -1.1331 | -2.6187 | -4.1093 | -5.6384 | -7.1853 | -8.9828 | -11.4933 | -11.5595
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | WPD Best View | Thermal headroom (MW) | 5.8765 | 5.5316 | 5.5033 | 5.3091 | 5.0773 | 4.3577 | 2.3816 | 0.32293 | -2.271 | -4.5979 | -6.908 | -8.8404 | -10.6306 | -12.4256 | -14.1811 | -16.262 | -18.5578 | -18.8061 | -17.1906
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Consumer Transformation | Thermal headroom (MW) | 8.4044 | 8.0401 | 8.0979 | 7.5284 | 7.4293 | 7.1159 | 6.8593 | 6.3872 | 5.8781 | 5.5023 | 5.1413 | 4.7433 | 4.3151 | 3.9474 | 3.5255 | 3.1866 | 1.9612 | 1.7487 | 2.1346
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Leading the Way | Thermal headroom (MW) | 8.3976 | 7.9272 | 7.9225 | 7.315 | 7.2107 | 6.9011 | 6.6292 | 6.0896 | 5.5704 | 5.1786 | 4.8141 | 4.5228 | 4.2567 | 3.9426 | 3.6379 | 3.3858 | 2.8125 | 3.0377 | 3.8854
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Steady Progression | Thermal headroom (MW) | 8.4496 | 8.3136 | 8.5448 | 8.3655 | 8.3041 | 8.3643 | 8.3732 | 8.3747 | 8.3675 | 8.36 | 8.3672 | 8.3288 | 8.2544 | 8.1912 | 8.0352 | 7.8676 | 7.1174 | 6.3768 | 6.2104
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | System Transformation | Thermal headroom (MW) | 8.4278 | 8.1832 | 8.3952 | 7.9826 | 8.0101 | 8.0039 | 8.0152 | 7.8912 | 7.7944 | 7.7242 | 7.6469 | 7.5244 | 7.446 | 7.2558 | 7.0458 | 6.8825 | 6.0093 | 5.5722 | 5.9001
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | WPD Best View | Thermal headroom (MW) | 8.3976 | 7.9272 | 7.9225 | 7.315 | 7.2107 | 6.9011 | 6.6292 | 6.0896 | 5.5704 | 5.1786 | 4.8141 | 4.5228 | 4.2567 | 3.9426 | 3.6379 | 3.3858 | 2.8125 | 3.0377 | 3.8854
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Consumer Transformation | Thermal headroom (MW) | 10.4144 | 10.2251 | 9.813 | 9.3099 | 8.7811 | 8.0525 | 7.2073 | 6.373 | 5.4495 | 4.4356 | 3.5491 | 2.4522 | 1.3143 | 0.22847 | -0.95091 | -2.0621 | -5.8282 | -7.0943 | -7.0789
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Leading the Way | Thermal headroom (MW) | 10.385 | 10.1985 | 9.7345 | 9.1736 | 8.5536 | 7.7684 | 6.8473 | 5.8701 | 4.8407 | 3.5816 | 2.6242 | 1.6791 | 0.71278 | -0.2309 | -1.1452 | -1.936 | -4.1472 | -4.3197 | -2.7177
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Steady Progression | Thermal headroom (MW) | 10.5039 | 10.5609 | 10.5208 | 10.3672 | 10.2272 | 10.0261 | 9.8454 | 9.6883 | 9.443 | 9.1551 | 8.9567 | 8.7505 | 8.481 | 8.1401 | 7.6618 | 7.1517 | 4.6491 | 2.0768 | 1.4534
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | System Transformation | Thermal headroom (MW) | 10.4422 | 10.4703 | 10.3104 | 10.0652 | 9.8312 | 9.4931 | 9.1719 | 8.8075 | 8.3659 | 7.8836 | 7.5647 | 7.1583 | 6.6857 | 6.1196 | 5.4451 | 4.8009 | 1.5532 | 0.085058 | 0.38754
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | WPD Best View | Thermal headroom (MW) | 10.385 | 10.1985 | 9.7345 | 9.1736 | 8.5536 | 7.7684 | 6.8473 | 5.8701 | 4.8407 | 3.5816 | 2.6242 | 1.6791 | 0.71278 | -0.2309 | -1.1452 | -1.936 | -4.1472 | -4.3197 | -2.7177
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Consumer Transformation | Thermal headroom (MW) | -14.3212 | -17.6979 | -21 | -28.941 | -34.0598 | -40.2899 | -47.7977 | -55.5136 | -63.4103 | -74.5539 | -81.8055 | -89.8878 | -97.1053 | -104.0411 | -112.3524 | -119.734 | -148.5835 | -158.1231 | -153.6305
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Leading the Way | Thermal headroom (MW) | -15.0129 | -18.9291 | -22.2036 | -32.0103 | -37.1506 | -43.6913 | -51.3607 | -59.2936 | -70.7543 | -79.7039 | -86.4635 | -92.4162 | -97.4535 | -103.2013 | -109.2759 | -116.5556 | -132.2356 | -129.9204 | -118.7071
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Steady Progression | Thermal headroom (MW) | -13.185 | -13.5253 | -13.0092 | -16.6778 | -17.9019 | -18.927 | -20.2047 | -21.8318 | -23.7275 | -26.0222 | -28.1722 | -31.3555 | -34.4467 | -37.8921 | -41.6374 | -48.4648 | -70.8353 | -92.147 | -96.9871
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | System Transformation | Thermal headroom (MW) | -13.9875 | -14.9875 | -15.5915 | -20.9158 | -22.8578 | -24.6616 | -27.0887 | -30.439 | -34.3327 | -38.5864 | -42.4761 | -49.8446 | -54.9527 | -60.7977 | -66.5293 | -72.0639 | -97.5444 | -108.5821 | -107.9238
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | WPD Best View | Thermal headroom (MW) | -15.0129 | -18.9291 | -22.2036 | -32.0361 | -37.255 | -43.8671 | -51.6144 | -59.3551 | -70.7543 | -79.7039 | -86.4635 | -92.4162 | -97.4535 | -103.2013 | -109.2759 | -116.5556 | -132.2356 | -129.9204 | -118.7071
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Consumer Transformation | Thermal headroom (MW) | 9.7822 | 9.2839 | 8.7257 | 7.8894 | 7.0672 | 6.3679 | 5.5519 | 4.6905 | 3.9091 | 2.4316 | 1.698 | 0.88719 | 0.21921 | -0.36893 | -1.3993 | -2.469 | -6.5456 | -7.9209 | -7.5587
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Leading the Way | Thermal headroom (MW) | 9.7184 | 9.1167 | 8.6046 | 7.6402 | 6.7145 | 6.0331 | 5.2169 | 4.3816 | 3.2758 | 2.0376 | 1.4016 | 0.88605 | 0.53825 | -0.169 | -1.1558 | -2.2797 | -4.3398 | -4.3134 | -3.2478
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Steady Progression | Thermal headroom (MW) | 9.9064 | 9.8171 | 9.7911 | 9.4136 | 9.1253 | 9.0542 | 8.9395 | 8.7345 | 8.5652 | 8.1588 | 7.9163 | 7.5824 | 7.2194 | 6.8259 | 6.3773 | 5.5654 | 3.2805 | 1.116 | 0.55293
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | System Transformation | Thermal headroom (MW) | 9.8197 | 9.6319 | 9.4358 | 8.9432 | 8.4839 | 8.3511 | 8.1189 | 7.7609 | 7.4273 | 6.7156 | 6.2917 | 5.3978 | 4.8482 | 4.2396 | 3.6072 | 3.0269 | 0.72517 | -0.42004 | -0.557
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | WPD Best View | Thermal headroom (MW) | 9.7184 | 9.1167 | 8.6046 | 7.6402 | 6.7145 | 6.0331 | 5.2169 | 4.3816 | 3.2758 | 2.0376 | 1.4016 | 0.88605 | 0.53825 | -0.169 | -1.1558 | -2.2797 | -4.3398 | -4.3134 | -3.2478
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Consumer Transformation | Thermal headroom (MW) | 3.9261 | 3.6898 | 3.4751 | 3.1238 | 2.8051 | 2.4516 | 2.0367 | 1.6386 | 1.2358 | 0.4648 | 0.055006 | -0.30695 | -0.62356 | -0.95131 | -1.2282 | -1.4631 | -2.7709 | -3.5587 | -3.3552
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Leading the Way | Thermal headroom (MW) | 3.8972 | 3.6606 | 3.412 | 3.1272 | 2.8269 | 2.4616 | 2.0564 | 1.6667 | 0.89477 | 0.4703 | 0.080352 | -0.20434 | -0.47957 | -0.70868 | -0.83402 | -1.2627 | -2.118 | -1.974 | -1.6814
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Steady Progression | Thermal headroom (MW) | 4.0055 | 4.0113 | 4.0719 | 4.0521 | 3.9557 | 3.9197 | 3.8693 | 3.8043 | 3.7064 | 3.5956 | 3.4466 | 3.2351 | 3.002 | 2.7394 | 2.4533 | 1.7941 | 0.11421 | -1.5043 | -1.9717
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | System Transformation | Thermal headroom (MW) | 3.9611 | 3.916 | 3.9282 | 3.7968 | 3.7124 | 3.6194 | 3.4705 | 3.2822 | 3.0632 | 2.8117 | 2.5373 | 1.8334 | 1.4373 | 1.0235 | 0.61221 | 0.21212 | -1.7189 | -2.5205 | -2.7228
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | WPD Best View | Thermal headroom (MW) | 3.8972 | 3.6606 | 3.412 | 3.1272 | 2.8269 | 2.4616 | 2.0564 | 1.6667 | 0.89477 | 0.4703 | 0.080352 | -0.20434 | -0.47957 | -0.70868 | -0.83402 | -1.2627 | -2.118 | -1.974 | -1.6814
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Consumer Transformation | Thermal headroom (MW) | 7.0038 | 6.947 | 7.0203 | 5.2795 | 5.2929 | 5.1808 | 5.0078 | 4.6487 | 4.3366 | 4.0869 | 3.8177 | 3.5651 | 3.3292 | 3.0659 | 2.8304 | 2.6444 | 2.2907 | 2.7976 | 3.6021
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Leading the Way | Thermal headroom (MW) | 6.8754 | 6.7308 | 6.8134 | 4.4144 | 4.4203 | 4.2937 | 4.1048 | 3.8453 | 3.4644 | 3.3045 | 3.1509 | 3.0302 | 2.8554 | 2.7076 | 2.5622 | 2.45 | 2.6368 | 3.5388 | 4.7368
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Steady Progression | Thermal headroom (MW) | 7.1175 | 7.1234 | 7.3355 | 6.0682 | 6.1379 | 6.1983 | 6.1522 | 6.0921 | 6.0214 | 5.9955 | 5.9525 | 5.9016 | 5.8315 | 5.7728 | 5.7166 | 5.5906 | 5.1846 | 4.5461 | 4.9361
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | System Transformation | Thermal headroom (MW) | 7.0201 | 6.9996 | 7.1141 | 5.3826 | 5.4609 | 5.5323 | 5.5773 | 5.4068 | 5.2571 | 5.1752 | 5.0856 | 5.0012 | 4.9169 | 4.7709 | 4.5962 | 4.4572 | 3.7971 | 3.9664 | 4.7321
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | WPD Best View | Thermal headroom (MW) | 6.8754 | 6.7308 | 6.8134 | 4.4144 | 4.4203 | 4.2937 | 4.1048 | 3.8453 | 3.4644 | 3.3045 | 3.1509 | 3.0302 | 2.8554 | 2.7076 | 2.5622 | 2.45 | 2.6368 | 3.5388 | 4.7368
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Consumer Transformation | Thermal headroom (MW) | 7.0658 | 6.7964 | 6.6431 | 6.2801 | 5.5474 | 4.8821 | 3.9614 | 3.168 | 2.2974 | 1.3852 | 0.43777 | -1.0237 | -2.1519 | -3.1772 | -4.5909 | -5.5894 | -9.9782 | -11.4107 | -11.199
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Leading the Way | Thermal headroom (MW) | 6.9937 | 6.7191 | 6.5959 | 5.8382 | 5.4719 | 4.7979 | 3.903 | 3.1343 | 2.276 | 1.3772 | 0.41842 | -0.71468 | -1.5319 | -2.3243 | -3.4597 | -4.1872 | -6.826 | -7.3898 | -5.842
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Steady Progression | Thermal headroom (MW) | 7.1531 | 7.1681 | 7.3363 | 7.2952 | 7.2903 | 7.3017 | 7.2673 | 7.2435 | 7.1871 | 7.0656 | 6.9336 | 6.4199 | 6.2517 | 5.9924 | 5.7035 | 5.4028 | 3.1417 | 0.34568 | -0.38974
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | System Transformation | Thermal headroom (MW) | 7.0701 | 7.0493 | 7.1785 | 7.1127 | 7.0264 | 6.9716 | 6.8326 | 6.6829 | 6.1409 | 5.9241 | 5.6572 | 5.3787 | 5.0076 | 4.2639 | 3.8884 | 3.5336 | -0.32916 | -2.3881 | -2.4299
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | WPD Best View | Thermal headroom (MW) | 6.9937 | 6.7191 | 6.5959 | 5.8382 | 5.4719 | 4.7979 | 3.903 | 3.1343 | 2.276 | 1.3772 | 0.41842 | -0.71468 | -1.5319 | -2.3243 | -3.4597 | -4.1872 | -6.826 | -7.3898 | -5.842
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Consumer Transformation | Thermal headroom (MW) | 9.382 | 8.761 | 8.3909 | 7.8468 | 7.3169 | 6.5487 | 5.5748 | 4.6814 | 3.7759 | 2.9088 | 2.0599 | 1.2299 | 0.49348 | -0.12396 | -1.2272 | -2.2823 | -6.0337 | -7.1228 | -6.8082
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Leading the Way | Thermal headroom (MW) | 9.2784 | 8.5676 | 8.2143 | 7.6394 | 7.0916 | 6.3444 | 5.4051 | 4.5888 | 3.6999 | 2.8511 | 2.146 | 1.7142 | 1.4064 | 0.87473 | 0.0088232 | -0.72593 | -2.9621 | -3.1374 | -1.7863
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Steady Progression | Thermal headroom (MW) | 9.5234 | 9.3397 | 9.3805 | 9.2648 | 9.1345 | 9.0445 | 8.9506 | 8.8431 | 8.7243 | 8.5797 | 8.367 | 8.1134 | 7.8203 | 7.4902 | 7.1497 | 6.7738 | 4.8993 | 3.737 | 3.4087
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | System Transformation | Thermal headroom (MW) | 9.4113 | 9.1112 | 9.0592 | 8.8526 | 8.6517 | 8.4887 | 8.2756 | 8.0586 | 7.7913 | 7.4802 | 7.1003 | 6.689 | 6.2349 | 5.7597 | 5.299 | 4.8746 | 3.4244 | 2.8408 | 2.9784
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | WPD Best View | Thermal headroom (MW) | 9.2784 | 8.5676 | 8.2143 | 7.6394 | 7.0916 | 6.3444 | 5.4051 | 4.5888 | 3.6999 | 2.8511 | 2.146 | 1.7142 | 1.4064 | 0.87473 | 0.0088232 | -0.72593 | -2.9621 | -3.1374 | -1.7863
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Consumer Transformation | Thermal headroom (MW) | 5.7459 | 5.5785 | 5.4109 | 5.1707 | 4.8916 | 4.5621 | 4.0959 | 3.6067 | 3.0943 | 2.2044 | 1.6904 | 1.0872 | 0.49599 | -0.019994 | -0.43618 | -0.78819 | -2.6114 | -3.917 | -4.0055
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Leading the Way | Thermal headroom (MW) | 5.7416 | 5.5842 | 5.4541 | 5.2242 | 4.9452 | 4.6181 | 4.1539 | 3.6629 | 2.7626 | 2.178 | 1.6236 | 1.0633 | 0.57466 | 0.22424 | 0.025134 | -0.44758 | -1.9801 | -2.1227 | -1.6122
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Steady Progression | Thermal headroom (MW) | 5.7948 | 5.8044 | 5.8555 | 5.8333 | 5.7953 | 5.7428 | 5.6548 | 5.5388 | 5.3806 | 5.1921 | 4.9678 | 4.6844 | 4.3537 | 3.9976 | 3.6028 | 2.8211 | 0.29817 | -1.5122 | -2.0328
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | System Transformation | Thermal headroom (MW) | 5.7759 | 5.7681 | 5.798 | 5.7457 | 5.6767 | 5.5791 | 5.4141 | 5.1948 | 4.9394 | 4.6337 | 4.2659 | 3.4581 | 2.9517 | 2.4034 | 1.8062 | 1.1719 | -1.4977 | -2.4381 | -2.757
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | WPD Best View | Thermal headroom (MW) | 5.7416 | 5.5842 | 5.4541 | 5.2242 | 4.9452 | 4.6181 | 4.1539 | 3.6629 | 2.7626 | 2.178 | 1.6236 | 1.0633 | 0.57466 | 0.22424 | 0.025134 | -0.44758 | -1.9801 | -2.1227 | -1.6122
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Consumer Transformation | Thermal headroom (MW) | 4.2659 | 3.9458 | 3.6891 | 3.3493 | 2.9719 | 2.4253 | 1.8273 | 1.2425 | 0.69816 | -0.12789 | -0.5794 | -1.0909 | -1.4889 | -2.0064 | -2.7151 | -3.3652 | -5.9384 | -6.8289 | -6.4789
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Leading the Way | Thermal headroom (MW) | 4.2222 | 3.8585 | 3.627 | 3.2597 | 2.8627 | 2.3143 | 1.7106 | 1.1324 | 0.22318 | -0.24459 | -0.60593 | -0.95255 | -1.2393 | -1.8529 | -2.4964 | -3.4085 | -4.6743 | -4.4684 | -3.8478
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Steady Progression | Thermal headroom (MW) | 4.3527 | 4.294 | 4.3154 | 4.2458 | 4.1664 | 4.0805 | 3.995 | 3.8803 | 3.751 | 3.6311 | 3.4837 | 3.2457 | 3.0312 | 2.7891 | 2.5281 | 1.8716 | 0.51364 | -0.92329 | -1.5639
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | System Transformation | Thermal headroom (MW) | 4.289 | 4.1596 | 4.1142 | 3.9948 | 3.8493 | 3.7014 | 3.4972 | 3.2503 | 3.011 | 2.7683 | 2.5132 | 1.7789 | 1.4108 | 1.0387 | 0.67093 | 0.33589 | -1.1965 | -2.7424 | -2.9726
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | WPD Best View | Thermal headroom (MW) | 4.2222 | 3.8585 | 3.627 | 3.2597 | 2.8627 | 2.3143 | 1.7106 | 1.1324 | 0.22318 | -0.24459 | -0.60593 | -0.95255 | -1.2393 | -1.8529 | -2.4964 | -3.4085 | -4.6743 | -4.4684 | -3.8478
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Consumer Transformation | Thermal headroom (MW) | 13.791 | 11.0788 | 9.057 | 6.3894 | 3.8371 | 0.53337 | -4.2632 | -8.9448 | -13.9037 | -19.9063 | -26.0723 | -34.5806 | -41.6569 | -48.1851 | -55.6016 | -62.2983 | -89.1214 | -97.0481 | -94.7688
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Leading the Way | Thermal headroom (MW) | 13.276 | 9.79 | 8.8601 | 5.9347 | 3.6543 | 0.38657 | -4.5221 | -9.1441 | -14.5805 | -20.9806 | -27.4272 | -35.1612 | -42.084 | -48.2026 | -54.5013 | -60.3644 | -76.6834 | -76.1396 | -65.3142
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Steady Progression | Thermal headroom (MW) | 14.381 | 14.3528 | 15.3105 | 14.292 | 14.3408 | 14.3478 | 14.168 | 13.8375 | 13.2744 | 12.1835 | 10.6916 | 7.9449 | 5.3018 | 2.6341 | -0.33877 | -3.824 | -23.1469 | -38.9748 | -43.1402
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | System Transformation | Thermal headroom (MW) | 14.042 | 13.1296 | 13.1164 | 12.4266 | 12.1787 | 11.7402 | 10.8028 | 9.5837 | 7.7131 | 5.3572 | 2.3078 | -2.389 | -6.684 | -11.2417 | -16.0466 | -20.8 | -41.8649 | -50.2953 | -48.2508
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | WPD Best View | Thermal headroom (MW) | 14.0213 | 13.0783 | 13.0052 | 12.2375 | 11.8932 | 11.2673 | 10.0863 | 8.6031 | 6.44 | 3.7968 | 0.67088 | -3.8969 | -7.8693 | -12.0505 | -16.4237 | -20.9662 | -41.3866 | -50.05 | -47.7482
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Consumer Transformation | Thermal headroom (MW) | 8.8227 | 8.2631 | 7.9885 | 7.5902 | 7.1652 | 6.3229 | 5.2563 | 4.2757 | 3.2675 | 2.3338 | 1.4347 | -0.87104 | -2.0116 | -3.1172 | -4.5869 | -5.7657 | -9.3449 | -9.8275 | -9.0713
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Leading the Way | Thermal headroom (MW) | 8.7612 | 8.0596 | 7.8125 | 7.3899 | 6.9315 | 6.0938 | 5.004 | 4.0479 | 3.0321 | 2.1198 | 1.3356 | -0.64728 | -1.3253 | -1.99 | -2.993 | -3.5585 | -5.3784 | -5.22 | -3.9135
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Steady Progression | Thermal headroom (MW) | 8.9033 | 8.7204 | 8.8056 | 8.707 | 8.5971 | 8.4804 | 8.378 | 8.2456 | 8.0836 | 7.9109 | 7.6939 | 7.0497 | 6.7047 | 6.3128 | 5.8866 | 5.4831 | 3.7707 | 3.1643 | 3.3784
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | System Transformation | Thermal headroom (MW) | 8.8406 | 8.5366 | 8.5101 | 8.3708 | 8.2131 | 8.0179 | 7.7946 | 7.541 | 7.2438 | 6.9482 | 6.6179 | 5.6179 | 5.1113 | 4.5506 | 4.0229 | 3.6106 | 2.673 | 2.7815 | 3.4361
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | WPD Best View | Thermal headroom (MW) | 8.8406 | 8.5366 | 8.5101 | 8.3708 | 8.2131 | 8.0179 | 7.7946 | 7.541 | 7.2438 | 6.9482 | 6.6179 | 5.6179 | 5.1113 | 4.5506 | 4.0229 | 3.6106 | 2.673 | 2.7815 | 3.4361
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Consumer Transformation | Thermal headroom (MW) | 5.6243 | 4.8979 | 3.73 | 3.38 | 3.223 | 2.9506 | 2.431 | 1.8704 | 1.2876 | 0.70536 | 0.16331 | -0.42297 | -0.92044 | -1.486 | -1.96 | -2.3331 | -6.6954 | -7.7677 | -7.6954
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Leading the Way | Thermal headroom (MW) | 5.6237 | 3.6187 | 3.4755 | 3.0361 | 2.8783 | 2.6302 | 2.0879 | 1.5429 | 0.9476 | 0.33685 | -0.20273 | -0.61197 | -1.0711 | -1.4258 | -1.8374 | -2.5865 | -6.2825 | -6.2689 | -4.515
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Steady Progression | Thermal headroom (MW) | 5.6787 | 5.3052 | 5.4478 | 4.3206 | 4.3601 | 4.3746 | 4.3497 | 4.3031 | 4.2196 | 4.0722 | 3.8614 | 3.585 | 3.2307 | 2.8363 | 2.4284 | 1.9797 | -0.91808 | -2.4946 | -2.7488
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | System Transformation | Thermal headroom (MW) | 5.6601 | 5.0933 | 4.1182 | 3.9443 | 3.9956 | 3.9423 | 3.8403 | 3.6788 | 3.4458 | 3.1456 | 2.7542 | 2.2815 | 1.7449 | 1.137 | 0.51942 | -0.065893 | -3.2259 | -3.6287 | -3.2655
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | WPD Best View | Thermal headroom (MW) | 5.6516 | 5.0568 | 4.0413 | 3.8189 | 3.8144 | 3.6996 | 3.5237 | 3.2146 | 2.829 | 2.4491 | 2.024 | 1.6081 | 1.1975 | 0.81677 | 0.34538 | -0.10043 | -2.4896 | -3.7472 | -3.2853
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Consumer Transformation | Thermal headroom (MW) | 6.3647 | 5.6507 | 5.3707 | 4.6802 | 4.1797 | 3.4046 | 2.33 | 1.2511 | 0.13383 | -1.3394 | -2.4328 | -3.665 | -4.7586 | -5.7 | -6.5492 | -7.3038 | -11.787 | -13.6605 | -13.517
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Leading the Way | Thermal headroom (MW) | 5.93 | 5.6116 | 5.3358 | 4.6049 | 4.0963 | 3.3305 | 2.2345 | 1.1474 | -0.3551 | -1.4945 | -2.5069 | -3.3522 | -4.0549 | -4.66 | -4.9594 | -5.8812 | -8.6288 | -8.9916 | -7.8361
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Steady Progression | Thermal headroom (MW) | 6.4426 | 6.4795 | 6.2068 | 5.9892 | 5.8545 | 5.7822 | 5.6686 | 5.5226 | 5.2645 | 4.9735 | 4.6157 | 4.1689 | 3.6255 | 3.0741 | 2.4999 | 1.4677 | -1.7578 | -4.1147 | -4.612
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | System Transformation | Thermal headroom (MW) | 6.4129 | 5.9905 | 6.0502 | 5.6806 | 5.5327 | 5.3845 | 5.1888 | 4.8602 | 4.4307 | 3.9394 | 3.3528 | 2.2933 | 1.5123 | 0.70449 | -0.078925 | -0.89437 | -4.2168 | -5.3242 | -5.3405
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | WPD Best View | Thermal headroom (MW) | 6.4025 | 5.9732 | 6.0114 | 5.6202 | 5.4434 | 5.2641 | 4.9824 | 4.5914 | 4.1104 | 3.5827 | 2.9856 | 1.958 | 1.2652 | 0.59042 | -0.018842 | -0.72899 | -3.6247 | -4.6095 | -4.5466
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Consumer Transformation | Thermal headroom (MW) | 11.5525 | 11.6485 | 11.8242 | 11.9194 | 12.0058 | 12.0463 | 12.081 | 12.1077 | 12.1036 | 12.0392 | 11.9517 | 11.7226 | 11.6489 | 11.6101 | 11.6181 | 11.5459 | 11.3289 | 11.5729 | 11.986
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Leading the Way | Thermal headroom (MW) | 11.5508 | 11.6211 | 11.8172 | 11.9082 | 11.9908 | 12.0297 | 12.0649 | 12.0846 | 12.0518 | 11.9705 | 11.9014 | 11.6975 | 11.6844 | 11.6522 | 11.538 | 11.468 | 11.517 | 11.9977 | 12.6067
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Steady Progression | Thermal headroom (MW) | 11.5562 | 11.6604 | 11.8654 | 11.9489 | 12.0507 | 12.1522 | 12.2476 | 12.3382 | 12.4249 | 12.5076 | 12.5891 | 12.593 | 12.5782 | 12.5456 | 12.478 | 12.4079 | 12.0322 | 12.0588 | 12.272
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | System Transformation | Thermal headroom (MW) | 11.5551 | 11.6532 | 11.835 | 11.9359 | 12.0371 | 12.1306 | 12.2205 | 12.3052 | 12.3795 | 12.4521 | 12.4637 | 12.3539 | 12.2517 | 12.1376 | 12.0265 | 11.9326 | 11.8477 | 12.1083 | 12.4827
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | WPD Best View | Thermal headroom (MW) | 11.5551 | 11.6532 | 11.835 | 11.9359 | 12.0371 | 12.1306 | 12.2205 | 12.3052 | 12.3795 | 12.4408 | 12.4336 | 12.3284 | 12.2517 | 12.1376 | 12.0265 | 11.9326 | 11.8477 | 12.1083 | 12.4827
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Consumer Transformation | Thermal headroom (MW) | 2.4248 | 2.2226 | 2.1701 | 1.4951 | 0.87252 | 0.56822 | -0.038546 | -0.63614 | -1.2499 | -2.0833 | -3.5008 | -5.6489 | -7.5374 | -9.3612 | -11.6179 | -13.4377 | -20.8023 | -23.4478 | -23.4181
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Leading the Way | Thermal headroom (MW) | 2.4157 | 2.2021 | 2.2085 | 1.122 | 0.90123 | 0.60406 | 0.002539 | -0.54616 | -1.1925 | -2.3561 | -3.9422 | -5.9096 | -7.7094 | -9.4622 | -11.4854 | -12.9419 | -17.4541 | -18.0803 | -15.2498
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Steady Progression | Thermal headroom (MW) | 2.5083 | 2.6942 | 3.0873 | 2.9247 | 3.0251 | 3.1557 | 3.2437 | 3.3043 | 3.3542 | 3.3633 | 3.3611 | 2.9025 | 2.7661 | 2.5965 | 2.388 | 2.1586 | -3.074 | -8.8662 | -10.4185
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | System Transformation | Thermal headroom (MW) | 2.4686 | 2.6122 | 2.9179 | 2.5963 | 2.7112 | 2.7818 | 2.789 | 2.7256 | 2.2673 | 2.1453 | 1.972 | 1.7352 | 1.439 | 0.52305 | -0.59702 | -1.787 | -9.2877 | -13.063 | -13.0154
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | WPD Best View | Thermal headroom (MW) | 2.4634 | 2.6039 | 2.8995 | 2.5659 | 2.6662 | 2.7207 | 2.7097 | 2.6243 | 2.1471 | 2.0119 | 1.839 | 1.6227 | 1.3726 | 0.36205 | -0.77497 | -1.9779 | -9.3879 | -13.0584 | -12.9634
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Consumer Transformation | Thermal headroom (MW) | 4.9232 | 4.7393 | 4.5878 | 4.3773 | 4.1362 | 3.8575 | 3.4559 | 3.0302 | 2.6062 | 1.9246 | 1.2443 | 0.52373 | -0.19973 | -0.75455 | -1.5623 | -2.3296 | -4.8252 | -5.8624 | -5.8181
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Leading the Way | Thermal headroom (MW) | 4.9053 | 4.7242 | 4.603 | 4.4055 | 4.1855 | 3.9096 | 3.511 | 3.109 | 2.6593 | 1.8493 | 1.0421 | 0.26429 | -0.87753 | -1.7096 | -2.469 | -3.1387 | -4.5738 | -4.6232 | -3.683
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Steady Progression | Thermal headroom (MW) | 4.9768 | 4.9859 | 5.061 | 5.0732 | 5.0676 | 5.0431 | 4.9953 | 4.9276 | 4.8368 | 4.5752 | 4.2737 | 3.8982 | 3.4815 | 3.1559 | 2.8132 | 2.4492 | 0.61037 | -0.95203 | -1.594
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | System Transformation | Thermal headroom (MW) | 4.9463 | 4.9288 | 4.979 | 4.9534 | 4.915 | 4.8522 | 4.736 | 4.5884 | 4.399 | 3.9325 | 3.3851 | 2.7798 | 2.13 | 1.6535 | 1.1519 | 0.63264 | -1.1521 | -2.0377 | -1.9391
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | WPD Best View | Thermal headroom (MW) | 4.9463 | 4.9288 | 4.979 | 4.9534 | 4.915 | 4.8522 | 4.736 | 4.5884 | 4.399 | 3.9325 | 3.3851 | 2.7798 | 2.13 | 1.6535 | 1.1519 | 0.63264 | -1.1521 | -2.0377 | -1.9391
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Consumer Transformation | Thermal headroom (MW) | 2.7287 | 2.5053 | 2.3201 | 2.0507 | 1.7453 | 1.4596 | 0.99423 | 0.55385 | 0.04724 | -0.51844 | -1.092 | -1.7996 | -2.5804 | -3.3013 | -4.0412 | -4.7709 | -7.3149 | -8.0888 | -7.9173
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Leading the Way | Thermal headroom (MW) | 2.7183 | 2.5033 | 2.384 | 2.1572 | 1.8643 | 1.5701 | 1.0653 | 0.64838 | 0.12052 | -0.49748 | -1.1368 | -1.8084 | -2.4954 | -3.184 | -3.8801 | -4.4698 | -6.0071 | -6.0005 | -4.9396
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Steady Progression | Thermal headroom (MW) | 2.7984 | 2.855 | 2.9866 | 3.0045 | 3.0237 | 3.0353 | 3.0305 | 3.0033 | 2.9543 | 2.9032 | 2.8538 | 2.7363 | 2.5606 | 2.3724 | 2.1103 | 1.8183 | -0.04024 | -2.1786 | -2.7553
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | System Transformation | Thermal headroom (MW) | 2.74 | 2.7642 | 2.8292 | 2.829 | 2.7853 | 2.7305 | 2.6418 | 2.5283 | 2.3821 | 2.2276 | 2.0356 | 1.761 | 1.4343 | 1.0594 | 0.59711 | 0.12138 | -2.3988 | -3.6465 | -3.5084
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | WPD Best View | Thermal headroom (MW) | 2.74 | 2.7642 | 2.8292 | 2.829 | 2.7853 | 2.7305 | 2.6418 | 2.5283 | 2.3821 | 2.2276 | 2.0356 | 1.761 | 1.4343 | 1.0594 | 0.59711 | 0.12138 | -2.3988 | -3.6465 | -3.5084
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Consumer Transformation | Thermal headroom (MW) | 2.1114 | 1.9256 | 1.7889 | 1.5841 | 1.3365 | 1.0283 | 0.63047 | 0.27818 | -0.1094 | -0.51724 | -1.0295 | -1.5412 | -2.1002 | -2.6876 | -3.2687 | -3.8271 | -5.7035 | -6.1142 | -5.8147
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Leading the Way | Thermal headroom (MW) | 2.0965 | 1.9214 | 1.8227 | 1.6275 | 1.3978 | 1.095 | 0.69345 | 0.30407 | -0.082799 | -0.57645 | -1.1166 | -1.6689 | -2.2862 | -2.8859 | -3.4609 | -3.9735 | -5.0593 | -4.7495 | -3.8598
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Steady Progression | Thermal headroom (MW) | 2.1944 | 2.2356 | 2.3488 | 2.3856 | 2.4107 | 2.4146 | 2.3986 | 2.3904 | 2.3854 | 2.3351 | 2.1904 | 1.9722 | 1.7343 | 1.4637 | 1.1708 | 0.87115 | -0.85824 | -2.3692 | -2.96
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | System Transformation | Thermal headroom (MW) | 2.154 | 2.1404 | 2.2125 | 2.214 | 2.1827 | 2.1635 | 2.0322 | 1.9275 | 1.763 | 1.5848 | 1.2966 | 0.93592 | 0.53399 | 0.11234 | -0.31357 | -0.73054 | -2.6939 | -3.7849 | -3.62
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | WPD Best View | Thermal headroom (MW) | 2.1527 | 2.1382 | 2.2075 | 2.2005 | 2.1575 | 2.0806 | 1.8922 | 1.7402 | 1.5089 | 1.2343 | 0.9352 | 0.59732 | 0.24785 | -0.095455 | -0.42175 | -0.82689 | -2.9893 | -3.9386 | -3.7253
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Consumer Transformation | Thermal headroom (MW) | 11.5018 | 10.9666 | 10.5536 | 10.0002 | 8.8993 | 7.6092 | 5.8023 | 4.3584 | 2.7363 | -0.10841 | -2.8648 | -5.747 | -8.6994 | -11.562 | -14.5821 | -17.2031 | -26.6197 | -30.5204 | -30.1686
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Leading the Way | Thermal headroom (MW) | 11.4233 | 10.8235 | 10.5725 | 10.0738 | 8.8496 | 7.3625 | 5.3854 | 3.9248 | 1.5113 | -0.95401 | -4.3178 | -7.0351 | -9.9106 | -12.791 | -15.6563 | -18.4014 | -23.5221 | -23.7332 | -20.7066
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Steady Progression | Thermal headroom (MW) | 11.6421 | 11.7107 | 12.0448 | 12.0777 | 11.7981 | 11.5121 | 11.2318 | 11.1215 | 10.9863 | 10.5227 | 9.7012 | 9.0099 | 8.1574 | 7.2253 | 6.2023 | 4.5285 | -1.3273 | -8.8798 | -10.8874
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | System Transformation | Thermal headroom (MW) | 11.5439 | 11.5436 | 11.724 | 11.7926 | 11.3284 | 10.8168 | 10.177 | 9.9476 | 9.515 | 8.6933 | 7.1542 | 5.1451 | 3.7783 | 2.248 | 0.38865 | -1.3092 | -9.7335 | -14.4411 | -14.4622
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | WPD Best View | Thermal headroom (MW) | 11.5534 | 11.5641 | 11.7448 | 11.8139 | 11.3486 | 10.8383 | 10.2058 | 9.9787 | 9.5675 | 8.7262 | 7.2429 | 5.2261 | 3.8904 | 2.3805 | 0.57412 | -1.0713 | -9.2103 | -14.0332 | -14.1868
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Consumer Transformation | Thermal headroom (MW) | 34.4002 | 32.3865 | 31.9356 | 29.5574 | 27.7974 | 25.2302 | 21.5353 | 17.8789 | 14.2148 | 9.799 | 5.4981 | 0.44522 | -5.1703 | -10.2581 | -16.2015 | -21.4234 | -43.6739 | -51.6044 | -50.3971
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Leading the Way | Thermal headroom (MW) | 34.169 | 31.3551 | 31.2705 | 27.8209 | 26.6084 | 23.9592 | 19.6959 | 16.5535 | 11.997 | 7.9007 | 4.0641 | -0.54164 | -4.6816 | -9.4951 | -14.6163 | -18.8407 | -31.2429 | -32.339 | -23.8742
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Steady Progression | Thermal headroom (MW) | 34.8602 | 34.5772 | 36.0412 | 35.2851 | 35.564 | 35.6661 | 35.6823 | 35.7494 | 35.5722 | 35.3213 | 34.7979 | 33.3511 | 32.3122 | 30.5164 | 28.8903 | 26.5015 | 14.3897 | 0.48388 | -2.8904
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | System Transformation | Thermal headroom (MW) | 34.5633 | 33.7423 | 34.5897 | 33.446 | 33.5832 | 33.2771 | 32.8413 | 32.306 | 30.9458 | 29.9812 | 28.3023 | 25.8199 | 23.3922 | 20.2423 | 17.2855 | 14.5706 | -2.3233 | -10.273 | -9.507
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | WPD Best View | Thermal headroom (MW) | 34.4414 | 32.7946 | 32.7246 | 30.7049 | 29.7022 | 27.9443 | 25.4788 | 23.2465 | 20.2077 | 17.1599 | 13.7611 | 9.6209 | 4.6823 | -0.40029 | -5.3813 | -9.7767 | -27.404 | -35.0571 | -34.3529
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Consumer Transformation | Thermal headroom (MW) | 5.3922 | 4.0471 | 3.8137 | 2.417 | 1.6141 | 0.81158 | -0.37757 | -1.9773 | -3.2375 | -4.808 | -6.4175 | -8.1899 | -9.8668 | -10.9773 | -13.1211 | -15.1501 | -23.8015 | -27.7349 | -28.7219
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Leading the Way | Thermal headroom (MW) | 5.3557 | 3.6178 | 3.4272 | 1.2917 | 0.81817 | 0.044874 | -1.6339 | -2.7594 | -4.4349 | -6.0138 | -7.1956 | -8.9439 | -9.8086 | -11.1901 | -13.3426 | -14.9108 | -19.9948 | -22.1339 | -20.7083
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Steady Progression | Thermal headroom (MW) | 5.4835 | 4.7699 | 4.9295 | 4.1648 | 4.0661 | 3.9271 | 3.7597 | 3.5672 | 3.3237 | 3.0316 | 2.6438 | 1.8002 | 1.2654 | 0.35699 | -0.21996 | -1.179 | -5.8385 | -10.3827 | -11.7185
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | System Transformation | Thermal headroom (MW) | 5.4273 | 4.4019 | 4.4932 | 3.4029 | 3.3105 | 3.0707 | 2.8269 | 2.4624 | 1.6548 | 1.1612 | 0.21018 | -0.82951 | -1.9613 | -3.1073 | -4.2257 | -5.3156 | -11.3362 | -14.5644 | -15.7126
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | WPD Best View | Thermal headroom (MW) | 5.4133 | 4.2686 | 4.2257 | 3.01 | 2.7967 | 2.4265 | 1.9105 | 1.2797 | 0.19252 | -0.8738 | -2.0091 | -2.9404 | -4.2456 | -5.5192 | -6.704 | -7.8277 | -14.4542 | -19.1684 | -20.4813
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Consumer Transformation | Thermal headroom (MW) | -5.7417 | -5.8126 | -5.6663 | -5.797 | -5.9151 | -6.4736 | -7.2998 | -7.9183 | -8.6845 | -9.763 | -10.5351 | -11.5046 | -12.3622 | -13.3187 | -14.1356 | -14.5348 | -18.2753 | -19.7316 | -19.0747
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Leading the Way | Thermal headroom (MW) | -5.7613 | -5.8195 | -5.6539 | -5.7965 | -5.8979 | -6.5443 | -7.4622 | -8.0928 | -9.2825 | -10.0406 | -10.8562 | -11.5033 | -11.9858 | -12.6538 | -13.1121 | -13.658 | -15.5163 | -15.4813 | -14.1837
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Steady Progression | Thermal headroom (MW) | -5.6889 | -5.4823 | -5.036 | -4.8663 | -4.6847 | -4.7217 | -4.7232 | -4.6343 | -4.6332 | -4.6381 | -4.6929 | -4.7954 | -4.9317 | -5.2643 | -5.6632 | -6.2831 | -7.9548 | -8.7421 | -8.5032
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | System Transformation | Thermal headroom (MW) | -5.7155 | -5.5381 | -5.1259 | -4.9985 | -4.8685 | -5.0064 | -5.138 | -5.1638 | -5.2709 | -5.3977 | -5.6 | -6.2125 | -6.5523 | -7.2007 | -7.8657 | -8.2001 | -9.7059 | -9.8777 | -9.3129
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | WPD Best View | Thermal headroom (MW) | -5.7276 | -5.6556 | -5.3511 | -5.3339 | -5.3069 | -5.5464 | -5.8988 | -6.1258 | -6.5158 | -6.8896 | -7.2932 | -8.1785 | -8.7478 | -9.5266 | -10.276 | -10.6755 | -12.1919 | -12.8476 | -12.3631
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Consumer Transformation | Thermal headroom (MW) | 8.4138 | 8.3815 | 8.5006 | 8.3109 | 8.1434 | 8.1025 | 7.8814 | 7.6707 | 7.4498 | 7.1548 | 6.8294 | 6.4665 | 6.1645 | 5.9162 | 5.725 | 5.5404 | 4.3193 | 3.4527 | 3.4553
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Leading the Way | Thermal headroom (MW) | 8.3944 | 8.3659 | 8.5393 | 8.32 | 8.1648 | 8.1146 | 7.8811 | 7.6968 | 7.4568 | 7.1182 | 6.7828 | 6.534 | 6.3699 | 6.2858 | 6.3296 | 6.4134 | 5.5943 | 5.2808 | 6.382
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Steady Progression | Thermal headroom (MW) | 8.4755 | 8.6555 | 9.0258 | 9.0824 | 9.1606 | 9.326 | 9.4749 | 9.5914 | 9.6971 | 9.7749 | 9.8443 | 9.855 | 9.8434 | 9.7541 | 9.6407 | 9.5182 | 8.6749 | 8.1378 | 8.1435
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | System Transformation | Thermal headroom (MW) | 8.4401 | 8.5963 | 8.9193 | 8.9049 | 8.9423 | 9.1113 | 9.2139 | 9.2912 | 9.3369 | 9.3521 | 9.3364 | 9.2339 | 9.0804 | 8.8857 | 8.6822 | 8.4735 | 7.9474 | 7.9567 | 8.4752
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | WPD Best View | Thermal headroom (MW) | 8.419 | 8.3905 | 8.5209 | 8.341 | 8.1876 | 8.1617 | 7.9586 | 7.7703 | 7.5667 | 7.3314 | 7.0126 | 6.6393 | 6.3038 | 5.9959 | 5.7341 | 5.4746 | 4.2869 | 3.547 | 3.5738
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Consumer Transformation | Thermal headroom (MW) | 7.0784 | 6.7219 | 6.3526 | 6.0497 | 5.3412 | 4.756 | 3.934 | 3.2305 | 2.5038 | 1.9233 | 1.2932 | 0.20028 | -1.3242 | -2.8588 | -4.8099 | -6.4496 | -13.0063 | -15.363 | -15.3686
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Leading the Way | Thermal headroom (MW) | 7.0445 | 6.3424 | 6.3389 | 5.7012 | 5.3822 | 4.7905 | 3.9584 | 3.2827 | 2.545 | 1.9355 | 1.3337 | 0.20609 | -1.2035 | -2.6774 | -4.4521 | -5.7336 | -9.6462 | -10.3121 | -7.7427
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Steady Progression | Thermal headroom (MW) | 7.2215 | 7.3574 | 7.8171 | 7.7016 | 7.862 | 7.9738 | 8.0945 | 8.1943 | 8.2571 | 8.3398 | 8.3722 | 7.9398 | 7.8425 | 7.7113 | 7.5608 | 7.371 | 5.361 | 0.060782 | -1.7282
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | System Transformation | Thermal headroom (MW) | 7.1403 | 7.1735 | 7.2473 | 7.3615 | 7.4143 | 7.4495 | 7.4053 | 7.3254 | 6.8659 | 6.7837 | 6.6307 | 6.3987 | 6.1235 | 5.4533 | 5.1308 | 4.7426 | -0.56882 | -4.1317 | -4.199
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | WPD Best View | Thermal headroom (MW) | 7.0784 | 6.7219 | 6.3526 | 6.0497 | 5.3412 | 4.756 | 3.934 | 3.2305 | 2.5038 | 1.9233 | 1.2932 | 0.20028 | -1.3242 | -2.8588 | -4.8099 | -6.4496 | -13.0063 | -15.363 | -15.3686
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Consumer Transformation | Thermal headroom (MW) | 17.759 | 17.5173 | 17.3579 | 17.0262 | 16.8291 | 16.3122 | 15.6671 | 15.1152 | 14.419 | 13.5844 | 12.6212 | 11.6199 | 10.536 | 9.4998 | 8.6108 | 7.6783 | 5.4621 | 5.6794 | 6.815
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Leading the Way | Thermal headroom (MW) | 17.6781 | 17.329 | 17.1872 | 16.7301 | 16.5279 | 16.0251 | 15.4149 | 14.8723 | 14.2071 | 13.3533 | 12.4464 | 11.522 | 10.5027 | 9.4878 | 8.7186 | 7.9638 | 6.995 | 8.2695 | 10.1351
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Steady Progression | Thermal headroom (MW) | 17.8631 | 17.8243 | 17.9416 | 17.8653 | 17.8837 | 17.945 | 17.935 | 17.9247 | 17.8604 | 17.7913 | 17.6514 | 17.4338 | 17.2083 | 16.9187 | 16.5751 | 16.1516 | 13.6165 | 11.0282 | 10.4684
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | System Transformation | Thermal headroom (MW) | 17.7868 | 17.678 | 17.6795 | 17.5173 | 17.5431 | 17.4886 | 17.4269 | 17.3007 | 17.1292 | 16.8984 | 16.558 | 16.1484 | 15.6499 | 15.0678 | 14.4486 | 13.7052 | 10.6805 | 9.4933 | 10.1464
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | WPD Best View | Thermal headroom (MW) | 17.759 | 17.5173 | 17.3579 | 17.0262 | 16.8291 | 16.3122 | 15.6671 | 15.1152 | 14.419 | 13.5844 | 12.6212 | 11.6199 | 10.536 | 9.4998 | 8.6108 | 7.6783 | 5.4621 | 5.6794 | 6.815
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Consumer Transformation | Thermal headroom (MW) | 8.625 | 8.3102 | 8.0669 | 7.6231 | 7.3733 | 6.8268 | 6.1855 | 5.6123 | 5.0066 | 4.4271 | 3.7694 | 3.0392 | 1.4174 | -0.17891 | -1.6948 | -3.2483 | -8.2146 | -9.2431 | -8.5468
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Leading the Way | Thermal headroom (MW) | 8.5083 | 7.9379 | 7.7683 | 7.2913 | 7.0175 | 6.4567 | 5.8191 | 5.283 | 4.6872 | 4.1348 | 3.5467 | 2.662 | 1.0685 | -0.49022 | -1.9579 | -3.2315 | -5.9928 | -5.2321 | -2.3979
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Steady Progression | Thermal headroom (MW) | 8.7819 | 8.7689 | 9.0166 | 8.8087 | 8.8041 | 8.8735 | 8.8917 | 8.9184 | 8.9192 | 8.9115 | 8.8623 | 8.7224 | 8.557 | 8.3448 | 8.133 | 7.8681 | 5.0838 | 0.059373 | -1.4385
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | System Transformation | Thermal headroom (MW) | 8.6587 | 8.5376 | 8.5128 | 8.274 | 8.2641 | 8.248 | 8.1759 | 8.0847 | 7.9538 | 7.786 | 7.5832 | 7.2717 | 6.8976 | 6.4851 | 6.1283 | 5.7252 | 0.1522 | -2.5711 | -2.0658
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | WPD Best View | Thermal headroom (MW) | 8.625 | 8.3102 | 8.0669 | 7.6231 | 7.3733 | 6.8268 | 6.1855 | 5.6123 | 5.0066 | 4.4271 | 3.7694 | 3.0392 | 1.4174 | -0.17891 | -1.6948 | -3.2483 | -8.2146 | -9.2431 | -8.5468
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Consumer Transformation | Thermal headroom (MW) | 38.8908 | 37.3491 | 36.3317 | 34.1977 | 31.5275 | 28.3234 | 22.9994 | 17.7543 | 12.2598 | 5.6539 | -0.53663 | -8.677 | -16.6838 | -24.3526 | -32.4519 | -39.9793 | -73.591 | -88.4168 | -90.148
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Leading the Way | Thermal headroom (MW) | 38.7354 | 37.098 | 36.2787 | 33.7961 | 31.6335 | 28.3215 | 22.7535 | 17.4336 | 10.5429 | 4.3049 | -2.5142 | -9.7976 | -16.688 | -23.2662 | -29.5599 | -35.9645 | -59.0216 | -63.6915 | -53.2563
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Steady Progression | Thermal headroom (MW) | 39.3903 | 39.9481 | 41.3274 | 41.5047 | 41.7233 | 41.8519 | 41.7005 | 41.2206 | 40.5587 | 39.6376 | 38.4903 | 36.3609 | 34.4018 | 32.0953 | 29.332 | 25.2733 | 3.4878 | -17.8704 | -24.3867
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | System Transformation | Thermal headroom (MW) | 39.1092 | 39.3747 | 40.2758 | 40.1545 | 40.0832 | 39.8545 | 38.8671 | 37.52 | 35.452 | 33.385 | 30.9817 | 27.0591 | 23.5347 | 18.9268 | 14.5185 | 9.1578 | -18.952 | -32.3036 | -32.6432
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | WPD Best View | Thermal headroom (MW) | 38.9344 | 37.6943 | 37.0079 | 35.2385 | 33.4838 | 30.9577 | 26.4563 | 21.9266 | 16.2952 | 10.5968 | 4.8751 | -2.4408 | -10.0569 | -18.0268 | -25.8577 | -34.0965 | -64.4381 | -76.7842 | -78.873
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Consumer Transformation | Thermal headroom (MW) | 3.635 | 3.6488 | 3.7752 | 3.5551 | 3.5407 | 3.4654 | 3.304 | 3.1705 | 2.9856 | 2.446 | 2.2547 | 1.9486 | 1.6736 | 1.3887 | 1.0582 | 0.75511 | -1.007 | -1.453 | -0.9026
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Leading the Way | Thermal headroom (MW) | 3.62 | 3.6504 | 3.6683 | 3.5079 | 3.502 | 3.4003 | 3.2294 | 3.1057 | 2.5613 | 2.3413 | 2.1096 | 1.9237 | 1.6954 | 1.4456 | 1.21 | 0.5319 | -0.16292 | 0.25941 | 0.98432
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Steady Progression | Thermal headroom (MW) | 3.6672 | 3.8419 | 4.1512 | 4.2482 | 4.3032 | 4.4563 | 4.5804 | 4.735 | 4.8849 | 5.0035 | 5.1397 | 5.2087 | 5.289 | 5.3069 | 5.1932 | 4.7024 | 3.846 | 3.2679 | 3.4479
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | System Transformation | Thermal headroom (MW) | 3.645 | 3.803 | 4.074 | 4.0121 | 4.1429 | 4.2427 | 4.3697 | 4.4752 | 4.5534 | 4.607 | 4.6784 | 4.36 | 4.2764 | 4.0659 | 3.8507 | 3.6428 | 2.7451 | 2.3062 | 2.5079
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | WPD Best View | Thermal headroom (MW) | 3.6289 | 3.6449 | 3.7667 | 3.5461 | 3.5268 | 3.4534 | 3.2909 | 3.1559 | 2.9671 | 2.4259 | 2.2399 | 1.9447 | 1.6827 | 1.4034 | 1.085 | 0.77126 | -0.85548 | -1.1505 | -0.52783
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Consumer Transformation | Thermal headroom (MW) | 4.7528 | 4.5484 | 4.4276 | 4.2094 | 4.0867 | 3.9273 | 3.5459 | 3.3337 | 3.1038 | 2.8766 | 2.6073 | 2.0452 | 1.1955 | 0.31381 | -0.59982 | -1.5289 | -4.8421 | -5.7895 | -5.5934
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Leading the Way | Thermal headroom (MW) | 4.6931 | 4.3953 | 4.3382 | 4.1224 | 4.0355 | 3.8704 | 3.4212 | 3.2231 | 2.9893 | 2.7441 | 2.3337 | 1.4926 | 0.52962 | -0.41112 | -1.3482 | -2.2065 | -4.2061 | -3.879 | -2.2183
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Steady Progression | Thermal headroom (MW) | 4.8504 | 4.9027 | 5.1205 | 5.1042 | 5.2194 | 5.3152 | 5.3403 | 5.4058 | 5.4675 | 5.522 | 5.5401 | 5.4865 | 5.4312 | 5.3489 | 5.2439 | 5.1042 | 2.9457 | -0.74072 | -2.0953
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | System Transformation | Thermal headroom (MW) | 4.7775 | 4.765 | 4.8384 | 4.8302 | 4.899 | 4.9948 | 4.8676 | 4.859 | 4.8266 | 4.7803 | 4.6897 | 4.5348 | 4.3589 | 4.1441 | 3.9109 | 3.2724 | -0.60571 | -2.663 | -2.5312
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | WPD Best View | Thermal headroom (MW) | 4.7528 | 4.5484 | 4.4276 | 4.2094 | 4.0867 | 3.9273 | 3.5459 | 3.3337 | 3.1038 | 2.8766 | 2.6073 | 2.0452 | 1.1955 | 0.31381 | -0.59982 | -1.5289 | -4.8421 | -5.7895 | -5.5934
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Consumer Transformation | Thermal headroom (MW) | 3.6497 | 3.542 | 3.5458 | 3.3679 | 3.1656 | 2.8037 | 2.1685 | 1.5373 | 0.79555 | -0.38293 | -1.364 | -2.6473 | -3.9672 | -5.2551 | -6.6061 | -8.0491 | -13.8369 | -16.6339 | -17.3696
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Leading the Way | Thermal headroom (MW) | 3.6445 | 3.5114 | 3.5704 | 3.4028 | 3.1928 | 2.854 | 2.1782 | 1.4687 | 0.30578 | -0.61937 | -1.7598 | -2.9732 | -4.2233 | -5.479 | -6.7244 | -8.249 | -11.7995 | -12.7976 | -11.1763
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Steady Progression | Thermal headroom (MW) | 3.6885 | 3.8163 | 4.0664 | 4.1396 | 4.2376 | 4.2896 | 4.2698 | 4.3103 | 4.2495 | 4.1827 | 4.0815 | 3.8914 | 3.6571 | 3.3777 | 3.0482 | 2.2598 | -0.85049 | -4.4956 | -5.2682
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | System Transformation | Thermal headroom (MW) | 3.6716 | 3.7657 | 3.9657 | 4.0505 | 4.0589 | 4.0525 | 4.046 | 3.9544 | 3.8379 | 3.6339 | 3.3726 | 2.6316 | 2.1754 | 1.5696 | 0.87529 | 0.13593 | -4.4402 | -7.0282 | -7.2518
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | WPD Best View | Thermal headroom (MW) | 3.6497 | 3.542 | 3.5458 | 3.3679 | 3.1656 | 2.8037 | 2.1685 | 1.5373 | 0.79555 | -0.38293 | -1.364 | -2.6473 | -3.9672 | -5.2551 | -6.6061 | -8.0491 | -13.8369 | -16.6339 | -17.3696
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Consumer Transformation | Thermal headroom (MW) | 5.5567 | 5.3366 | 5.246 | 4.9881 | 4.7564 | 4.4589 | 3.8226 | 3.243 | 2.6828 | 2.1068 | 1.0964 | -0.44213 | -2.0327 | -3.5867 | -5.2353 | -6.913 | -13.4025 | -16.506 | -17.5715
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Leading the Way | Thermal headroom (MW) | 5.541 | 5.3352 | 5.3041 | 5.0709 | 4.8864 | 4.5932 | 3.9657 | 3.4389 | 2.8731 | 2.1795 | 0.8887 | -0.44145 | -1.8428 | -3.2896 | -4.7187 | -5.9822 | -10.3341 | -11.9646 | -10.0898
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Steady Progression | Thermal headroom (MW) | 5.6151 | 5.7286 | 5.9913 | 6.068 | 6.182 | 6.2526 | 6.3239 | 6.3671 | 6.4146 | 6.4301 | 6.4113 | 6.3216 | 6.2205 | 6.0789 | 5.8741 | 5.647 | 2.8339 | -0.9417 | -2.1109
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | System Transformation | Thermal headroom (MW) | 5.5893 | 5.652 | 5.8873 | 5.9318 | 6.0007 | 6.0514 | 6.044 | 6.0204 | 5.9633 | 5.8899 | 5.7549 | 5.5746 | 5.3217 | 4.98 | 4.63 | 3.9094 | -0.77848 | -3.5376 | -3.7184
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | WPD Best View | Thermal headroom (MW) | 5.5567 | 5.3366 | 5.246 | 4.9881 | 4.7564 | 4.4589 | 3.8226 | 3.243 | 2.6828 | 2.1068 | 1.0964 | -0.44213 | -2.0327 | -3.5867 | -5.2353 | -6.913 | -13.4025 | -16.506 | -17.5715
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Consumer Transformation | Thermal headroom (MW) | 5.0265 | 4.691 | 4.4201 | 4.0071 | 3.4589 | 2.7455 | 1.7179 | 0.67974 | -0.38431 | -1.4593 | -2.5749 | -3.7791 | -5.041 | -6.1848 | -7.1568 | -8.0124 | -12.32 | -14.7264 | -15.2238
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Leading the Way | Thermal headroom (MW) | 5.0148 | 4.7065 | 4.4801 | 4.073 | 3.558 | 2.8441 | 1.7962 | 0.77948 | -0.33148 | -1.4539 | -2.5869 | -3.6969 | -4.7149 | -5.4867 | -5.9991 | -6.375 | -10.4702 | -11.4271 | -9.6719
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Steady Progression | Thermal headroom (MW) | 5.1286 | 5.1732 | 5.3243 | 5.3419 | 5.322 | 5.2762 | 5.1523 | 4.9242 | 4.6871 | 4.3736 | 3.9991 | 3.485 | 2.8852 | 2.234 | 1.5058 | 0.75358 | -3.6702 | -6.3014 | -7.4633
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | System Transformation | Thermal headroom (MW) | 5.0886 | 5.0915 | 5.1838 | 5.1297 | 5.0724 | 4.9006 | 4.5972 | 4.2324 | 3.7718 | 3.2172 | 2.5295 | 1.7062 | 0.77538 | -0.23562 | -1.2759 | -2.3928 | -6.6289 | -7.9272 | -7.9248
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | WPD Best View | Thermal headroom (MW) | 5.0509 | 4.7852 | 4.6005 | 4.2923 | 3.9542 | 3.4009 | 2.608 | 1.8068 | 0.95195 | 0.039362 | -1.0072 | -2.1788 | -3.3651 | -4.5231 | -5.8053 | -7.029 | -11.0463 | -12.7653 | -13.1656
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Consumer Transformation | Thermal headroom (MW) | 4.9646 | 4.9181 | 4.9246 | 4.7812 | 4.6086 | 4.2822 | 3.5612 | 2.6825 | 1.857 | 0.61735 | -0.30298 | -1.4111 | -2.6264 | -3.7851 | -5.0111 | -6.3226 | -11.2495 | -12.8984 | -12.4622
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Leading the Way | Thermal headroom (MW) | 4.9451 | 4.915 | 4.907 | 4.7481 | 4.5566 | 4.1656 | 3.3712 | 2.3375 | 0.94219 | -0.13787 | -1.1404 | -2.2097 | -3.3164 | -4.4308 | -5.5105 | -6.978 | -9.6128 | -9.4617 | -8.026
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Steady Progression | Thermal headroom (MW) | 5.0186 | 5.1353 | 5.3352 | 5.4265 | 5.5085 | 5.5498 | 5.5503 | 5.3855 | 5.2542 | 5.1243 | 4.9502 | 4.7433 | 4.4891 | 4.1878 | 3.8374 | 3.016 | 0.03783 | -3.2745 | -3.8777
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | System Transformation | Thermal headroom (MW) | 4.9653 | 5.0872 | 5.2492 | 5.3456 | 5.3955 | 5.4251 | 5.2413 | 4.854 | 4.5997 | 4.2814 | 3.9356 | 3.1752 | 2.6799 | 2.0998 | 1.4426 | 0.56409 | -3.6105 | -5.6446 | -5.5219
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | WPD Best View | Thermal headroom (MW) | 4.9447 | 4.9038 | 4.8855 | 4.7446 | 4.5147 | 4.1588 | 3.3595 | 2.352 | 0.98464 | 0.013391 | -0.93702 | -2.0047 | -3.088 | -4.1749 | -5.301 | -6.7983 | -10.3855 | -11.0581 | -10.74
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Consumer Transformation | Thermal headroom (MW) | 4.983 | 4.455 | 3.9244 | 3.3139 | 2.1727 | 1.1167 | -0.39034 | -1.8984 | -3.5136 | -5.1233 | -6.6093 | -8.534 | -9.9238 | -11.2107 | -12.7974 | -13.8542 | -20.5335 | -23.6492 | -24.078
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Leading the Way | Thermal headroom (MW) | 4.9527 | 4.3723 | 3.9149 | 2.9377 | 2.1455 | 1.0511 | -0.50073 | -1.9716 | -3.6772 | -5.3749 | -6.8164 | -8.2277 | -9.1491 | -10.0031 | -10.9368 | -11.447 | -16.4893 | -18.0817 | -16.7291
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Steady Progression | Thermal headroom (MW) | 5.0855 | 5.0605 | 5.1156 | 4.997 | 4.8352 | 4.67 | 4.509 | 4.2239 | 3.848 | 3.3854 | 2.8972 | 1.9685 | 1.3467 | 0.65288 | -0.10887 | -0.89545 | -5.6255 | -9.2927 | -10.7101
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | System Transformation | Thermal headroom (MW) | 5.0361 | 4.9307 | 4.8703 | 4.6919 | 4.4338 | 4.1998 | 3.8228 | 3.3633 | 2.3628 | 1.6201 | 0.86279 | 0.024189 | -0.89757 | -2.2835 | -3.313 | -4.2466 | -9.5243 | -11.7567 | -12.0744
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | WPD Best View | Thermal headroom (MW) | 5.0163 | 4.6705 | 4.3602 | 3.9555 | 3.4372 | 2.8237 | 1.8494 | 0.82032 | -0.68746 | -1.8948 | -3.0284 | -4.3198 | -5.5655 | -7.1572 | -8.2919 | -9.4336 | -14.7689 | -17.3374 | -18.129
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Consumer Transformation | Thermal headroom (MW) | 29.7378 | 28.3806 | 27.3947 | 25.8003 | 22.2238 | 19.3465 | 14.9886 | 11.2591 | 7.1502 | 2.6668 | -1.7878 | -9.025 | -14.9947 | -21.0011 | -28.4592 | -34.3629 | -59.7301 | -69.9567 | -70.6445
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Leading the Way | Thermal headroom (MW) | 29.5932 | 28.0803 | 27.3037 | 24.3373 | 22.0102 | 19.0043 | 14.6064 | 10.7033 | 5.9289 | 1.6081 | -3.4541 | -9.5702 | -14.5945 | -20.2268 | -26.811 | -31.8446 | -46.9406 | -50.9624 | -43.8898
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Steady Progression | Thermal headroom (MW) | 30.1645 | 30.521 | 31.5863 | 31.7964 | 31.6263 | 31.6352 | 31.8982 | 31.9082 | 31.8219 | 31.6956 | 31.2503 | 28.8836 | 27.9147 | 26.443 | 25.0451 | 22.8535 | 9.5264 | -7.8647 | -13.857
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | System Transformation | Thermal headroom (MW) | 29.9252 | 30.0244 | 30.6383 | 30.7376 | 30.1279 | 29.9566 | 29.4431 | 28.9677 | 26.7724 | 25.9149 | 24.6499 | 22.5312 | 20.5968 | 16.6048 | 14.1155 | 11.1659 | -9.405 | -21.8389 | -23.4672
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | WPD Best View | Thermal headroom (MW) | 29.7007 | 28.3872 | 27.5389 | 26.0807 | 22.5767 | 19.7137 | 15.4922 | 11.9236 | 7.9028 | 3.8086 | -0.47597 | -7.6106 | -13.0213 | -18.6398 | -25.6824 | -31.0693 | -54.2551 | -63.2216 | -62.2918
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Consumer Transformation | Thermal headroom (MW) | 7.8896 | 7.8871 | 8.0747 | 7.8796 | 7.6829 | 7.2648 | 6.5848 | 5.9547 | 5.2722 | 4.3528 | 3.7999 | 3.0476 | 2.2648 | 1.1947 | 0.38027 | -0.33966 | -3.5565 | -4.8116 | -4.4442
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Leading the Way | Thermal headroom (MW) | 7.8578 | 7.8453 | 8.0688 | 7.8201 | 7.5748 | 7.1564 | 6.5121 | 5.8398 | 4.7542 | 4.0867 | 3.5227 | 3.0509 | 2.515 | 1.4084 | 0.75854 | -0.094984 | -1.7594 | -1.6991 | -0.39916
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Steady Progression | Thermal headroom (MW) | 7.9448 | 8.1911 | 8.6185 | 8.7237 | 8.8509 | 8.9986 | 9.1852 | 9.355 | 9.453 | 9.5534 | 9.6553 | 9.688 | 9.7571 | 9.5128 | 9.4664 | 9.0303 | 8.1138 | 6.5362 | 6.5705
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | System Transformation | Thermal headroom (MW) | 7.9267 | 8.119 | 8.5081 | 8.5675 | 8.6023 | 8.7445 | 8.884 | 8.8976 | 8.9411 | 8.9916 | 8.9997 | 8.5667 | 8.5156 | 7.9986 | 7.7986 | 7.6023 | 5.6741 | 4.5626 | 4.7938
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | WPD Best View | Thermal headroom (MW) | 7.8673 | 7.8594 | 8.0596 | 7.8554 | 7.6714 | 7.2134 | 6.5726 | 5.9352 | 5.2181 | 4.2501 | 3.6624 | 2.9034 | 2.1233 | 1.029 | 0.23038 | -0.48088 | -3.4004 | -4.3363 | -3.6303
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Consumer Transformation | Thermal headroom (MW) | 8.3329 | 8.0696 | 7.8143 | 7.4699 | 6.6582 | 6.112 | 4.9743 | 4.0981 | 3.0965 | 2.0359 | 0.85277 | -1.002 | -2.4933 | -3.9448 | -5.7839 | -7.1989 | -13.1748 | -15.6059 | -15.9369
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Leading the Way | Thermal headroom (MW) | 8.3067 | 8.0323 | 7.8551 | 7.1727 | 6.6849 | 6.1036 | 4.9117 | 3.98 | 2.9383 | 1.7827 | 0.5381 | -1.029 | -2.2532 | -3.5558 | -5.11 | -6.1564 | -9.8476 | -11.0232 | -9.5425
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Steady Progression | Thermal headroom (MW) | 8.3958 | 8.4593 | 8.6601 | 8.6608 | 8.5957 | 8.6262 | 8.6335 | 8.5639 | 8.4955 | 8.4021 | 8.2703 | 7.6695 | 7.4185 | 7.062 | 6.7414 | 6.3185 | 3.0502 | -0.81386 | -2.124
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | System Transformation | Thermal headroom (MW) | 8.3644 | 8.4118 | 8.5237 | 8.5602 | 8.4278 | 8.4401 | 8.2017 | 8.1011 | 7.5619 | 7.3435 | 7.0222 | 6.6692 | 6.2061 | 5.2529 | 4.6372 | 3.9624 | -0.9598 | -3.9543 | -4.3678
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | WPD Best View | Thermal headroom (MW) | 8.3131 | 8.0255 | 7.841 | 7.5103 | 6.6858 | 6.1329 | 4.9368 | 4.0323 | 3.0062 | 1.8795 | 0.67219 | -1.0232 | -2.3023 | -3.6319 | -5.297 | -6.4606 | -11.2854 | -12.9789 | -12.2652
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Consumer Transformation | Thermal headroom (MW) | 3.615 | 3.2756 | 3.0995 | 2.7282 | 2.3909 | 1.847 | 0.81587 | -0.10984 | -1.0116 | -2.331 | -3.3913 | -4.7359 | -6.253 | -7.7709 | -9.3211 | -10.8021 | -16.9645 | -19.6445 | -20.0759
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Leading the Way | Thermal headroom (MW) | 3.5926 | 3.2942 | 3.1409 | 2.8298 | 2.5197 | 1.9598 | 0.93715 | -0.0091275 | -1.3364 | -2.3661 | -3.5742 | -4.7215 | -6.0378 | -7.5132 | -8.8578 | -10.379 | -14.0377 | -15.0438 | -13.7412
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Steady Progression | Thermal headroom (MW) | 3.6946 | 3.8372 | 4.1367 | 4.2794 | 4.3531 | 4.4171 | 4.4909 | 4.5514 | 4.6204 | 4.6126 | 4.3764 | 4.0298 | 3.5876 | 3.0705 | 2.5089 | 1.5751 | -1.613 | -4.7355 | -5.6755
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | System Transformation | Thermal headroom (MW) | 3.6525 | 3.7648 | 4.0041 | 4.0934 | 4.1199 | 4.085 | 4.0648 | 3.9983 | 3.8781 | 3.6053 | 3.1527 | 2.2069 | 1.5094 | 0.7034 | -0.11374 | -0.85634 | -4.4121 | -6.454 | -6.8515
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | WPD Best View | Thermal headroom (MW) | 3.6148 | 3.3614 | 3.2378 | 3.0088 | 2.7623 | 2.2711 | 1.4458 | 0.74547 | 0.00027301 | -0.75565 | -1.5668 | -3.0036 | -4.1724 | -5.397 | -6.7195 | -7.9567 | -13.39 | -15.8478 | -16.0756
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Consumer Transformation | Thermal headroom (MW) | 11.6419 | 11.3463 | 11.0214 | 10.7114 | 9.9157 | 9.3628 | 8.6254 | 7.9833 | 7.2243 | 6.5275 | 5.7881 | 4.5154 | 3.6005 | 2.7391 | 1.4564 | 0.54252 | -3.5673 | -5.309 | -5.496
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Leading the Way | Thermal headroom (MW) | 11.6206 | 11.2372 | 10.9288 | 10.2604 | 9.7937 | 9.2317 | 8.5169 | 7.8291 | 7.082 | 6.3788 | 5.588 | 4.5352 | 3.7954 | 3.0497 | 1.9396 | 1.2081 | -1.3057 | -2.2515 | -1.125
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Steady Progression | Thermal headroom (MW) | 11.7335 | 11.7008 | 11.7386 | 11.709 | 11.6384 | 11.5849 | 11.6209 | 11.571 | 11.5189 | 11.4775 | 11.3996 | 10.8778 | 10.7423 | 10.5506 | 10.3314 | 10.0693 | 7.8644 | 4.8941 | 3.7309
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | System Transformation | Thermal headroom (MW) | 11.6855 | 11.5855 | 11.5084 | 11.473 | 11.3017 | 11.2877 | 11.1575 | 11.0359 | 10.4983 | 10.3455 | 10.1409 | 9.8965 | 9.5875 | 8.8649 | 8.4633 | 8.0263 | 4.5552 | 2.3249 | 1.9593
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | WPD Best View | Thermal headroom (MW) | 11.6419 | 11.3463 | 11.0214 | 10.7114 | 9.9157 | 9.3628 | 8.6254 | 7.9833 | 7.2243 | 6.5275 | 5.7881 | 4.5154 | 3.6005 | 2.7391 | 1.4564 | 0.54252 | -3.5673 | -5.309 | -5.496
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Consumer Transformation | Thermal headroom (MW) | 12.3542 | 12.1264 | 12.0176 | 11.8108 | 11.0418 | 10.5319 | 10.0976 | 9.7016 | 9.2751 | 8.9367 | 8.429 | 7.2915 | 6.5152 | 5.7455 | 4.6041 | 3.7512 | 0.13474 | -1.0781 | -0.9562
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Leading the Way | Thermal headroom (MW) | 12.3211 | 12.0649 | 11.9955 | 11.4409 | 10.9597 | 10.4028 | 9.936 | 9.5457 | 9.1055 | 8.6678 | 7.9055 | 6.8435 | 6.0909 | 5.3229 | 4.1712 | 3.5323 | 1.4653 | 1.2192 | 2.5246
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Steady Progression | Thermal headroom (MW) | 12.4389 | 12.485 | 12.6821 | 12.7348 | 12.6344 | 12.5625 | 12.5784 | 12.5893 | 12.5536 | 12.5492 | 12.5317 | 12.085 | 11.9942 | 11.8761 | 11.7526 | 11.5961 | 9.4635 | 5.8703 | 4.4097
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | System Transformation | Thermal headroom (MW) | 12.3755 | 12.3623 | 12.4868 | 12.4841 | 12.2994 | 12.1234 | 12.0466 | 11.9532 | 11.4403 | 11.319 | 11.1808 | 11.0016 | 10.7935 | 10.221 | 9.9855 | 9.4267 | 5.389 | 3.0302 | 2.7422
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | WPD Best View | Thermal headroom (MW) | 12.3542 | 12.1264 | 12.0176 | 11.8108 | 11.0418 | 10.5319 | 10.0976 | 9.7016 | 9.2751 | 8.9367 | 8.429 | 7.2915 | 6.5152 | 5.7455 | 4.6041 | 3.7512 | 0.13474 | -1.0781 | -0.9562
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Consumer Transformation | Thermal headroom (MW) | 16.1735 | 15.8613 | 15.7021 | 15.307 | 14.9045 | 14.3266 | 13.2292 | 12.2541 | 11.1064 | 9.5408 | 8.2345 | 6.4517 | 4.5644 | 2.6893 | 0.79881 | -1.0831 | -8.9962 | -12.4884 | -13.1148
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Leading the Way | Thermal headroom (MW) | 16.1379 | 15.8251 | 15.7227 | 15.4084 | 14.9732 | 14.4173 | 13.3004 | 12.298 | 10.7355 | 9.3994 | 7.86 | 6.2546 | 4.5788 | 2.7689 | 1.0552 | -0.8069 | -5.571 | -6.9144 | -5.0163
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Steady Progression | Thermal headroom (MW) | 16.3351 | 16.4819 | 16.7884 | 16.9153 | 16.9628 | 16.9868 | 17.1049 | 17.0875 | 17.1466 | 17.075 | 16.992 | 16.7524 | 16.4394 | 16.1035 | 15.6817 | 14.8883 | 10.8501 | 6.2416 | 5.0682
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | System Transformation | Thermal headroom (MW) | 16.2414 | 16.2918 | 16.5693 | 16.6326 | 16.6757 | 16.7 | 16.6734 | 16.5482 | 16.4339 | 16.2269 | 15.8679 | 15.022 | 14.4853 | 13.7469 | 12.8993 | 11.9825 | 6.1181 | 2.8058 | 2.4996
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | WPD Best View | Thermal headroom (MW) | 16.221 | 16.2273 | 16.4048 | 16.3681 | 16.3579 | 16.2754 | 16.0178 | 15.6872 | 15.3597 | 14.9278 | 14.3981 | 13.2609 | 12.3908 | 11.3548 | 10.2719 | 9.0634 | 2.3299 | -1.274 | -1.8467
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Consumer Transformation | Thermal headroom (MW) | 13.0043 | 10.8714 | 10.4972 | 9.3816 | 8.0458 | 5.0363 | 0.78379 | -2.7747 | -6.3102 | -10.1577 | -13.5019 | -18.0027 | -22.092 | -25.9185 | -30.5003 | -35.1279 | -51.8065 | -57.5569 | -56.9096
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Leading the Way | Thermal headroom (MW) | 12.9094 | 10.2197 | 10.0289 | 8.6613 | 7.5388 | 4.1933 | -0.72547 | -4.4748 | -8.5966 | -13.0528 | -16.8261 | -20.2661 | -23.1285 | -26.238 | -30.1977 | -33.2126 | -43.0369 | -44.5957 | -38.0295
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Steady Progression | Thermal headroom (MW) | 13.2867 | 12.612 | 13.4929 | 13.6042 | 13.7415 | 12.8457 | 12.066 | 11.5055 | 10.8383 | 9.7999 | 9.1216 | 7.9402 | 6.86 | 5.4951 | 3.9787 | 2.4064 | -6.1004 | -14.8276 | -16.6144
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | System Transformation | Thermal headroom (MW) | 13.078 | 11.9052 | 12.6324 | 12.6486 | 12.7152 | 11.2047 | 9.4222 | 8.283 | 6.6205 | 4.9274 | 3.5591 | 1.9297 | -0.10413 | -2.5748 | -4.8898 | -7.1463 | -17.6017 | -22.1236 | -20.6759
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | WPD Best View | Thermal headroom (MW) | 13.0483 | 11.8574 | 12.5083 | 12.4515 | 12.4101 | 10.783 | 8.7958 | 7.4189 | 5.5458 | 3.6342 | 2.1353 | 0.26235 | -1.7923 | -4.2008 | -6.3583 | -8.4655 | -19.5314 | -24.5476 | -23.551
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Consumer Transformation | Thermal headroom (MW) | 6.962 | 6.931 | 7.0226 | 6.9233 | 6.846 | 5.926 | 4.5494 | 3.6426 | 2.67 | 1.5896 | 0.82502 | -0.10204 | -1.0213 | -1.8819 | -2.7736 | -3.6585 | -5.9923 | -6.5383 | -6.0548
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Leading the Way | Thermal headroom (MW) | 6.9546 | 6.9387 | 7.0755 | 7.0118 | 6.9238 | 5.7243 | 3.9146 | 2.7414 | 1.3985 | -0.045577 | -1.1022 | -1.8345 | -2.487 | -3.1277 | -3.6838 | -4.0786 | -5.1205 | -4.8841 | -3.3306
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Steady Progression | Thermal headroom (MW) | 6.9944 | 7.1292 | 7.4126 | 7.5337 | 7.6693 | 7.167 | 6.645 | 6.3548 | 5.9921 | 5.5437 | 5.3543 | 5.1703 | 4.926 | 4.717 | 4.4371 | 4.1791 | 2.8735 | 0.826 | 0.69174
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | System Transformation | Thermal headroom (MW) | 6.9588 | 7.0876 | 7.3602 | 7.4618 | 7.5698 | 6.8333 | 5.8298 | 5.2726 | 4.6818 | 4.005 | 3.6265 | 3.2269 | 2.8159 | 2.4155 | 1.9292 | 1.409 | -0.30253 | -0.83719 | -0.16605
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | WPD Best View | Thermal headroom (MW) | 6.9588 | 7.0876 | 7.3602 | 7.4618 | 7.5698 | 6.8333 | 5.8298 | 5.2726 | 4.6818 | 4.005 | 3.6265 | 3.2269 | 2.8159 | 2.4155 | 1.9292 | 1.409 | -0.30253 | -0.83719 | -0.16605
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Consumer Transformation | Thermal headroom (MW) | 4.1641 | 2.8545 | 2.8173 | 2.4838 | 2.2012 | 1.5125 | 0.79565 | 0.055642 | -0.69107 | -1.5053 | -2.3903 | -3.5534 | -4.7849 | -5.9968 | -7.2055 | -8.3956 | -12.763 | -14.0508 | -13.7545
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Leading the Way | Thermal headroom (MW) | 4.1386 | 2.3618 | 2.3826 | 2.0284 | 1.6744 | 1.0246 | 0.243 | -0.39671 | -1.2127 | -2.0434 | -3.0034 | -4.01 | -5.0217 | -6.1542 | -7.1787 | -8.0681 | -10.6075 | -10.6142 | -8.6322
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Steady Progression | Thermal headroom (MW) | 4.2531 | 3.5222 | 3.7774 | 3.7458 | 3.7183 | 3.6071 | 3.6118 | 3.559 | 3.529 | 3.4105 | 3.3055 | 3.128 | 2.8878 | 2.4251 | 1.9585 | 1.4586 | -1.1922 | -3.6674 | -4.1028
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | System Transformation | Thermal headroom (MW) | 4.1846 | 3.1001 | 3.3328 | 3.2998 | 3.3195 | 3.0268 | 2.8784 | 2.7804 | 2.6182 | 2.4416 | 2.1782 | 1.8191 | 1.2034 | 0.51884 | -0.16428 | -0.80736 | -4.1787 | -5.7729 | -5.2854
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | WPD Best View | Thermal headroom (MW) | 4.1668 | 3.1118 | 3.3393 | 3.295 | 3.2715 | 2.9442 | 2.7442 | 2.5922 | 2.3722 | 2.1171 | 1.8035 | 1.3312 | 0.73125 | 0.097118 | -0.49613 | -1.0747 | -4.9791 | -6.5775 | -6.1207
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Consumer Transformation | Thermal headroom (MW) | 4.537 | 3.8778 | 3.3157 | 2.6007 | 1.5035 | 0.38237 | -1.4443 | -3.1877 | -4.7806 | -6.4742 | -7.9862 | -10.2361 | -11.8942 | -13.3582 | -15.7019 | -18.1403 | -28.2784 | -32.5336 | -32.9968
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Leading the Way | Thermal headroom (MW) | 4.4704 | 3.782 | 3.2834 | 2.2279 | 1.5152 | 0.40236 | -1.4079 | -3.0765 | -4.6557 | -6.4512 | -7.8819 | -9.3895 | -10.3165 | -11.3914 | -13.8128 | -15.5462 | -22.1351 | -24.4448 | -21.9215
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Steady Progression | Thermal headroom (MW) | 4.699 | 4.7046 | 4.9304 | 4.9063 | 4.8832 | 4.8033 | 4.7311 | 4.6157 | 4.4597 | 4.123 | 3.7666 | 2.8883 | 2.3287 | 1.6833 | 0.97862 | 0.21656 | -4.1405 | -7.7556 | -9.0871
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | System Transformation | Thermal headroom (MW) | 4.6033 | 4.5225 | 4.6107 | 4.505 | 4.3734 | 4.2033 | 3.9454 | 3.6412 | 2.845 | 2.1791 | 1.529 | 0.73367 | -0.16537 | -1.519 | -2.5364 | -3.4822 | -8.4895 | -10.8081 | -10.8872
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | WPD Best View | Thermal headroom (MW) | 4.5927 | 4.4467 | 4.4488 | 4.2698 | 4.0684 | 3.8056 | 3.3712 | 2.8538 | 1.883 | 1.0631 | 0.32563 | -0.60404 | -1.5516 | -2.9023 | -3.8571 | -4.7136 | -9.6941 | -12.6139 | -13.2027
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Consumer Transformation | Thermal headroom (MW) | 52.1643 | 50.237 | 48.6442 | 47.0841 | 44.3943 | 40.2843 | 34.7183 | 29.1829 | 23.6626 | 15.8019 | 8.8858 | 1.043 | -6.9758 | -13.9684 | -21.5448 | -29.5085 | -63.628 | -75.6084 | -74.4963
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Leading the Way | Thermal headroom (MW) | 51.6955 | 49.1786 | 47.6068 | 45.8743 | 42.6954 | 37.343 | 30.9653 | 24.4452 | 15.8105 | 8.06 | -0.022965 | -7.9578 | -15.2644 | -22.8459 | -30.88 | -40.0356 | -63.2417 | -61.955 | -51.7668
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Steady Progression | Thermal headroom (MW) | 52.7672 | 52.7615 | 53.3425 | 53.0743 | 52.3137 | 51.3369 | 50.2007 | 48.6679 | 46.7517 | 44.7866 | 42.4935 | 39.6035 | 36.5796 | 33.3465 | 29.8629 | 24.0116 | 1.7577 | -19.1743 | -26.5312
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | System Transformation | Thermal headroom (MW) | 52.2889 | 51.8209 | 51.5159 | 51.2975 | 49.9931 | 47.9934 | 45.5671 | 42.779 | 39.7863 | 36.5285 | 32.683 | 26.0009 | 20.5255 | 14.8583 | 8.6397 | 2.1719 | -28.5535 | -41.505 | -41.5197
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | WPD Best View | Thermal headroom (MW) | 51.9937 | 50.2623 | 49.3484 | 48.0495 | 45.437 | 40.8434 | 35.2474 | 29.4778 | 22.1782 | 15.0696 | 7.5246 | -1.0427 | -8.2742 | -15.5608 | -22.5406 | -30.3074 | -55.8348 | -59.4571 | -51.6421
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Consumer Transformation | Thermal headroom (MW) | 2.2361 | 1.6997 | 1.3441 | 1.5124 | 1.2682 | 0.62528 | -0.21643 | -0.90933 | -1.0513 | -1.2289 | -1.4469 | -2.0035 | -3.2769 | -4.4649 | -5.0533 | -5.2924 | -8.3131 | -8.4896 | -7.4247
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Leading the Way | Thermal headroom (MW) | 1.9951 | 1.2184 | 0.60109 | 0.78046 | 0.32332 | -0.48355 | -1.6193 | -2.5684 | -2.7275 | -2.9158 | -3.1057 | -3.548 | -5.0253 | -6.5747 | -7.3003 | -7.4808 | -10.1656 | -8.9031 | -7.1527
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Steady Progression | Thermal headroom (MW) | 2.4184 | 2.096 | 1.967 | 2.1121 | 1.9185 | 1.5334 | 1.1213 | 0.78399 | 0.74372 | 0.69189 | 0.62599 | 0.38322 | -0.29868 | -0.99933 | -1.3748 | -1.498 | -3.5117 | -4.86 | -5.1489
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | System Transformation | Thermal headroom (MW) | 2.2378 | 1.7215 | 1.384 | 1.5639 | 1.3196 | 0.78758 | 0.048373 | -0.51883 | -0.5726 | -0.62166 | -0.69337 | -1.1692 | -2.3844 | -3.5292 | -4.0632 | -4.223 | -7.34 | -7.7141 | -6.6571
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | WPD Best View | Thermal headroom (MW) | 2.2335 | 1.6897 | 1.3298 | 1.4929 | 1.0884 | 0.24541 | -0.90172 | -1.8693 | -2.1079 | -2.3485 | -2.5961 | -2.9532 | -4.3227 | -5.7166 | -6.3928 | -6.5554 | -9.4024 | -8.6439 | -7.0143
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Consumer Transformation | Thermal headroom (MW) | 17.2384 | 16.7401 | 16.0592 | 15.6139 | 14.6138 | 13.2747 | 11.0053 | 8.7425 | 6.3544 | 3.3313 | -0.50752 | -4.9345 | -8.8874 | -12.7209 | -16.6519 | -21.0949 | -34.3714 | -40.3736 | -40.4712
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Leading the Way | Thermal headroom (MW) | 17.0048 | 16.243 | 15.7063 | 15.2463 | 14.0615 | 11.7978 | 9.0133 | 6.1608 | 2.365 | -1.9508 | -6.8281 | -11.9007 | -16.2082 | -20.3383 | -24.3886 | -29.128 | -37.8547 | -37.3316 | -33.1781
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Steady Progression | Thermal headroom (MW) | 17.4803 | 17.3804 | 17.3981 | 17.1232 | 16.6885 | 16.2502 | 15.3886 | 14.4493 | 13.413 | 12.2528 | 10.7911 | 9.065 | 7.634 | 6.114 | 4.3771 | 1.5496 | -7.9637 | -18.6647 | -23.7973
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | System Transformation | Thermal headroom (MW) | 17.2757 | 17.0796 | 16.7409 | 16.615 | 15.9832 | 15.3506 | 13.9268 | 12.4097 | 10.7062 | 8.9124 | 6.6507 | 3.571 | 0.85234 | -2.1516 | -5.3971 | -9.2966 | -22.7791 | -29.775 | -30.2418
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | WPD Best View | Thermal headroom (MW) | 17.0281 | 16.3322 | 15.8726 | 15.4827 | 14.3807 | 12.2955 | 9.6748 | 6.9918 | 3.5941 | -0.5206 | -5.2039 | -10.5283 | -14.7115 | -18.7655 | -22.791 | -27.0866 | -36.6604 | -37.0114 | -33.1737
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Consumer Transformation | Thermal headroom (MW) | 5.7315 | 5.4561 | 5.6855 | 5.6569 | 5.5493 | 5.4704 | 5.3716 | 5.0031 | 4.4324 | 3.4569 | 2.8342 | 2.21 | 1.3855 | 1.101 | 0.018429 | -0.38919 | -6.6826 | -8.0216 | -8.0405
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Leading the Way | Thermal headroom (MW) | 5.7231 | 5.4159 | 5.6402 | 5.5649 | 5.4041 | 5.2944 | 5.2026 | 4.7093 | 3.5914 | 2.7461 | 1.8875 | 0.72526 | 0.21966 | -0.48906 | -1.3103 | -1.9352 | -7.8528 | -7.7352 | -6.4593
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Steady Progression | Thermal headroom (MW) | 5.7452 | 5.882 | 6.176 | 6.2072 | 6.2224 | 6.3244 | 6.4522 | 6.4022 | 5.8877 | 5.6799 | 5.4753 | 5.238 | 5.1143 | 5.0663 | 4.7644 | 4.3242 | 0.33703 | -2.0851 | -2.9681
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | System Transformation | Thermal headroom (MW) | 5.7381 | 5.8265 | 6.1004 | 6.1178 | 6.0765 | 5.8203 | 5.9389 | 5.7615 | 5.3802 | 4.9973 | 4.5586 | 3.762 | 3.4948 | 3.3578 | 2.4542 | 1.8198 | -4.6767 | -6.702 | -6.7769
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | WPD Best View | Thermal headroom (MW) | 5.7261 | 5.4232 | 5.6561 | 5.6277 | 5.4767 | 5.4153 | 5.3742 | 5.0331 | 4.0004 | 3.2163 | 2.4174 | 1.2785 | 0.75339 | 0.12568 | -0.52771 | -1.1387 | -7.1411 | -7.4236 | -6.2786
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Consumer Transformation | Thermal headroom (MW) | 9.0234 | 8.6827 | 8.0767 | 7.2354 | 6.8322 | 5.8722 | 4.2664 | 2.8931 | 1.6807 | 0.0019799 | -1.352 | -3.1392 | -5.0371 | -6.7223 | -8.5535 | -10.7995 | -17.9215 | -21.2776 | -21.8198
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Leading the Way | Thermal headroom (MW) | 8.995 | 8.6416 | 7.9676 | 7.0163 | 6.6548 | 5.6124 | 3.8757 | 2.3747 | 0.72313 | -0.65939 | -2.1386 | -3.503 | -4.9212 | -6.3442 | -7.7115 | -9.8916 | -14.1344 | -15.2929 | -13.2293
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Steady Progression | Thermal headroom (MW) | 9.1001 | 9.254 | 9.2886 | 9.0519 | 9.1625 | 9.0415 | 8.8743 | 8.685 | 8.6332 | 8.4851 | 8.379 | 8.159 | 7.8901 | 7.5265 | 7.1486 | 6.1126 | 2.7236 | -1.7027 | -2.6874
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | System Transformation | Thermal headroom (MW) | 9.0535 | 9.1346 | 8.9526 | 8.6173 | 8.6744 | 8.4604 | 8.001 | 7.5813 | 7.3432 | 7.0715 | 6.7425 | 5.948 | 5.3955 | 4.764 | 4.0221 | 2.7787 | -2.193 | -5.2707 | -5.3892
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | WPD Best View | Thermal headroom (MW) | 8.9992 | 8.7008 | 8.0009 | 7.0867 | 6.7479 | 5.7422 | 4.0469 | 2.5998 | 1.0141 | -0.28136 | -1.6361 | -2.8839 | -4.1813 | -5.4664 | -6.7446 | -8.8482 | -13.5257 | -15.1217 | -13.3208
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Consumer Transformation | Thermal headroom (MW) | 10.17 | 10.1133 | 10.0502 | 9.9218 | 9.4476 | 8.6867 | 7.935 | 7.1785 | 6.2943 | 5.0167 | 4.1639 | 3.3951 | 2.7525 | 2.1635 | 1.6054 | 0.96513 | -2.5721 | -3.8075 | -3.6536
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Leading the Way | Thermal headroom (MW) | 10.149 | 10.0983 | 10.0346 | 9.8719 | 9.2903 | 8.3831 | 7.6236 | 6.8119 | 5.5295 | 4.5519 | 3.7001 | 3.2395 | 2.8521 | 2.4387 | 1.6872 | 0.67819 | -1.1931 | -1.217 | -0.29805
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Steady Progression | Thermal headroom (MW) | 10.1939 | 10.2856 | 10.4128 | 10.4873 | 10.2932 | 10.0987 | 10.1294 | 10.0192 | 9.8049 | 9.5033 | 9.1762 | 8.8355 | 8.472 | 8.0505 | 7.5989 | 6.7716 | 4.4528 | 2.7615 | 2.4466
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | System Transformation | Thermal headroom (MW) | 10.1676 | 10.2497 | 10.3387 | 10.3926 | 10.0991 | 9.784 | 9.685 | 9.4889 | 9.0955 | 8.6036 | 8.1006 | 7.2307 | 6.6757 | 6.0885 | 5.4974 | 4.9477 | 2.4046 | 1.6703 | 1.5996
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | WPD Best View | Thermal headroom (MW) | 10.1503 | 10.1005 | 10.0395 | 9.8804 | 9.3034 | 8.4374 | 7.7317 | 6.9506 | 5.6956 | 4.7388 | 3.8912 | 3.4093 | 3.0454 | 2.6433 | 2.0195 | 1.0275 | -1.0299 | -1.2614 | -0.44597
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Consumer Transformation | Thermal headroom (MW) | 1.0236 | 0.67865 | 0.3546 | -0.04391 | -0.48193 | -0.97775 | -1.5177 | -2.0417 | -2.6098 | -3.5541 | -4.1086 | -4.643 | -5.1063 | -5.4901 | -5.9822 | -6.8363 | -10.0946 | -11.1503 | -10.8059
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Leading the Way | Thermal headroom (MW) | 1.0131 | 0.57378 | 0.36292 | -0.039235 | -0.4674 | -0.98414 | -1.5509 | -2.0653 | -3.0051 | -3.5896 | -4.1316 | -4.5178 | -4.8282 | -5.2311 | -6.1044 | -7.1827 | -8.8687 | -8.5361 | -7.5914
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Steady Progression | Thermal headroom (MW) | 1.1288 | 1.1197 | 1.253 | 1.1639 | 1.1265 | 1.0959 | 1.0161 | 0.9275 | 0.81321 | 0.66094 | 0.47169 | 0.21235 | -0.10183 | -0.45247 | -0.82479 | -1.5947 | -3.8219 | -5.9805 | -6.5167
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | System Transformation | Thermal headroom (MW) | 1.0716 | 0.98307 | 0.97855 | 0.8881 | 0.77424 | 0.63053 | 0.43544 | 0.2214 | -0.075203 | -0.39675 | -0.75938 | -1.5818 | -2.1221 | -2.6883 | -3.2639 | -3.8287 | -6.3015 | -7.4506 | -7.614
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | WPD Best View | Thermal headroom (MW) | 1.0663 | 0.97676 | 1.0374 | 0.85458 | 0.72318 | 0.56397 | 0.34991 | 0.11293 | -0.19765 | -0.52396 | -0.87384 | -1.6511 | -2.1105 | -2.5715 | -3.0234 | -3.4643 | -5.7431 | -7.3727 | -7.5293
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Consumer Transformation | Thermal headroom (MW) | 47.784 | 45.7574 | 44.394 | 42.1533 | 40.2196 | 37.6861 | 33.7044 | 29.7456 | 25.6487 | 20.6458 | 16.7774 | 12.4944 | 7.9287 | 4.1494 | -0.23564 | -4.0258 | -21.2767 | -27.9242 | -27.5461
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Leading the Way | Thermal headroom (MW) | 47.1592 | 44.7737 | 43.3002 | 41.3026 | 39.2042 | 36.7288 | 32.7462 | 28.701 | 23.2625 | 19.2414 | 15.6057 | 12.1216 | 9.0548 | 5.7587 | 2.9796 | -1.014 | -9.9048 | -11.0909 | -5.9176
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Steady Progression | Thermal headroom (MW) | 48.5205 | 48.4669 | 49.0603 | 48.5114 | 47.8546 | 47.6974 | 47.1252 | 46.5094 | 45.274 | 44.5175 | 43.534 | 42.1253 | 40.5717 | 38.8787 | 37.0831 | 34.0542 | 22.8092 | 12.9567 | 10.6561
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | System Transformation | Thermal headroom (MW) | 47.9457 | 47.6094 | 47.5729 | 46.5991 | 46.0564 | 45.0694 | 44.1081 | 42.8311 | 41.3857 | 39.9171 | 37.9704 | 34.5231 | 32.0063 | 29.4876 | 26.4816 | 23.6137 | 11.5975 | 5.709 | 6.043
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | WPD Best View | Thermal headroom (MW) | 47.8559 | 47.1769 | 46.6588 | 45.671 | 44.8269 | 43.2965 | 41.5626 | 39.5254 | 37.0451 | 34.8041 | 32.4877 | 29.3278 | 26.9796 | 24.8396 | 22.2655 | 19.4426 | 8.7008 | 3.013 | 4.1936
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Consumer Transformation | Thermal headroom (MW) | 10.3939 | 9.6507 | 9.4125 | 8.7852 | 8.2138 | 7.7649 | 6.5654 | 5.2497 | 3.8604 | 2.4503 | 1.4282 | 0.26094 | -1.3822 | -2.7954 | -4.657 | -6.0336 | -11.8523 | -14.0817 | -14.368
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Leading the Way | Thermal headroom (MW) | 10.3769 | 9.5909 | 9.4027 | 8.6693 | 8.0334 | 7.5915 | 6.2049 | 4.709 | 2.6909 | 1.5027 | 0.43092 | -0.85346 | -2.2355 | -3.7743 | -4.8641 | -6.1244 | -8.9728 | -9.7206 | -8.5195
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Steady Progression | Thermal headroom (MW) | 10.459 | 10.4231 | 10.5538 | 10.3349 | 10.1652 | 10.1362 | 9.8239 | 9.4191 | 8.6336 | 8.3356 | 7.9655 | 7.5089 | 6.9998 | 6.505 | 5.9797 | 5.099 | 1.8366 | -1.1053 | -2.0201
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | System Transformation | Thermal headroom (MW) | 10.4251 | 10.3244 | 10.3865 | 10.0519 | 9.7698 | 9.307 | 8.7855 | 8.0831 | 7.3118 | 6.8019 | 6.2035 | 5.1521 | 4.3713 | 3.635 | 2.5477 | 1.5138 | -1.8854 | -4.2404 | -4.3604
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | WPD Best View | Thermal headroom (MW) | 10.4199 | 10.2983 | 10.3681 | 10.0215 | 9.7248 | 9.2458 | 8.7061 | 7.9818 | 7.1574 | 6.615 | 6.0124 | 4.9823 | 4.2558 | 3.5998 | 2.6155 | 1.69 | -1.5742 | -4.2358 | -4.3084
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Consumer Transformation | Thermal headroom (MW) | 10.0264 | 9.9601 | 9.919 | 9.8433 | 9.7351 | 9.5561 | 9.1182 | 8.7032 | 8.2766 | 7.4285 | 6.9463 | 6.2879 | 5.6589 | 5.0221 | 4.3404 | 3.7052 | 1.0936 | -0.047323 | 0.070977
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Leading the Way | Thermal headroom (MW) | 10.0243 | 9.9082 | 9.9496 | 9.8898 | 9.8073 | 9.6157 | 9.2186 | 8.7676 | 7.9703 | 7.3805 | 6.8631 | 6.3556 | 5.7941 | 5.2693 | 4.718 | 3.9025 | 2.5319 | 2.4229 | 3.0508
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Steady Progression | Thermal headroom (MW) | 10.0598 | 10.1568 | 10.3912 | 10.437 | 10.5292 | 10.6114 | 10.6293 | 10.7013 | 10.7194 | 10.7453 | 10.7191 | 10.5668 | 10.3567 | 10.132 | 9.8902 | 9.2494 | 7.7879 | 6.3249 | 6.1205
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | System Transformation | Thermal headroom (MW) | 10.0488 | 10.1519 | 10.3022 | 10.3722 | 10.4502 | 10.4796 | 10.508 | 10.5082 | 10.472 | 10.3845 | 10.1277 | 9.5023 | 9.1681 | 8.8008 | 8.4417 | 8.0904 | 6.3755 | 5.5401 | 5.3963
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | WPD Best View | Thermal headroom (MW) | 10.0269 | 9.9126 | 9.9595 | 9.9068 | 9.8335 | 9.6536 | 9.2721 | 8.8432 | 8.0738 | 7.5195 | 7.0446 | 6.5846 | 6.0706 | 5.5913 | 5.0739 | 4.2842 | 2.7324 | 2.4138 | 2.9468
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Consumer Transformation | Thermal headroom (MW) | 17.3365 | 16.3454 | 16.0427 | 15.5464 | 15.0089 | 13.9535 | 12.5037 | 11.2431 | 9.9286 | 8.2107 | 6.705 | 4.8606 | 2.7699 | 1.2418 | -0.75018 | -2.3205 | -9.1194 | -11.8482 | -12.2358
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Leading the Way | Thermal headroom (MW) | 17.2035 | 16.152 | 15.8672 | 15.4036 | 14.8238 | 13.7642 | 12.3537 | 11.112 | 9.4529 | 8.0472 | 6.5917 | 4.8035 | 3.5077 | 1.9075 | 0.68048 | -0.77675 | -4.6933 | -5.747 | -4.0658
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Steady Progression | Thermal headroom (MW) | 17.5163 | 17.4635 | 17.7091 | 17.7403 | 17.7608 | 17.7415 | 17.6601 | 17.6201 | 17.2257 | 17.088 | 16.9434 | 16.6051 | 16.277 | 15.8466 | 15.3929 | 14.564 | 11.0884 | 6.8977 | 5.5662
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | System Transformation | Thermal headroom (MW) | 17.3782 | 17.214 | 17.3356 | 17.3079 | 17.2899 | 16.7956 | 16.5914 | 16.3848 | 16.1538 | 15.8755 | 15.4463 | 14.4329 | 13.8218 | 13.2038 | 12.238 | 11.2961 | 6.2037 | 2.7919 | 2.6188
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | WPD Best View | Thermal headroom (MW) | 17.3769 | 17.2118 | 17.3307 | 17.2994 | 17.2768 | 16.7767 | 16.5646 | 16.347 | 16.0966 | 15.7422 | 15.2723 | 14.2631 | 13.7063 | 13.1686 | 12.2375 | 11.1561 | 6.1035 | 2.7964 | 2.6708
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Consumer Transformation | Thermal headroom (MW) | 1.85 | 1.5777 | 1.1225 | 0.62906 | 0.23782 | -0.18684 | -0.66956 | -1.186 | -1.6988 | -2.2067 | -2.7277 | -3.2701 | -3.7299 | -4.1082 | -4.5066 | -5.0818 | -7.5235 | -8.1966 | -8.0686
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Leading the Way | Thermal headroom (MW) | 1.4825 | 1.1031 | 0.59627 | 0.15699 | -0.31143 | -0.67635 | -1.0848 | -1.5342 | -2.0164 | -2.476 | -2.8669 | -3.1617 | -3.396 | -3.6676 | -4.1469 | -4.5909 | -5.8796 | -5.9353 | -5.0597
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Steady Progression | Thermal headroom (MW) | 2.1709 | 2.1206 | 2.0722 | 1.7925 | 1.5335 | 1.4252 | 1.304 | 1.1911 | 1.0813 | 0.93251 | 0.7376 | 0.48251 | 0.24742 | -0.028013 | -0.28624 | -0.55604 | -2.3628 | -3.6035 | -3.8584
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | System Transformation | Thermal headroom (MW) | 1.8784 | 1.773 | 1.5172 | 1.2119 | 1.0186 | 0.90192 | 0.78551 | 0.63396 | 0.47777 | 0.24437 | -0.06816 | -0.4344 | -0.81355 | -1.1779 | -1.5457 | -1.9027 | -3.5702 | -3.964 | -3.7226
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | WPD Best View | Thermal headroom (MW) | 1.8731 | 1.7667 | 1.501 | 1.1826 | 0.97037 | 0.84126 | 0.70802 | 0.53612 | 0.36775 | 0.11717 | -0.18262 | -0.50369 | -0.80191 | -1.0611 | -1.3053 | -1.5643 | -3.0118 | -3.4792 | -3.2261
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Consumer Transformation | Thermal headroom (MW) | 5.6757 | 5.4214 | 5.1436 | 4.8327 | 4.4662 | 4.002 | 3.3421 | 2.7066 | 2.0283 | 1.0216 | 0.41618 | -0.23088 | -0.79122 | -1.2457 | -1.6942 | -2.0941 | -5.5718 | -7.0088 | -6.894
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Leading the Way | Thermal headroom (MW) | 5.6607 | 5.3446 | 5.1753 | 4.8709 | 4.5115 | 4.0425 | 3.3882 | 2.7524 | 1.7087 | 1.0428 | 0.47914 | 0.02734 | -0.27507 | -0.61366 | -0.82331 | -1.9084 | -3.8424 | -3.9301 | -3.058
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Steady Progression | Thermal headroom (MW) | 5.7691 | 5.8059 | 5.9542 | 5.9254 | 5.9314 | 5.9078 | 5.8391 | 5.734 | 5.5938 | 5.44 | 5.2561 | 4.9894 | 4.6645 | 4.3199 | 3.9267 | 3.1486 | 0.82521 | -1.4634 | -1.9965
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | System Transformation | Thermal headroom (MW) | 5.7195 | 5.7034 | 5.7369 | 5.7152 | 5.6679 | 5.5402 | 5.3696 | 5.1298 | 4.8574 | 4.5395 | 4.1886 | 3.3611 | 2.83 | 2.2645 | 1.6917 | 1.1503 | -1.4203 | -2.5093 | -2.6153
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | WPD Best View | Thermal headroom (MW) | 5.7142 | 5.6971 | 5.7207 | 5.6817 | 5.6168 | 5.4737 | 5.2841 | 5.0213 | 4.735 | 4.4123 | 4.0742 | 3.2918 | 2.8416 | 2.3814 | 1.9322 | 1.5147 | -0.86197 | -2.0246 | -2.1188
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Consumer Transformation | Thermal headroom (MW) | 43.7064 | 42.4618 | 41.6054 | 40.0589 | 37.9795 | 34.6158 | 30.2643 | 26.2518 | 22.479 | 17.929 | 14.1586 | 9.4617 | 5.2979 | 1.4109 | -2.7697 | -7.0815 | -23.074 | -29.2562 | -28.2979
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Leading the Way | Thermal headroom (MW) | 43.5506 | 42.0404 | 41.2408 | 39.6185 | 37.5651 | 34.0695 | 29.6891 | 25.5616 | 20.8639 | 16.9949 | 13.1546 | 9.9129 | 7.01 | 4.1233 | 0.47965 | -3.2042 | -12.2278 | -12.8904 | -6.6783
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Steady Progression | Thermal headroom (MW) | 44.1057 | 44.2135 | 45.0862 | 45.1034 | 44.7364 | 44.3602 | 43.881 | 43.3582 | 42.8208 | 42.1346 | 41.2323 | 39.7333 | 38.1936 | 36.5317 | 34.6983 | 31.8743 | 20.7735 | 11.0597 | 8.7133
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | System Transformation | Thermal headroom (MW) | 43.8702 | 43.7608 | 44.1643 | 43.8644 | 43.3299 | 42.4519 | 41.426 | 40.2132 | 38.7956 | 37.2855 | 35.4057 | 32.4783 | 30.1063 | 27.3002 | 24.6163 | 21.8719 | 9.0453 | 3.1483 | 3.5569
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | WPD Best View | Thermal headroom (MW) | 43.6742 | 42.6984 | 42.1787 | 41.2855 | 39.7086 | 36.9842 | 33.7826 | 30.6498 | 27.0549 | 23.943 | 20.6576 | 17.3957 | 14.6801 | 11.7163 | 8.656 | 5.6619 | -5.3135 | -8.9489 | -5.2484
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Consumer Transformation | Thermal headroom (MW) | -3.3035 | -3.7865 | -4.0662 | -5.0802 | -5.5801 | -6.6173 | -7.8788 | -9.0842 | -10.2923 | -11.5129 | -12.7075 | -13.6359 | -14.4421 | -15.0347 | -15.4134 | -15.5887 | -15.4633 | -15.6204 | -14.5786
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Leading the Way | Thermal headroom (MW) | -3.4159 | -4.0146 | -4.9002 | -5.3973 | -5.9331 | -6.987 | -8.24 | -9.4284 | -10.6092 | -11.778 | -12.799 | -13.1804 | -13.3816 | -13.3193 | -13.0205 | -12.6623 | -11.9751 | -11.3487 | -9.6362
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Steady Progression | Thermal headroom (MW) | -3.1755 | -3.2889 | -3.1383 | -3.2047 | -3.8259 | -3.9068 | -4.0314 | -4.1853 | -4.3892 | -4.6572 | -4.986 | -5.2712 | -5.6161 | -5.9938 | -6.4333 | -6.8833 | -8.7585 | -8.9733 | -8.5342
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | System Transformation | Thermal headroom (MW) | -3.2663 | -3.5033 | -3.4842 | -4.2025 | -4.3527 | -4.5402 | -4.8159 | -5.1464 | -5.5386 | -6.0212 | -6.5828 | -7.0713 | -7.6286 | -8.1762 | -8.7059 | -9.168 | -9.96 | -9.4702 | -8.4645
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | WPD Best View | Thermal headroom (MW) | -3.3868 | -3.904 | -4.7257 | -5.1219 | -5.5176 | -6.3984 | -7.4464 | -8.4518 | -9.4844 | -10.538 | -11.4928 | -11.9412 | -12.3176 | -12.5506 | -12.6304 | -12.6676 | -12.2561 | -11.5339 | -10.2153
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Consumer Transformation | Thermal headroom (MW) | 3.7546 | 3.4854 | 3.2265 | 2.8792 | 2.1503 | 1.3638 | 0.014172 | -0.89534 | -1.9175 | -3.2386 | -4.223 | -5.8076 | -7.0482 | -8.1846 | -9.685 | -10.7728 | -15.5915 | -17.0744 | -16.3818
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Leading the Way | Thermal headroom (MW) | 3.7398 | 3.4047 | 3.2677 | 2.602 | 2.225 | 1.4368 | -0.095884 | -1.0634 | -2.4801 | -3.5176 | -4.533 | -5.8036 | -6.8167 | -7.7942 | -9.1187 | -10.2817 | -12.5606 | -12.5159 | -11.0144
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Steady Progression | Thermal headroom (MW) | 3.8624 | 3.9432 | 4.1816 | 4.1611 | 4.2097 | 4.2437 | 3.9087 | 3.8482 | 3.7429 | 3.6258 | 3.497 | 2.8118 | 2.4345 | 1.99 | 1.5057 | 0.65992 | -2.4152 | -6.1734 | -7.068
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | System Transformation | Thermal headroom (MW) | 3.8062 | 3.8409 | 3.9306 | 3.9202 | 3.8653 | 3.7636 | 3.2148 | 2.9956 | 2.3932 | 2.138 | 1.683 | 0.74461 | 0.10185 | -0.92097 | -1.5885 | -2.2212 | -7.0187 | -9.7052 | -9.9091
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | WPD Best View | Thermal headroom (MW) | 3.7975 | 3.812 | 3.8825 | 3.8386 | 3.7413 | 3.3749 | 2.5547 | 2.0764 | 1.2244 | 0.69753 | 0.23309 | -0.58127 | -1.0146 | -1.7811 | -2.4434 | -3.1346 | -8.0253 | -10.3549 | -10.4413
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Consumer Transformation | Thermal headroom (MW) | 6.5741 | 6.1482 | 5.6882 | 5.1277 | 4.0132 | 2.0125 | 0.34375 | -1.3816 | -2.969 | -4.502 | -5.9544 | -7.3098 | -8.4834 | -9.8568 | -11.3441 | -12.7459 | -17.4568 | -18.6283 | -18.0494
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Leading the Way | Thermal headroom (MW) | 6.5409 | 5.9933 | 5.6581 | 4.9296 | 3.6529 | 1.4602 | -0.24509 | -2.048 | -3.6998 | -5.2538 | -6.5488 | -7.2988 | -8.164 | -9.3231 | -10.489 | -11.4884 | -14.08 | -13.9131 | -11.9831
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Steady Progression | Thermal headroom (MW) | 6.7093 | 6.6773 | 6.7712 | 6.6434 | 6.2135 | 5.5843 | 5.2884 | 4.8341 | 4.4031 | 3.8615 | 3.2624 | 2.6245 | 1.9178 | 1.1413 | 0.3129 | -0.5714 | -4.6214 | -7.0409 | -7.7731
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | System Transformation | Thermal headroom (MW) | 6.6261 | 6.5404 | 6.4338 | 6.3063 | 5.605 | 4.6549 | 4.1539 | 3.4507 | 2.731 | 1.9159 | 1.0063 | 0.038759 | -1.005 | -2.0691 | -3.099 | -4.0791 | -7.6314 | -8.3633 | -7.8884
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | WPD Best View | Thermal headroom (MW) | 6.5588 | 6.1181 | 5.7171 | 5.1675 | 3.9446 | 1.8743 | 0.44487 | -1.0644 | -2.5151 | -3.8934 | -5.1464 | -6.0109 | -6.8235 | -7.7861 | -8.8131 | -9.7185 | -12.9138 | -13.437 | -11.9702
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Consumer Transformation | Thermal headroom (MW) | 1.7816 | 1.2374 | 0.9992 | 0.60064 | 0.14473 | -0.67339 | -1.7503 | -3.027 | -3.9275 | -5.1354 | -5.9681 | -6.7766 | -7.4993 | -8.0551 | -8.5912 | -9.9647 | -14.4821 | -16.1488 | -15.8467
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Leading the Way | Thermal headroom (MW) | 1.7129 | 1.0634 | 0.82607 | 0.3988 | -0.060783 | -0.8628 | -1.9908 | -3.3266 | -4.633 | -5.4689 | -6.1734 | -6.628 | -6.9129 | -7.0213 | -8.1714 | -9.7759 | -12.5029 | -12.4341 | -10.815
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Steady Progression | Thermal headroom (MW) | 1.9031 | 1.7712 | 1.9393 | 1.9181 | 1.9028 | 1.8041 | 1.6917 | 1.3844 | 1.2312 | 1.0319 | 0.77882 | 0.45777 | 0.1301 | -0.2842 | -0.81739 | -1.7498 | -4.0383 | -5.5795 | -5.9644
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | System Transformation | Thermal headroom (MW) | 1.8236 | 1.5636 | 1.6342 | 1.5312 | 1.4395 | 1.2695 | 0.96968 | 0.35178 | 0.017995 | -0.37101 | -0.81325 | -1.6958 | -2.3006 | -2.9005 | -3.6702 | -4.4029 | -6.5015 | -8.0547 | -8.217
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | WPD Best View | Thermal headroom (MW) | 1.8236 | 1.5636 | 1.6342 | 1.5312 | 1.4395 | 1.2695 | 0.96968 | 0.35178 | 0.017995 | -0.37101 | -0.81325 | -1.6958 | -2.3006 | -2.9005 | -3.6702 | -4.4029 | -6.5015 | -8.0547 | -8.217
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Consumer Transformation | Thermal headroom (MW) | 11.3426 | 10.7729 | 10.4455 | 9.961 | 9.3942 | 8.4727 | 6.5728 | 5.2724 | 4.0542 | 2.5775 | 0.96357 | -2.3863 | -5.8077 | -8.7166 | -12.0506 | -15.4271 | -27.7603 | -33.1748 | -34.5538
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Leading the Way | Thermal headroom (MW) | 11.2382 | 10.6266 | 10.4348 | 10.0327 | 9.1521 | 8.2422 | 6.7332 | 5.5389 | 3.9644 | 2.8305 | 0.41438 | -2.4103 | -5.0339 | -8.0034 | -10.9216 | -13.5589 | -21.2095 | -23.4926 | -19.8613
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Steady Progression | Thermal headroom (MW) | 11.5466 | 11.6816 | 12.1575 | 12.3289 | 12.4706 | 12.5804 | 12.6302 | 12.6659 | 12.7022 | 12.7114 | 12.6646 | 12.4633 | 11.866 | 11.5671 | 11.2301 | 10.4688 | 3.9412 | -5.0783 | -7.9832
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | System Transformation | Thermal headroom (MW) | 11.4036 | 11.4503 | 11.7807 | 11.8939 | 11.9565 | 11.9368 | 11.7515 | 11.5867 | 11.3782 | 10.7982 | 10.5082 | 9.727 | 9.2305 | 8.306 | 7.2915 | 5.6717 | -5.6734 | -12.5208 | -13.076
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | WPD Best View | Thermal headroom (MW) | 11.2434 | 10.6349 | 10.4532 | 10.0631 | 9.197 | 8.3034 | 6.8125 | 5.6402 | 4.0845 | 2.9639 | 0.50518 | -2.2958 | -4.8957 | -7.8424 | -10.7437 | -13.3681 | -21.1093 | -23.4972 | -19.9133
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Consumer Transformation | Thermal headroom (MW) | 16.9541 | 16.9226 | 16.9237 | 16.8726 | 16.8025 | 16.713 | 16.5495 | 16.388 | 16.222 | 16.0401 | 15.8767 | 15.6642 | 15.501 | 15.3548 | 15.2451 | 15.0873 | 14.3241 | 13.851 | 13.7717
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Leading the Way | Thermal headroom (MW) | 16.9504 | 16.929 | 16.9469 | 16.8965 | 16.8351 | 16.7511 | 16.5784 | 16.4166 | 16.2438 | 16.0527 | 15.8698 | 15.7273 | 15.6287 | 15.5662 | 15.4704 | 15.4299 | 14.8196 | 14.6471 | 15.032
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Steady Progression | Thermal headroom (MW) | 16.9701 | 17.0103 | 17.0977 | 17.1336 | 17.1604 | 17.1786 | 17.1863 | 17.1841 | 17.1705 | 17.1515 | 17.1052 | 17.0266 | 16.9564 | 16.8622 | 16.7706 | 16.6538 | 16.0409 | 15.5757 | 15.4587
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | System Transformation | Thermal headroom (MW) | 16.9647 | 16.9998 | 17.0789 | 17.1071 | 17.1193 | 17.1238 | 17.1072 | 17.0761 | 17.0205 | 16.9577 | 16.8624 | 16.742 | 16.6105 | 16.4568 | 16.2975 | 16.1417 | 15.5519 | 15.3529 | 15.4326
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | WPD Best View | Thermal headroom (MW) | 16.9504 | 16.929 | 16.9469 | 16.8965 | 16.8351 | 16.7511 | 16.5784 | 16.4166 | 16.2438 | 16.0527 | 15.8698 | 15.7273 | 15.6287 | 15.5662 | 15.4704 | 15.4299 | 14.8196 | 14.6471 | 15.032
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Consumer Transformation | Thermal headroom (MW) | 81.4939 | 80.4628 | 79.3274 | 78.1866 | 76.8798 | 75.1035 | 72.9227 | 70.6916 | 68.5808 | 65.6633 | 63.5466 | 61.5186 | 59.5696 | 57.4875 | 55.4263 | 52.821 | 41.2326 | 36.8882 | 37.1739
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Leading the Way | Thermal headroom (MW) | 81.3491 | 80.1259 | 79.1833 | 78.033 | 76.7562 | 74.9725 | 72.8016 | 70.5766 | 67.645 | 65.4528 | 63.4049 | 61.7996 | 60.0782 | 58.3692 | 55.8924 | 52.38 | 45.5456 | 45.6019 | 49.004
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Steady Progression | Thermal headroom (MW) | 81.8215 | 81.6943 | 81.7896 | 81.5275 | 81.3218 | 81.0167 | 80.655 | 80.1484 | 79.6139 | 78.9807 | 78.1423 | 77.1062 | 75.9611 | 74.6756 | 73.2147 | 70.9114 | 62.3635 | 55.7222 | 53.4253
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | System Transformation | Thermal headroom (MW) | 81.6293 | 81.3132 | 81.07 | 80.7413 | 80.3639 | 79.8172 | 79.0789 | 78.0778 | 77.0876 | 75.9098 | 74.4866 | 72.09 | 70.2266 | 68.2616 | 66.2075 | 64.1644 | 55.4446 | 50.9221 | 50.5876
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | WPD Best View | Thermal headroom (MW) | 81.6169 | 81.2754 | 80.988 | 80.6105 | 80.1781 | 79.5661 | 78.7528 | 77.6773 | 76.6062 | 75.3628 | 73.9196 | 71.5475 | 69.7953 | 68.0018 | 66.0741 | 64.1297 | 55.285 | 51.1173 | 50.9579
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Consumer Transformation | Thermal headroom (MW) | -0.074284 | -0.31024 | -0.57004 | -0.82051 | -1.1182 | -1.4529 | -1.8618 | -2.2666 | -2.6992 | -3.1404 | -3.5765 | -3.9579 | -4.3942 | -4.7803 | -5.0877 | -5.3432 | -7.2825 | -7.9217 | -7.8108
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Leading the Way | Thermal headroom (MW) | -0.11472 | -0.39616 | -0.59205 | -0.83559 | -1.1213 | -1.4395 | -1.8305 | -2.2273 | -2.6655 | -3.1428 | -3.5603 | -3.9837 | -4.3557 | -4.631 | -4.9284 | -5.4726 | -6.7397 | -6.5716 | -5.7535
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Steady Progression | Thermal headroom (MW) | 0.022285 | -0.008301 | 0.012216 | -0.038997 | -0.089007 | -0.13949 | -0.21996 | -0.31394 | -0.44943 | -0.59414 | -0.79503 | -1.0468 | -1.3328 | -1.649 | -1.9967 | -2.3632 | -4.5866 | -6.1699 | -6.7366
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | System Transformation | Thermal headroom (MW) | -0.033778 | -0.11512 | -0.16872 | -0.22759 | -0.31728 | -0.42567 | -0.59605 | -0.80989 | -1.0602 | -1.3545 | -1.6902 | -2.0984 | -2.5639 | -3.0627 | -3.559 | -4.0816 | -6.1483 | -6.7457 | -6.6353
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | WPD Best View | Thermal headroom (MW) | -0.033778 | -0.11512 | -0.16872 | -0.22759 | -0.31728 | -0.42567 | -0.59605 | -0.80989 | -1.0602 | -1.3545 | -1.6902 | -2.0984 | -2.5639 | -3.0627 | -3.559 | -4.0816 | -6.1483 | -6.7457 | -6.6353
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Consumer Transformation | Thermal headroom (MW) | 10.726 | 10.3059 | 9.7205 | 9.2066 | 8.674 | 7.9683 | 7.0917 | 6.2736 | 5.447 | 4.2406 | 3.3372 | 2.4785 | 1.7179 | 0.98092 | 0.2948 | -0.81311 | -5.5846 | -7.5095 | -7.5041
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Leading the Way | Thermal headroom (MW) | 10.6603 | 10.1909 | 9.6005 | 9.0657 | 8.5393 | 7.821 | 6.9627 | 6.197 | 5.0235 | 4.2075 | 3.2992 | 2.7244 | 2.1253 | 1.6413 | 0.63475 | -0.68426 | -3.5004 | -3.7625 | -2.6449
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Steady Progression | Thermal headroom (MW) | 10.8378 | 10.7645 | 10.6693 | 10.5339 | 10.4308 | 10.2975 | 10.1447 | 9.9813 | 9.7909 | 9.559 | 9.1977 | 8.8121 | 8.3968 | 7.9195 | 7.39 | 6.4754 | 3.3677 | 0.75571 | 0.046968
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | System Transformation | Thermal headroom (MW) | 10.7657 | 10.6313 | 10.3993 | 10.2014 | 10.0313 | 9.8132 | 9.5476 | 9.2494 | 8.9074 | 8.4939 | 7.8965 | 6.954 | 6.2875 | 5.5682 | 4.8367 | 4.1131 | 0.79942 | -0.4719 | -0.6197
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | WPD Best View | Thermal headroom (MW) | 10.7605 | 10.623 | 10.3778 | 10.1604 | 9.9704 | 9.7303 | 9.4395 | 9.1107 | 8.7413 | 8.3069 | 7.7053 | 6.7842 | 6.172 | 5.533 | 4.9046 | 4.2626 | 1.1954 | 0.035727 | -0.10097
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Consumer Transformation | Thermal headroom (MW) | 5.2543 | 4.8649 | 4.3228 | 3.7767 | 3.1086 | 2.1467 | 1.0264 | -0.12238 | -1.2446 | -3.1392 | -4.2186 | -5.3454 | -6.3712 | -7.9203 | -9.707 | -11.4949 | -18.7799 | -21.5844 | -21.5657
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Leading the Way | Thermal headroom (MW) | 5.2207 | 4.7297 | 4.3873 | 3.8528 | 3.2049 | 2.1914 | 1.0594 | -0.12003 | -2.0166 | -3.2363 | -4.3236 | -5.1737 | -6.4619 | -8.2422 | -9.976 | -12.2782 | -16.2147 | -16.2628 | -14.6176
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Steady Progression | Thermal headroom (MW) | 5.3879 | 5.4175 | 5.5356 | 5.3639 | 5.249 | 5.0504 | 4.8573 | 4.5867 | 4.29 | 3.9195 | 3.511 | 2.9463 | 2.3086 | 1.628 | 0.85491 | -0.6572 | -5.3011 | -9.2036 | -10.853
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | System Transformation | Thermal headroom (MW) | 5.3221 | 5.3007 | 5.2216 | 5.0833 | 4.8905 | 4.5493 | 4.165 | 3.6788 | 3.1507 | 2.5162 | 1.7993 | 0.2184 | -0.77862 | -1.817 | -2.8868 | -3.9065 | -9.1482 | -13.275 | -13.8695
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | WPD Best View | Thermal headroom (MW) | 5.3055 | 5.241 | 5.0969 | 4.8927 | 4.6229 | 4.1885 | 3.6969 | 3.1112 | 2.4677 | 1.7381 | 0.9893 | -0.57271 | -1.4315 | -2.2527 | -3.2163 | -4.1547 | -9.93 | -13.5402 | -13.8256
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Consumer Transformation | Thermal headroom (MW) | 12.1969 | 11.7233 | 11.045 | 10.2853 | 9.4616 | 7.9355 | 6.1159 | 4.455 | 2.6963 | 0.47188 | -1.4934 | -3.6114 | -5.3281 | -6.8071 | -8.6496 | -10.6909 | -16.8339 | -18.8624 | -17.6974
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Leading the Way | Thermal headroom (MW) | 12.1284 | 11.3125 | 11.0035 | 10.2274 | 9.4043 | 7.8719 | 6.0264 | 4.3599 | 2.3504 | 0.23274 | -1.7109 | -3.336 | -4.4127 | -5.7207 | -6.9654 | -8.4861 | -11.6177 | -11.2236 | -7.8262
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Steady Progression | Thermal headroom (MW) | 12.4058 | 12.6367 | 13.1615 | 12.9339 | 12.9824 | 12.9249 | 12.8739 | 12.771 | 12.6001 | 12.1809 | 11.6752 | 10.9855 | 10.3103 | 9.5335 | 8.6402 | 7.3519 | 2.1782 | -2.1899 | -3.1632
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | System Transformation | Thermal headroom (MW) | 12.296 | 12.4107 | 12.4277 | 12.3849 | 12.2748 | 12.0001 | 11.6729 | 11.253 | 10.7167 | 9.8206 | 8.814 | 7.3608 | 6.1596 | 4.8965 | 3.5655 | 2.0571 | -3.0427 | -4.8424 | -4.1631
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | WPD Best View | Thermal headroom (MW) | 12.3905 | 12.6012 | 13.0722 | 12.7728 | 12.7424 | 12.5872 | 12.423 | 12.1878 | 11.8688 | 11.3073 | 10.6926 | 9.9286 | 9.2418 | 8.5316 | 7.7845 | 6.6219 | 2.211 | -1.2066 | -1.7074
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Consumer Transformation | Thermal headroom (MW) | 8.5376 | 8.4929 | 8.5118 | 8.4314 | 8.3607 | 8.1771 | 7.8999 | 7.6809 | 7.4734 | 6.9997 | 6.4863 | 5.8587 | 5.4689 | 5.0804 | 4.6469 | 3.9754 | 2.4629 | 1.7044 | 1.7969
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Leading the Way | Thermal headroom (MW) | 8.5207 | 8.4423 | 8.5034 | 8.429 | 8.3667 | 8.1926 | 7.9306 | 7.6985 | 7.5004 | 6.9219 | 6.3168 | 5.6416 | 5.2821 | 4.9086 | 4.5821 | 3.9551 | 2.9918 | 2.9887 | 3.9185
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Steady Progression | Thermal headroom (MW) | 8.5784 | 8.6594 | 8.8375 | 8.8922 | 8.9633 | 9.0339 | 9.1024 | 9.1731 | 9.2465 | 9.1519 | 9.0464 | 8.8968 | 8.8719 | 8.8039 | 8.7236 | 8.5018 | 7.7452 | 6.5179 | 6.1497
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | System Transformation | Thermal headroom (MW) | 8.5572 | 8.6204 | 8.7457 | 8.812 | 8.8616 | 8.898 | 8.9363 | 8.9702 | 8.9996 | 8.7567 | 8.5113 | 8.2054 | 8.097 | 7.9793 | 7.7739 | 7.3353 | 6.182 | 5.3217 | 5.4347
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | WPD Best View | Thermal headroom (MW) | 8.5784 | 8.6594 | 8.8375 | 8.8922 | 8.9633 | 9.0339 | 9.1024 | 9.1731 | 9.2465 | 9.1519 | 9.0464 | 8.8968 | 8.8719 | 8.8039 | 8.7236 | 8.5018 | 7.7452 | 6.5179 | 6.1497
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Consumer Transformation | Thermal headroom (MW) | 3.9778 | 3.524 | 3.0138 | 2.4481 | 1.8746 | 0.95893 | -0.17505 | -1.2847 | -2.4263 | -3.9413 | -5.06 | -6.2438 | -7.295 | -8.2078 | -9.7655 | -11.4694 | -17.4834 | -19.396 | -18.9412
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Leading the Way | Thermal headroom (MW) | 3.9297 | 3.4137 | 2.9655 | 2.4291 | 1.8811 | 1.0016 | -0.11541 | -1.1813 | -2.6628 | -3.8258 | -4.8521 | -5.6409 | -6.2567 | -7.3663 | -8.8189 | -10.4479 | -13.7593 | -13.8462 | -12.3111
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Steady Progression | Thermal headroom (MW) | 4.1181 | 4.1519 | 4.2835 | 4.2364 | 4.2126 | 4.1618 | 4.0775 | 3.9449 | 3.7764 | 3.5352 | 3.2639 | 2.8325 | 2.3758 | 1.8444 | 1.2727 | 0.30416 | -2.9503 | -5.8777 | -6.7514
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | System Transformation | Thermal headroom (MW) | 4.0375 | 3.9809 | 3.9321 | 3.8435 | 3.7462 | 3.5881 | 3.3219 | 2.9936 | 2.5859 | 2.0988 | 1.5628 | 0.51933 | -0.24449 | -1.0672 | -1.8848 | -2.6889 | -6.0177 | -7.4884 | -7.7194
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | WPD Best View | Thermal headroom (MW) | 4.1137 | 4.137 | 4.2513 | 4.1683 | 4.1037 | 4.0062 | 3.8624 | 3.657 | 3.4044 | 3.0688 | 2.7082 | 2.186 | 1.6383 | 1.0455 | 0.44185 | -0.51963 | -3.4467 | -5.8156 | -6.3779
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Consumer Transformation | Thermal headroom (MW) | 0.38363 | 0.3106 | 0.23345 | 0.10399 | -0.076542 | -0.37081 | -0.70673 | -0.99292 | -1.3541 | -1.7485 | -2.0958 | -2.4156 | -2.6784 | -2.9033 | -3.1344 | -3.3169 | -3.7541 | -3.8198 | -3.5169
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Leading the Way | Thermal headroom (MW) | 0.37647 | 0.28484 | 0.24431 | 0.10564 | -0.074267 | -0.37372 | -0.72907 | -1.0204 | -1.404 | -1.8118 | -2.1643 | -2.399 | -2.5713 | -2.7452 | -2.8121 | -2.8162 | -2.8829 | -2.6897 | -1.9273
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Steady Progression | Thermal headroom (MW) | 0.4259 | 0.46965 | 0.58317 | 0.59215 | 0.59184 | 0.56397 | 0.52177 | 0.47204 | 0.39133 | 0.27312 | 0.12368 | -0.047106 | -0.26695 | -0.49552 | -0.76109 | -1.0373 | -2.5656 | -3.5878 | -3.7993
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | System Transformation | Thermal headroom (MW) | 0.41045 | 0.43227 | 0.4989 | 0.4994 | 0.46489 | 0.39639 | 0.2872 | 0.15921 | -0.0074321 | -0.22629 | -0.48569 | -0.79589 | -1.1464 | -1.5179 | -1.8915 | -2.2536 | -3.6495 | -3.8913 | -3.6547
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | WPD Best View | Thermal headroom (MW) | 0.41575 | 0.44832 | 0.52701 | 0.49564 | 0.45168 | 0.36792 | 0.26357 | 0.14277 | -0.016273 | -0.20311 | -0.39689 | -0.58338 | -0.7684 | -0.91371 | -1.0461 | -1.2248 | -2.2984 | -2.8273 | -2.8098
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Consumer Transformation | Thermal headroom (MW) | 10.6298 | 10.5576 | 10.2462 | 10.0513 | 9.8511 | 9.3846 | 8.8932 | 8.432 | 7.975 | 7.5686 | 7.1607 | 6.7079 | 6.2874 | 5.9796 | 5.7516 | 5.5764 | 4.9683 | 4.8719 | 5.3284
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Leading the Way | Thermal headroom (MW) | 10.6138 | 10.2748 | 10.2269 | 10.0019 | 9.7769 | 9.2778 | 8.7588 | 8.2831 | 7.798 | 7.4003 | 7.0533 | 6.8063 | 6.6381 | 6.5565 | 6.575 | 6.6259 | 6.4567 | 6.6795 | 7.3849
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Steady Progression | Thermal headroom (MW) | 10.6659 | 10.7523 | 10.9006 | 10.6224 | 10.6196 | 10.5582 | 10.5463 | 10.518 | 10.4787 | 10.437 | 10.3748 | 10.291 | 10.181 | 10.0649 | 9.9116 | 9.7462 | 9.0971 | 8.8905 | 9.0588
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | System Transformation | Thermal headroom (MW) | 10.6421 | 10.7094 | 10.5467 | 10.492 | 10.434 | 10.2977 | 10.227 | 10.1266 | 10.0089 | 9.897 | 9.7549 | 9.5902 | 9.3726 | 9.1639 | 8.9689 | 8.7913 | 8.4851 | 8.6825 | 9.1297
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | WPD Best View | Thermal headroom (MW) | 10.6659 | 10.7523 | 10.9006 | 10.6224 | 10.6196 | 10.5582 | 10.5463 | 10.518 | 10.4787 | 10.437 | 10.3748 | 10.291 | 10.181 | 10.0649 | 9.9116 | 9.7462 | 9.0971 | 8.8905 | 9.0588
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Consumer Transformation | Thermal headroom (MW) | 36.819 | 35.8584 | 35.1961 | 32.2357 | 30.4414 | 28.431 | 25.2295 | 22.1605 | 18.9035 | 14.1992 | 10.7008 | 6.3127 | 2.1806 | -1.9593 | -6.6958 | -11.1111 | -33.4861 | -41.3194 | -40.835
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Leading the Way | Thermal headroom (MW) | 36.7631 | 35.5737 | 33.7873 | 31.6842 | 30.0539 | 28.0103 | 24.6114 | 21.4272 | 16.6043 | 12.8055 | 9.1278 | 5.3456 | 1.4454 | -2.7327 | -6.8245 | -12.0259 | -26.4534 | -27.0129 | -20.0888
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Steady Progression | Thermal headroom (MW) | 37.1139 | 37.3556 | 38.2575 | 37.9538 | 36.5946 | 36.6785 | 36.3749 | 36.0398 | 35.5498 | 34.837 | 33.974 | 32.4277 | 30.9281 | 29.2011 | 27.2777 | 23.839 | 9.6763 | -3.5314 | -6.871
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | System Transformation | Thermal headroom (MW) | 36.9744 | 36.976 | 37.4413 | 35.5926 | 35.2923 | 35.025 | 34.227 | 33.3095 | 31.8509 | 30.3857 | 28.6255 | 25.0714 | 22.4358 | 19.2524 | 16.1618 | 13.0403 | -6.1805 | -14.5361 | -14.4783
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | WPD Best View | Thermal headroom (MW) | 36.7631 | 35.5737 | 33.7873 | 31.6842 | 30.0539 | 28.0103 | 24.6114 | 21.4272 | 16.6043 | 12.8055 | 9.1278 | 5.3456 | 1.4454 | -2.7327 | -6.8245 | -12.0259 | -26.4534 | -27.0129 | -20.0888
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Consumer Transformation | Thermal headroom (MW) | 2.6705 | 2.4653 | 2.4506 | 2.2401 | 2.3317 | 2.3566 | 2.3066 | 2.2021 | 2.0539 | 1.9175 | 1.7454 | 1.5074 | 1.223 | 0.93099 | 0.61035 | 0.31504 | -0.47685 | -0.2416 | 0.44333
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Leading the Way | Thermal headroom (MW) | 2.6695 | 2.3489 | 2.2269 | 1.9059 | 1.9833 | 2.0225 | 1.9484 | 1.8474 | 1.7013 | 1.508 | 1.3307 | 1.0836 | 0.78879 | 0.47848 | 0.21636 | -0.0055413 | -0.17017 | 0.63394 | 2.0176
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Steady Progression | Thermal headroom (MW) | 2.6799 | 2.6194 | 2.7521 | 2.7036 | 2.8628 | 3.0009 | 3.0973 | 3.1745 | 3.2708 | 3.346 | 3.4144 | 3.4241 | 3.4364 | 3.4024 | 3.3863 | 3.3163 | 2.7022 | 1.8999 | 2.2814
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | System Transformation | Thermal headroom (MW) | 2.6754 | 2.5197 | 2.5441 | 2.4074 | 2.5809 | 2.6935 | 2.7545 | 2.7975 | 2.8276 | 2.8535 | 2.8431 | 2.7988 | 2.7385 | 2.6154 | 2.4365 | 2.245 | 1.1843 | 1.1254 | 1.9152
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | WPD Best View | Thermal headroom (MW) | 2.6695 | 2.3489 | 2.2269 | 1.9059 | 1.9833 | 2.0225 | 1.9484 | 1.8474 | 1.7013 | 1.508 | 1.3307 | 1.0836 | 0.78879 | 0.47848 | 0.21636 | -0.0055413 | -0.17017 | 0.63394 | 2.0176
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Consumer Transformation | Thermal headroom (MW) | 17.0676 | 16.6852 | 16.0118 | 15.5351 | 14.8188 | 14.1362 | 13.0931 | 12.069 | 10.8458 | 9.4536 | 7.9761 | 6.1327 | 4.2598 | 2.3331 | 0.42083 | -1.5781 | -8.4808 | -10.8993 | -11.1558
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Leading the Way | Thermal headroom (MW) | 17.0782 | 16.6074 | 16.0339 | 15.6152 | 14.8715 | 14.1262 | 13.0574 | 11.9897 | 10.7313 | 9.1933 | 7.5348 | 5.7461 | 3.863 | 1.9376 | 0.10566 | -1.5095 | -5.9099 | -6.1676 | -3.0454
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Steady Progression | Thermal headroom (MW) | 17.1932 | 17.273 | 17.2714 | 17.2052 | 17.1133 | 17.0909 | 16.9468 | 16.7962 | 16.6216 | 16.3615 | 16.0665 | 15.622 | 15.1042 | 14.4686 | 13.7411 | 12.9278 | 7.0917 | 0.92229 | -0.88078
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | System Transformation | Thermal headroom (MW) | 17.1397 | 17.1174 | 16.8942 | 16.874 | 16.6355 | 16.4864 | 16.1608 | 15.8314 | 15.4328 | 14.919 | 14.3063 | 13.5271 | 12.5266 | 11.3667 | 10.0786 | 8.629 | 1.251 | -2.3656 | -2.1253
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | WPD Best View | Thermal headroom (MW) | 17.0782 | 16.6074 | 16.0339 | 15.6152 | 14.8715 | 14.1262 | 13.0574 | 11.9897 | 10.7313 | 9.1933 | 7.5348 | 5.7461 | 3.863 | 1.9376 | 0.10566 | -1.5095 | -5.9099 | -6.1676 | -3.0454
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Consumer Transformation | Thermal headroom (MW) | 13.678 | 13.3582 | 13.1942 | 11.4206 | 10.851 | 10.2528 | 9.5019 | 8.7396 | 7.9592 | 6.8054 | 5.9146 | 4.8185 | 3.7438 | 2.7026 | 1.5916 | 0.49208 | -3.6584 | -4.9425 | -4.4941
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Leading the Way | Thermal headroom (MW) | 13.6183 | 13.1907 | 12.4409 | 11.0606 | 10.4228 | 9.8255 | 9.0738 | 8.354 | 7.1727 | 6.3075 | 5.4555 | 4.5681 | 3.6336 | 2.6793 | 1.7239 | 0.56507 | -1.4188 | -1.1828 | 0.67382
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Steady Progression | Thermal headroom (MW) | 13.7777 | 13.8266 | 14.1131 | 13.5473 | 12.7365 | 12.8218 | 12.7723 | 12.7854 | 12.7159 | 12.6792 | 12.6089 | 12.4528 | 12.2315 | 12.0012 | 11.7121 | 10.9939 | 8.402 | 5.2004 | 4.7232
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | System Transformation | Thermal headroom (MW) | 13.7088 | 13.6838 | 13.8174 | 12.364 | 12.1159 | 12.0656 | 12.0592 | 11.8847 | 11.6725 | 11.4632 | 11.2034 | 10.5117 | 10.1091 | 9.5967 | 8.9931 | 8.369 | 4.5843 | 2.7877 | 3.1011
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | WPD Best View | Thermal headroom (MW) | 13.6183 | 13.1907 | 12.4409 | 11.0606 | 10.4228 | 9.8255 | 9.0738 | 8.354 | 7.1727 | 6.3075 | 5.4555 | 4.5681 | 3.6336 | 2.6793 | 1.7239 | 0.56507 | -1.4188 | -1.1828 | 0.67382
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Consumer Transformation | Thermal headroom (MW) | 14.137 | 14.1907 | 14.3148 | 13.6876 | 13.7219 | 13.7395 | 13.737 | 13.7047 | 13.6519 | 13.5973 | 13.5456 | 13.5017 | 13.4832 | 13.4974 | 13.5463 | 13.5784 | 13.6329 | 13.725 | 13.9687
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Leading the Way | Thermal headroom (MW) | 14.1274 | 14.1844 | 13.6366 | 13.6778 | 13.7125 | 13.7315 | 13.7373 | 13.695 | 13.6352 | 13.5697 | 13.5221 | 13.5016 | 13.5236 | 13.5926 | 13.6549 | 13.7075 | 14.0377 | 14.3313 | 14.7613
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Steady Progression | Thermal headroom (MW) | 14.1521 | 14.2192 | 14.3661 | 14.4357 | 13.829 | 13.8897 | 13.9397 | 13.9837 | 14.023 | 14.0521 | 14.0657 | 14.0499 | 14.0165 | 13.9745 | 13.9217 | 13.8615 | 13.4798 | 13.2694 | 13.3743
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | System Transformation | Thermal headroom (MW) | 14.1474 | 14.2087 | 14.3554 | 13.7475 | 13.8103 | 13.8605 | 13.899 | 13.9319 | 13.9517 | 13.9454 | 13.9061 | 13.8426 | 13.756 | 13.6642 | 13.5705 | 13.4769 | 13.2467 | 13.3148 | 13.5724
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | WPD Best View | Thermal headroom (MW) | 14.1274 | 14.1844 | 13.6366 | 13.6778 | 13.7125 | 13.7315 | 13.7373 | 13.695 | 13.6352 | 13.5697 | 13.5221 | 13.5016 | 13.5236 | 13.5926 | 13.6549 | 13.7075 | 14.0377 | 14.3313 | 14.7613
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Consumer Transformation | Thermal headroom (MW) | 5.1225 | 4.9739 | 4.833 | 4.6296 | 4.3873 | 4.1174 | 3.6849 | 3.2508 | 2.7949 | 1.9648 | 1.5328 | 1.0519 | 0.61968 | 0.1525 | -0.24303 | -0.55895 | -3.468 | -4.7101 | -4.7483
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Leading the Way | Thermal headroom (MW) | 5.1185 | 4.9811 | 4.8882 | 4.6957 | 4.4615 | 4.2003 | 3.7671 | 3.3472 | 2.5111 | 2.0016 | 1.5673 | 1.2124 | 0.82274 | 0.51199 | 0.22214 | -0.74169 | -2.2923 | -2.462 | -1.9756
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Steady Progression | Thermal headroom (MW) | 5.1659 | 5.2051 | 5.3153 | 5.3203 | 5.3181 | 5.3048 | 5.2615 | 5.183 | 5.0886 | 4.9428 | 4.7985 | 4.6001 | 4.3599 | 4.0833 | 3.7838 | 3.0989 | 1.2029 | -0.53183 | -0.91874
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | System Transformation | Thermal headroom (MW) | 5.1481 | 5.1692 | 5.2433 | 5.2272 | 5.2017 | 5.1336 | 5.0178 | 4.875 | 4.6897 | 4.4573 | 4.1996 | 3.5068 | 3.1088 | 2.6948 | 2.2507 | 1.8371 | -0.39127 | -1.3057 | -1.5611
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | WPD Best View | Thermal headroom (MW) | 5.1185 | 4.9811 | 4.8882 | 4.6957 | 4.4615 | 4.2003 | 3.7671 | 3.3472 | 2.5111 | 2.0016 | 1.5673 | 1.2124 | 0.82274 | 0.51199 | 0.22214 | -0.74169 | -2.2923 | -2.462 | -1.9756
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Consumer Transformation | Thermal headroom (MW) | 8.2605 | 8.0545 | 7.7401 | 7.0162 | 6.5306 | 5.4288 | 3.9228 | 2.5482 | 1.2247 | -0.47657 | -1.8266 | -3.3692 | -4.7958 | -6.2139 | -8.2032 | -10.2228 | -21.5584 | -24.6301 | -24.5689
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Leading the Way | Thermal headroom (MW) | 8.2472 | 8.0045 | 7.4357 | 6.9976 | 6.4624 | 5.317 | 3.6347 | 2.1075 | 0.20282 | -1.3694 | -2.8595 | -4.1556 | -5.6991 | -7.7371 | -9.6389 | -11.7968 | -21.0027 | -21.3226 | -19.4609
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Steady Progression | Thermal headroom (MW) | 8.3266 | 8.3922 | 8.4943 | 8.3868 | 7.9775 | 7.7689 | 7.4335 | 7.0633 | 6.6046 | 6.0913 | 5.5058 | 4.8135 | 4.0459 | 3.2347 | 2.3646 | 1.1077 | -5.1489 | -8.3844 | -9.9655
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | System Transformation | Thermal headroom (MW) | 8.2963 | 8.3425 | 8.3156 | 7.8744 | 7.7131 | 7.3905 | 6.7739 | 6.0979 | 5.3857 | 4.5555 | 3.6388 | 2.1851 | 1.005 | -0.20555 | -1.4271 | -2.6305 | -10.8848 | -14.1341 | -14.3276
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | WPD Best View | Thermal headroom (MW) | 8.2472 | 8.0045 | 7.4357 | 6.9976 | 6.4624 | 5.317 | 3.6347 | 2.1075 | 0.20282 | -1.3694 | -2.8595 | -4.1556 | -5.6991 | -7.7371 | -9.6389 | -11.7968 | -21.0027 | -21.3226 | -19.4609
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Consumer Transformation | Thermal headroom (MW) | 41.9053 | 39.9597 | 38.338 | 36.1128 | 32.9133 | 29.6993 | 24.8087 | 19.8665 | 14.5976 | 8.1487 | 2.6581 | -4.4466 | -10.4481 | -15.7934 | -22.1514 | -27.4967 | -52.6425 | -64.7553 | -66.0016
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Leading the Way | Thermal headroom (MW) | 41.7561 | 39.7848 | 38.3497 | 35.3564 | 32.999 | 29.8438 | 24.8924 | 19.9713 | 13.5782 | 7.6938 | 1.9294 | -4.1295 | -8.9287 | -13.714 | -18.7856 | -23.6921 | -41.7899 | -45.019 | -36.9343
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Steady Progression | Thermal headroom (MW) | 42.4273 | 42.3798 | 42.8991 | 42.7232 | 42.6333 | 42.2683 | 41.5819 | 40.6666 | 39.4787 | 37.9648 | 35.9867 | 32.7445 | 29.798 | 26.5774 | 22.9445 | 18.0071 | -6.1787 | -23.9889 | -29.7339
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | System Transformation | Thermal headroom (MW) | 42.1545 | 41.804 | 41.9465 | 41.3981 | 41.0935 | 40.3259 | 38.9685 | 37.2591 | 34.3808 | 31.6211 | 28.3213 | 23.3464 | 18.7007 | 12.8151 | 7.2415 | 1.587 | -23.7886 | -33.1597 | -34.2977
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | WPD Best View | Thermal headroom (MW) | 41.8554 | 40.3067 | 39.2252 | 37.3547 | 35.5509 | 33.1343 | 29.2331 | 25.2292 | 19.2112 | 14.1136 | 9.1394 | 4.0957 | -0.6926 | -5.8491 | -10.1059 | -14.5796 | -33.3951 | -40.8491 | -36.0283
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Consumer Transformation | Thermal headroom (MW) | 12.911 | 12.5806 | 12.3149 | 11.7672 | 11.2803 | 10.1748 | 8.6502 | 7.3093 | 5.8385 | 4.0492 | 2.5109 | 0.59009 | -1.4063 | -3.2432 | -5.1219 | -6.9458 | -14.1183 | -16.3447 | -16.0174
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Leading the Way | Thermal headroom (MW) | 12.8755 | 12.448 | 12.3128 | 11.7277 | 11.2047 | 10.1425 | 8.5971 | 7.2131 | 5.3382 | 3.857 | 2.3827 | 0.90328 | -0.71505 | -2.2607 | -3.7788 | -5.491 | -9.7999 | -10.0903 | -7.8762
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Steady Progression | Thermal headroom (MW) | 12.9827 | 13.1022 | 13.4 | 13.2615 | 13.3196 | 13.2641 | 13.2496 | 13.1549 | 13.0563 | 12.9452 | 12.7426 | 12.4817 | 12.1421 | 11.6413 | 11.1101 | 10.1701 | 6.28 | 2.3326 | 1.7424
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | System Transformation | Thermal headroom (MW) | 12.9323 | 12.9964 | 13.1353 | 13.0133 | 12.9099 | 12.8799 | 12.6246 | 12.4018 | 12.1846 | 11.8536 | 11.4495 | 10.5202 | 9.8236 | 9.0837 | 8.3591 | 7.5005 | 1.7542 | -0.83944 | -0.67542
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | WPD Best View | Thermal headroom (MW) | 12.9188 | 12.721 | 12.621 | 12.2063 | 11.8611 | 11.4811 | 10.5747 | 9.7624 | 8.8471 | 7.8057 | 6.6722 | 5.0865 | 3.7455 | 2.3844 | 0.99412 | -0.24138 | -5.6821 | -7.3552 | -5.634
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Consumer Transformation | Thermal headroom (MW) | 1.9638 | 1.7631 | 1.5395 | 1.2578 | 0.9034 | 0.48847 | -0.063571 | -0.65469 | -1.2817 | -2.362 | -3.0938 | -3.8753 | -4.5958 | -5.2124 | -5.7102 | -6.1173 | -8.2569 | -9.7633 | -9.9466
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Leading the Way | Thermal headroom (MW) | 1.958 | 1.7733 | 1.5809 | 1.2877 | 0.94128 | 0.5242 | -0.028726 | -0.64156 | -1.6771 | -2.5048 | -3.2744 | -3.9899 | -4.6043 | -5.0252 | -5.2869 | -5.7797 | -7.7727 | -7.9287 | -7.288
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Steady Progression | Thermal headroom (MW) | 2.0254 | 1.9923 | 1.9709 | 1.9055 | 1.815 | 1.703 | 1.5295 | 1.3407 | 1.1061 | 0.8182 | 0.48085 | 0.087223 | -0.37567 | -0.86245 | -1.4332 | -2.4284 | -5.8821 | -8.0651 | -8.7701
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | System Transformation | Thermal headroom (MW) | 2.0096 | 1.9563 | 1.9128 | 1.8154 | 1.6914 | 1.4981 | 1.2721 | 0.97002 | 0.61742 | 0.18283 | -0.32857 | -1.2922 | -2.0045 | -2.8236 | -3.6752 | -4.5231 | -7.9339 | -9.0398 | -9.4359
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | WPD Best View | Thermal headroom (MW) | 1.9649 | 1.7845 | 1.6058 | 1.3287 | 1.0021 | 0.60716 | 0.079348 | -0.50287 | -1.4987 | -2.287 | -3.0373 | -3.7546 | -4.4002 | -4.8763 | -5.2178 | -5.8017 | -7.6179 | -7.9818 | -7.4443
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Consumer Transformation | Thermal headroom (MW) | 5.0904 | 4.925 | 4.809 | 4.6471 | 4.0297 | 3.7158 | 3.2324 | 2.7487 | 2.2374 | 1.7243 | 1.2136 | 0.21405 | -0.38625 | -0.91364 | -2.0225 | -2.7821 | -6.3845 | -7.9523 | -8.2286
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Leading the Way | Thermal headroom (MW) | 5.0749 | 4.9298 | 4.8045 | 4.2762 | 4.0316 | 3.7325 | 3.233 | 2.7576 | 2.2437 | 1.7088 | 1.1259 | 0.2196 | -0.27639 | -1.0181 | -2.1257 | -2.7807 | -4.9973 | -5.7059 | -4.9
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Steady Progression | Thermal headroom (MW) | 5.137 | 5.1242 | 5.1603 | 5.1675 | 5.1537 | 5.0902 | 4.9879 | 4.868 | 4.7135 | 4.5395 | 4.3129 | 3.6742 | 3.3729 | 3.0368 | 2.6629 | 2.2686 | -0.63261 | -3.1159 | -4.0572
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | System Transformation | Thermal headroom (MW) | 5.1006 | 5.0711 | 5.0908 | 5.0278 | 5.0273 | 4.9387 | 4.7795 | 4.597 | 4.007 | 3.7112 | 3.3706 | 2.9706 | 2.5021 | 1.649 | 1.053 | 0.45936 | -2.9485 | -4.4822 | -4.9176
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | WPD Best View | Thermal headroom (MW) | 5.0983 | 5.0609 | 5.0705 | 4.9958 | 4.9155 | 4.7659 | 4.5419 | 4.2987 | 3.6545 | 3.3125 | 2.9655 | 2.5606 | 2.0774 | 1.2598 | 0.79286 | 0.34951 | -2.4917 | -4.4429 | -4.7874
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Consumer Transformation | Thermal headroom (MW) | 10.1239 | 9.9611 | 9.8728 | 9.6739 | 9.4461 | 9.1093 | 8.5272 | 7.9558 | 7.3567 | 6.7447 | 6.1621 | 5.4848 | 4.9043 | 4.2869 | 3.741 | 3.259 | 1.0033 | -0.42114 | -0.69301
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Leading the Way | Thermal headroom (MW) | 10.1116 | 9.9752 | 9.9263 | 9.7515 | 9.538 | 9.2159 | 8.6228 | 8.0569 | 7.4352 | 6.7862 | 6.1754 | 5.7152 | 5.2328 | 4.8047 | 4.5641 | 4.3712 | 2.332 | 1.7709 | 2.8399
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Steady Progression | Thermal headroom (MW) | 10.1754 | 10.2495 | 10.4247 | 10.4876 | 10.5353 | 10.5665 | 10.5805 | 10.5313 | 10.4384 | 10.3223 | 10.1471 | 9.9085 | 9.6147 | 9.2884 | 8.9394 | 8.5615 | 6.3094 | 4.7743 | 4.2623
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | System Transformation | Thermal headroom (MW) | 10.1527 | 10.2042 | 10.3554 | 10.392 | 10.4147 | 10.4154 | 10.3388 | 10.1911 | 9.9999 | 9.7398 | 9.4235 | 9.0099 | 8.5548 | 8.0475 | 7.5198 | 7.0241 | 4.7875 | 4.0886 | 4.1752
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | WPD Best View | Thermal headroom (MW) | 10.1204 | 10.0049 | 9.9821 | 9.8422 | 9.6699 | 9.4462 | 8.9356 | 8.4457 | 7.9164 | 7.3446 | 6.7634 | 6.248 | 5.7823 | 5.3285 | 4.8951 | 4.481 | 3.0015 | 2.0165 | 2.7786
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Consumer Transformation | Thermal headroom (MW) | 4.8965 | 4.4224 | 3.8996 | 3.3915 | 2.8474 | 2.2056 | 1.3235 | 0.46129 | -0.45729 | -1.3827 | -2.2947 | -3.3264 | -4.3179 | -5.1947 | -5.9266 | -6.5319 | -10.0562 | -11.7216 | -11.8788
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Leading the Way | Thermal headroom (MW) | 4.8441 | 4.3337 | 3.8776 | 3.3794 | 2.8749 | 2.2387 | 1.3708 | 0.53265 | -0.40207 | -1.3532 | -2.2984 | -3.2353 | -4.019 | -4.6187 | -4.9914 | -5.609 | -8.3693 | -8.7579 | -7.5366
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Steady Progression | Thermal headroom (MW) | 5.0309 | 4.9544 | 4.9115 | 4.8028 | 4.7156 | 4.5845 | 4.4055 | 4.1707 | 3.9083 | 3.5922 | 3.2163 | 2.7257 | 2.1485 | 1.5518 | 0.88239 | 0.1791 | -4.0934 | -6.9492 | -8.0816
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | System Transformation | Thermal headroom (MW) | 4.9523 | 4.7969 | 4.6449 | 4.4958 | 4.3442 | 4.116 | 3.7823 | 3.3983 | 2.9254 | 2.3823 | 1.7336 | 0.95765 | 0.09751 | -0.82602 | -1.8231 | -2.8857 | -6.762 | -8.0304 | -8.0409
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | WPD Best View | Thermal headroom (MW) | 4.8555 | 4.4264 | 3.9846 | 3.5523 | 3.1158 | 2.5557 | 1.7862 | 1.0421 | 0.21862 | -0.65783 | -1.4999 | -2.3682 | -3.1999 | -3.918 | -4.4694 | -4.9169 | -7.5465 | -8.2859 | -7.3112
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Consumer Transformation | Thermal headroom (MW) | 14.5933 | 14.2738 | 14.0953 | 13.8594 | 13.6261 | 13.3619 | 12.8127 | 12.2785 | 11.7377 | 11.2042 | 10.6836 | 10.0118 | 9.4073 | 8.8381 | 7.9267 | 6.9449 | 3.0691 | 1.1214 | 0.48153
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Leading the Way | Thermal headroom (MW) | 14.5739 | 14.2557 | 14.1083 | 13.9131 | 13.7121 | 13.4645 | 12.9204 | 12.434 | 11.9133 | 11.3636 | 10.8314 | 10.4173 | 10.0452 | 9.5139 | 8.7358 | 8.0269 | 5.4773 | 4.199 | 5.0036
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Steady Progression | Thermal headroom (MW) | 14.6519 | 14.6579 | 14.7987 | 14.8655 | 14.9174 | 14.9654 | 15.0075 | 15.0213 | 15.0319 | 15.0178 | 14.9571 | 14.8428 | 14.6868 | 14.5163 | 14.3299 | 14.1172 | 12.792 | 11.6459 | 11.1348
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | System Transformation | Thermal headroom (MW) | 14.6189 | 14.5786 | 14.6835 | 14.7017 | 14.7446 | 14.7655 | 14.7242 | 14.6887 | 14.6226 | 14.4924 | 14.3282 | 14.114 | 13.8555 | 13.5552 | 13.253 | 12.9491 | 11.6955 | 10.8529 | 10.8208
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | WPD Best View | Thermal headroom (MW) | 14.5739 | 14.2557 | 14.1083 | 13.9131 | 13.7121 | 13.4645 | 12.9204 | 12.434 | 11.9133 | 11.3636 | 10.8314 | 10.4173 | 10.0452 | 9.5139 | 8.7358 | 8.0269 | 5.4773 | 4.199 | 5.0036
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Consumer Transformation | Thermal headroom (MW) | 40.1042 | 38.3594 | 36.5681 | 33.096 | 30.7078 | 27.9234 | 23.7647 | 19.9197 | 15.9592 | 11.1522 | 7.3653 | 2.5796 | -2.2792 | -6.9778 | -11.9588 | -16.2904 | -33.6715 | -40.3352 | -39.3182
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Leading the Way | Thermal headroom (MW) | 39.9373 | 37.7995 | 35.2498 | 31.6835 | 29.6776 | 26.895 | 22.5113 | 18.6319 | 13.6244 | 9.6028 | 6.0083 | 2.0751 | -1.8227 | -5.5638 | -9.2262 | -12.8217 | -22.9087 | -23.8057 | -17.2427
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Steady Progression | Thermal headroom (MW) | 40.5533 | 40.4494 | 40.7622 | 39.847 | 38.8687 | 38.7655 | 38.2658 | 37.7603 | 37.19 | 36.4363 | 35.4648 | 33.5731 | 31.9615 | 30.1264 | 28.1695 | 25.2073 | 13.8076 | 1.5724 | -1.4496
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | System Transformation | Thermal headroom (MW) | 40.2932 | 39.809 | 39.4137 | 37.2941 | 36.7902 | 36.3135 | 35.23 | 34.1286 | 32.3161 | 30.7039 | 28.8037 | 25.609 | 22.9927 | 19.7204 | 16.9738 | 14.3601 | -0.047299 | -7.1978 | -6.9383
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | WPD Best View | Thermal headroom (MW) | 40 | 38.0976 | 35.7129 | 32.5819 | 30.8103 | 28.4191 | 24.5896 | 21.1511 | 16.6444 | 13.0373 | 9.8292 | 6.2355 | 2.8183 | -0.74892 | -4.0822 | -7.5087 | -19.2953 | -22.365 | -17.1827
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Consumer Transformation | Thermal headroom (MW) | 0.23637 | 0.19339 | 0.3393 | 0.27894 | 0.18958 | 0.048378 | -0.30494 | -0.62701 | -0.96573 | -1.686 | -2.2004 | -2.8287 | -4.0024 | -5.3307 | -6.6785 | -8.1489 | -14.0767 | -16.9502 | -17.7008
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Leading the Way | Thermal headroom (MW) | 0.2266 | 0.20751 | 0.40128 | 0.37427 | 0.32755 | 0.16925 | -0.1817 | -0.4982 | -1.2162 | -1.6363 | -2.2111 | -2.9718 | -4.2297 | -5.5348 | -6.763 | -8.2959 | -11.9707 | -13.056 | -11.3894
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Steady Progression | Thermal headroom (MW) | 0.30227 | 0.4788 | 0.87074 | 1.0588 | 1.2184 | 1.3724 | 1.492 | 1.6064 | 1.696 | 1.7634 | 1.8051 | 1.7509 | 1.6747 | 1.5636 | 1.3828 | 0.79953 | -0.79684 | -4.8059 | -5.9391
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | System Transformation | Thermal headroom (MW) | 0.27198 | 0.42999 | 0.78899 | 0.9325 | 1.0744 | 1.18 | 1.2651 | 1.3089 | 1.3146 | 1.2903 | 1.1954 | 0.67339 | 0.41154 | 0.082919 | -0.27268 | -0.65589 | -4.7618 | -7.5838 | -7.8958
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | WPD Best View | Thermal headroom (MW) | 0.2266 | 0.20751 | 0.40128 | 0.37427 | 0.32755 | 0.16925 | -0.1817 | -0.4982 | -1.2162 | -1.6363 | -2.2111 | -2.9718 | -4.2297 | -5.5348 | -6.763 | -8.2959 | -11.9707 | -13.056 | -11.3894
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Consumer Transformation | Thermal headroom (MW) | 9.6391 | 9.3461 | 9.2819 | 8.9222 | 8.194 | 7.8875 | 7.2185 | 6.6597 | 6.0591 | 5.1146 | 4.528 | 3.5055 | 2.9336 | 2.4627 | 1.6294 | 1.2288 | -1.6021 | -3.102 | -2.9411
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Leading the Way | Thermal headroom (MW) | 9.6338 | 9.2338 | 9.221 | 8.4426 | 7.9945 | 7.709 | 6.9666 | 6.3894 | 5.4297 | 4.7979 | 4.24 | 3.4504 | 3.1303 | 2.7714 | 2.2394 | 1.8026 | -0.034193 | -0.48395 | 0.30898
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Steady Progression | Thermal headroom (MW) | 9.6797 | 9.6177 | 9.7971 | 9.6666 | 9.5541 | 9.5694 | 9.4708 | 9.4178 | 9.3442 | 9.2016 | 9.0141 | 8.4234 | 8.1532 | 7.8375 | 7.5001 | 6.7991 | 4.6751 | 2.5504 | 2.0389
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | System Transformation | Thermal headroom (MW) | 9.6588 | 9.5258 | 9.6409 | 9.4628 | 9.2685 | 9.2478 | 9.0489 | 8.9358 | 8.3516 | 8.0793 | 7.7573 | 7.0175 | 6.5836 | 5.7537 | 5.2909 | 4.8596 | 1.7858 | 0.47332 | 0.10156
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | WPD Best View | Thermal headroom (MW) | 9.6338 | 9.2338 | 9.221 | 8.4426 | 7.9945 | 7.709 | 6.9666 | 6.3894 | 5.4297 | 4.7979 | 4.24 | 3.4504 | 3.1303 | 2.7714 | 2.2394 | 1.8026 | -0.034193 | -0.48395 | 0.30898
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Consumer Transformation | Thermal headroom (MW) | 2.0624 | 1.8832 | 1.592 | 1.1721 | 0.93102 | 0.65853 | 0.26483 | -0.14016 | -0.57081 | -0.99273 | -1.3871 | -1.7684 | -2.1218 | -2.5084 | -2.7955 | -3.046 | -4.0011 | -4.5487 | -4.4627
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Leading the Way | Thermal headroom (MW) | 2.0529 | 1.8509 | 1.5769 | 1.0907 | 0.87042 | 0.59756 | 0.19751 | -0.20753 | -0.65092 | -1.0881 | -1.4621 | -1.7606 | -2.0857 | -2.3167 | -2.4373 | -2.4941 | -3.5071 | -3.4496 | -2.7185
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Steady Progression | Thermal headroom (MW) | 2.1201 | 2.1371 | 2.1315 | 1.9505 | 1.9402 | 1.9105 | 1.8402 | 1.7388 | 1.6378 | 1.4991 | 1.3316 | 1.1174 | 0.8689 | 0.59059 | 0.28254 | -0.02796 | -1.8372 | -3.1759 | -3.5787
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | System Transformation | Thermal headroom (MW) | 2.0922 | 2.0768 | 1.982 | 1.7386 | 1.6999 | 1.6128 | 1.4804 | 1.2868 | 1.0627 | 0.80779 | 0.52777 | 0.17426 | -0.21922 | -0.64379 | -1.0629 | -1.4649 | -3.1703 | -3.6122 | -3.4755
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | WPD Best View | Thermal headroom (MW) | 2.0581 | 1.8621 | 1.6018 | 1.1317 | 0.93125 | 0.68052 | 0.30559 | -0.068843 | -0.48484 | -0.90119 | -1.271 | -1.5786 | -1.8816 | -2.1678 | -2.3682 | -2.516 | -3.344 | -3.494 | -2.8664
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Consumer Transformation | Thermal headroom (MW) | 6.6901 | 5.3867 | 4.0663 | 2.6602 | 1.5993 | 0.28667 | -1.3403 | -3.0766 | -4.7694 | -6.3747 | -7.6437 | -8.9445 | -10.4785 | -11.9643 | -13.5711 | -14.9668 | -19.6381 | -20.7505 | -20.1141
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Leading the Way | Thermal headroom (MW) | 6.5435 | 4.8486 | 3.4547 | 1.7847 | 0.59262 | -0.71978 | -2.385 | -4.1152 | -5.8642 | -7.4697 | -8.5405 | -9.6183 | -10.6818 | -11.7458 | -12.7644 | -13.586 | -15.9259 | -16.01 | -14.2689
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Steady Progression | Thermal headroom (MW) | 6.9012 | 6.3488 | 5.9444 | 5.1782 | 4.7622 | 4.4753 | 4.1594 | 3.7173 | 3.259 | 2.774 | 2.3113 | 1.7636 | 1.183 | 0.57156 | -0.064096 | -0.72769 | -3.6157 | -6.2075 | -6.8434
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | System Transformation | Thermal headroom (MW) | 6.7483 | 5.9093 | 5.0782 | 4.1548 | 3.5905 | 3.193 | 2.7021 | 1.9471 | 1.1805 | 0.36307 | -0.33654 | -1.1085 | -1.9183 | -2.7563 | -3.5684 | -4.3029 | -6.9176 | -7.565 | -7.0206
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | WPD Best View | Thermal headroom (MW) | 6.5487 | 4.8569 | 3.4732 | 1.8151 | 0.63761 | -0.65861 | -2.3057 | -3.9765 | -5.6981 | -7.2828 | -8.3934 | -9.5038 | -10.5435 | -11.5848 | -12.5865 | -13.3951 | -15.8257 | -16.0146 | -14.3209
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Consumer Transformation | Thermal headroom (MW) | 8.1341 | 7.8047 | 7.2083 | 6.4721 | 6.1447 | 5.4947 | 4.5573 | 3.7142 | 2.9507 | 1.763 | 0.8562 | -0.3165 | -1.4593 | -2.5798 | -3.7046 | -4.8732 | -9.4388 | -11.4069 | -11.5523
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Leading the Way | Thermal headroom (MW) | 8.1041 | 7.772 | 7.0646 | 6.1872 | 5.8861 | 5.2268 | 4.2777 | 3.464 | 2.2737 | 1.4971 | 0.61188 | -0.30047 | -1.215 | -2.1493 | -3.0511 | -4.2898 | -6.947 | -7.6288 | -6.5871
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Steady Progression | Thermal headroom (MW) | 8.2188 | 8.2317 | 8.0802 | 7.8249 | 7.8119 | 7.7749 | 7.7395 | 7.66 | 7.6034 | 7.5218 | 7.3142 | 7.0007 | 6.6795 | 6.2986 | 5.8982 | 5.094 | 2.9496 | 0.93504 | 0.47286
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | System Transformation | Thermal headroom (MW) | 8.1712 | 8.1371 | 7.8372 | 7.3963 | 7.3807 | 7.2797 | 7.1315 | 7.0176 | 6.8648 | 6.6065 | 6.2223 | 5.4331 | 4.9207 | 4.3714 | 3.8099 | 3.2798 | 0.85876 | -1.0805 | -1.3356
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | WPD Best View | Thermal headroom (MW) | 8.1274 | 7.8364 | 7.1547 | 6.3517 | 6.0972 | 5.5838 | 4.7751 | 4.0666 | 3.0418 | 2.3768 | 1.629 | 0.89408 | 0.11662 | -0.66851 | -1.4908 | -2.6959 | -5.9203 | -7.1993 | -6.5638
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Consumer Transformation | Thermal headroom (MW) | 7.883 | 7.697 | 7.4778 | 7.0636 | 6.7185 | 6.0068 | 5.1235 | 4.286 | 3.3737 | 2.4412 | 1.5366 | 0.44148 | -1.2331 | -2.8026 | -4.1963 | -5.5596 | -10.0624 | -11.2641 | -11.0071
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Leading the Way | Thermal headroom (MW) | 7.8622 | 7.6575 | 7.4387 | 6.9675 | 6.608 | 5.8963 | 4.9428 | 4.0961 | 3.1486 | 2.2081 | 1.3768 | 0.43498 | -0.99679 | -2.4074 | -3.5143 | -4.4681 | -6.9942 | -6.9638 | -5.0952
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Steady Progression | Thermal headroom (MW) | 7.9484 | 8.0536 | 8.2049 | 8.1351 | 8.139 | 8.1016 | 8.0552 | 7.9616 | 7.8384 | 7.6891 | 7.4875 | 7.2192 | 6.9046 | 6.5516 | 6.2573 | 5.9049 | 4.0955 | 1.2124 | 0.36221
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | System Transformation | Thermal headroom (MW) | 7.9043 | 7.9628 | 8.0073 | 7.8613 | 7.7864 | 7.6764 | 7.4818 | 7.2667 | 6.9876 | 6.6568 | 6.2954 | 5.8388 | 5.3398 | 4.7948 | 4.3482 | 3.9112 | 1.0679 | -0.92077 | -0.66816
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | WPD Best View | Thermal headroom (MW) | 7.8674 | 7.6658 | 7.4571 | 6.9979 | 6.653 | 5.9575 | 5.0222 | 4.1974 | 3.2688 | 2.3415 | 1.5098 | 0.54952 | -0.85854 | -2.2464 | -3.3363 | -4.2772 | -6.894 | -6.9684 | -5.1472
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Consumer Transformation | Thermal headroom (MW) | 31.212 | 29.2023 | 27.7301 | 26.4221 | 24.1774 | 21.5145 | 18.0999 | 14.5511 | 11.2481 | 5.6488 | 2.2391 | -1.6985 | -6.0608 | -9.2329 | -12.9218 | -15.6535 | -31.4758 | -38.8296 | -38.5404
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Leading the Way | Thermal headroom (MW) | 31.1539 | 28.8349 | 27.6556 | 26.1744 | 24.1149 | 21.2991 | 17.6688 | 13.8706 | 8.2381 | 4.5567 | 0.96238 | -3.0211 | -6.2708 | -9.1376 | -11.3935 | -16.5516 | -26.6192 | -26.7151 | -22.6788
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Steady Progression | Thermal headroom (MW) | 31.5453 | 31.4369 | 31.6771 | 31.4961 | 31.2817 | 30.7833 | 30.0645 | 29.0767 | 27.5624 | 26.4461 | 25.1133 | 23.1261 | 21.0489 | 18.8934 | 16.4566 | 11.7324 | -3.9885 | -16.0756 | -19.858
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | System Transformation | Thermal headroom (MW) | 31.3913 | 30.9747 | 30.669 | 30.5593 | 30.0444 | 28.4409 | 26.9018 | 25.2328 | 23.3229 | 21.3843 | 19.1097 | 14.1481 | 10.7828 | 7.2304 | 3.0086 | -1.2354 | -18.5065 | -25.7498 | -27.1849
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | WPD Best View | Thermal headroom (MW) | 31.3947 | 30.9067 | 30.4873 | 30.3023 | 29.657 | 27.9446 | 26.3193 | 24.588 | 22.6426 | 20.1209 | 17.877 | 13.6394 | 10.4655 | 7.0292 | 3.0879 | -0.88803 | -17.6989 | -25.2733 | -26.3716
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Consumer Transformation | Thermal headroom (MW) | 10.8801 | 10.3112 | 9.8131 | 9.7951 | 9.3766 | 8.6603 | 8.2698 | 7.9272 | 7.5107 | 7.0448 | 6.569 | 6.0718 | 5.4896 | 5.005 | 4.4117 | 3.9254 | 2.6109 | 2.8437 | 3.639
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Leading the Way | Thermal headroom (MW) | 10.8758 | 10.1193 | 9.4414 | 9.4353 | 8.9079 | 8.0899 | 7.665 | 7.2885 | 6.9005 | 6.4263 | 5.9801 | 5.587 | 5.1639 | 4.7787 | 4.2645 | 3.9436 | 3.5674 | 4.2733 | 5.293
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Steady Progression | Thermal headroom (MW) | 10.9161 | 10.6022 | 10.3933 | 10.4851 | 10.2887 | 10.0086 | 9.9818 | 9.9548 | 9.8869 | 9.8134 | 9.7218 | 9.5873 | 9.4279 | 9.2967 | 9.0975 | 8.9293 | 7.9802 | 7.0305 | 7.1094
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | System Transformation | Thermal headroom (MW) | 10.8999 | 10.4201 | 10.0403 | 10.1183 | 9.841 | 9.4052 | 9.2621 | 9.1696 | 9.0507 | 8.8904 | 8.706 | 8.5393 | 8.275 | 8.0421 | 7.7131 | 7.4252 | 6.2982 | 6.1364 | 6.7072
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | WPD Best View | Thermal headroom (MW) | 10.8999 | 10.4201 | 10.0403 | 10.1183 | 9.841 | 9.4052 | 9.2621 | 9.1696 | 9.0507 | 8.8904 | 8.706 | 8.5393 | 8.275 | 8.0421 | 7.7131 | 7.4252 | 6.2982 | 6.1364 | 6.7072
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Consumer Transformation | Thermal headroom (MW) | 3.049 | 2.9741 | 2.8645 | 2.7652 | 2.6488 | 2.5169 | 2.3231 | 2.136 | 1.9311 | 1.3577 | 1.1521 | 0.93631 | 0.74497 | 0.53515 | 0.35163 | 0.20501 | -0.80856 | -1.5637 | -1.5783
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Leading the Way | Thermal headroom (MW) | 3.045 | 2.9387 | 2.8926 | 2.8011 | 2.6833 | 2.5596 | 2.3649 | 2.1741 | 1.6068 | 1.3523 | 1.1499 | 0.98265 | 0.79317 | 0.64569 | 0.54412 | 0.1287 | -0.45201 | -0.51313 | -0.52023
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Steady Progression | Thermal headroom (MW) | 3.0701 | 3.0876 | 3.1329 | 3.0964 | 3.0927 | 3.0819 | 3.0667 | 3.0223 | 2.9706 | 2.9077 | 2.8299 | 2.7229 | 2.6062 | 2.4836 | 2.3327 | 1.8129 | 0.9223 | -0.038896 | -0.26824
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | System Transformation | Thermal headroom (MW) | 3.0591 | 3.0686 | 3.0538 | 3.0511 | 3.0298 | 2.9843 | 2.9238 | 2.8497 | 2.7435 | 2.6269 | 2.4917 | 1.9705 | 1.78 | 1.5686 | 1.3508 | 1.143 | -0.091746 | -0.7059 | -1.0289
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | WPD Best View | Thermal headroom (MW) | 3.0591 | 3.0686 | 3.0538 | 3.0511 | 3.0298 | 2.9843 | 2.9238 | 2.8497 | 2.7435 | 2.6269 | 2.4917 | 1.9705 | 1.78 | 1.5686 | 1.3508 | 1.143 | -0.091746 | -0.7059 | -1.0289
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Consumer Transformation | Thermal headroom (MW) | 1.569 | 1.458 | 1.358 | 1.1955 | 0.8943 | 0.53418 | 0.087536 | -0.44358 | -0.97813 | -1.8775 | -2.4348 | -3.0455 | -3.6109 | -4.0963 | -4.4756 | -4.7909 | -7.0663 | -8.1515 | -8.1388
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Leading the Way | Thermal headroom (MW) | 1.5626 | 1.4359 | 1.396 | 1.2197 | 0.93612 | 0.56642 | 0.1146 | -0.43209 | -1.3528 | -1.9222 | -2.5704 | -3.1517 | -3.642 | -3.9769 | -4.177 | -5.1794 | -6.7616 | -6.6723 | -6.0995
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Steady Progression | Thermal headroom (MW) | 1.6198 | 1.6579 | 1.7282 | 1.7211 | 1.7582 | 1.7297 | 1.6243 | 1.464 | 1.2684 | 1.0642 | 0.80256 | 0.47311 | 0.12026 | -0.291 | -0.73579 | -1.5689 | -4.3639 | -6.1861 | -6.7642
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | System Transformation | Thermal headroom (MW) | 1.595 | 1.6094 | 1.6309 | 1.6325 | 1.6349 | 1.508 | 1.3106 | 1.0576 | 0.74257 | 0.3824 | -0.029807 | -0.90559 | -1.4676 | -2.0836 | -2.7902 | -3.4914 | -6.3035 | -7.2012 | -7.5152
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | WPD Best View | Thermal headroom (MW) | 1.5943 | 1.5606 | 1.5077 | 1.4572 | 1.374 | 1.1736 | 0.91106 | 0.60812 | 0.25106 | -0.48027 | -0.8965 | -1.3467 | -1.8188 | -2.3861 | -2.9427 | -3.4932 | -6.0052 | -7.0486 | -7.0822
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Consumer Transformation | Thermal headroom (MW) | 5.3696 | 5.0655 | 4.7267 | 4.3433 | 3.5602 | 3.0716 | 2.3313 | 1.5418 | 0.76517 | -0.012968 | -0.80986 | -2.0552 | -3.1923 | -3.8424 | -5.0533 | -6.2855 | -11.4093 | -13.1566 | -12.8679
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Leading the Way | Thermal headroom (MW) | 5.3425 | 4.9331 | 4.7598 | 4.0325 | 3.6277 | 3.1392 | 2.3907 | 1.6253 | 0.8232 | 0.027508 | -0.77441 | -1.7661 | -2.8059 | -3.419 | -4.9512 | -5.9507 | -9.1129 | -9.4074 | -7.5905
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Steady Progression | Thermal headroom (MW) | 5.4742 | 5.5447 | 5.7625 | 5.7057 | 5.7304 | 5.7107 | 5.6728 | 5.584 | 5.4837 | 5.3174 | 5.1197 | 4.4207 | 3.8259 | 3.3971 | 2.946 | 2.4552 | -0.47679 | -3.0452 | -4.0038
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | System Transformation | Thermal headroom (MW) | 5.4195 | 5.4383 | 5.4747 | 5.4399 | 5.4012 | 5.3251 | 5.1463 | 4.9254 | 4.2731 | 3.9285 | 3.5024 | 2.9598 | 1.9578 | 0.92333 | 0.2527 | -0.36711 | -3.8157 | -5.7472 | -5.837
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | WPD Best View | Thermal headroom (MW) | 5.4276 | 5.4594 | 5.5102 | 5.4934 | 5.4716 | 5.4159 | 5.2738 | 5.0877 | 4.4959 | 4.1933 | 3.835 | 3.3452 | 2.4242 | 1.4561 | 0.85005 | 0.26983 | -3.2328 | -5.3338 | -5.644
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Consumer Transformation | Thermal headroom (MW) | 5.7699 | 5.1517 | 4.8972 | 4.5633 | 4.1555 | 3.6234 | 2.7417 | 1.843 | 1.1664 | 0.11028 | -0.57154 | -1.346 | -2.4704 | -3.1155 | -3.9917 | -4.4469 | -7.7833 | -9.4427 | -9.7503
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Leading the Way | Thermal headroom (MW) | 5.7589 | 5.1505 | 4.9382 | 4.6083 | 4.2259 | 3.6445 | 2.6548 | 1.6314 | 0.53423 | -0.21914 | -0.94249 | -2.0024 | -2.6245 | -3.407 | -3.6453 | -4.5998 | -6.9669 | -7.2646 | -6.452
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Steady Progression | Thermal headroom (MW) | 5.8347 | 5.8311 | 5.8594 | 5.7916 | 5.717 | 5.6019 | 5.3136 | 4.9828 | 4.3961 | 4.1131 | 3.7998 | 3.3928 | 2.9474 | 2.4518 | 1.9071 | 0.98563 | -2.9153 | -5.5346 | -6.6109
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | System Transformation | Thermal headroom (MW) | 5.8104 | 5.7542 | 5.7469 | 5.6539 | 5.5208 | 4.9749 | 4.4555 | 3.9249 | 3.5259 | 3.0889 | 2.5684 | 1.5614 | 0.8488 | 0.10684 | -1.0267 | -2.2355 | -6.2061 | -7.977 | -8.2344
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | WPD Best View | Thermal headroom (MW) | 5.8104 | 5.7542 | 5.7469 | 5.6539 | 5.5208 | 4.9749 | 4.4555 | 3.9249 | 3.5259 | 3.0889 | 2.5684 | 1.5614 | 0.8488 | 0.10684 | -1.0267 | -2.2355 | -6.2061 | -7.977 | -8.2344
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Consumer Transformation | Thermal headroom (MW) | 57.5692 | 55.7738 | 54.1446 | 51.6802 | 48.8728 | 44.7558 | 39.4613 | 34.2866 | 29.0523 | 22.7075 | 16.6061 | 10.12 | 3.848 | -1.8316 | -7.0966 | -11.7925 | -31.3324 | -40.1718 | -40.6144
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Leading the Way | Thermal headroom (MW) | 57.437 | 55.6287 | 54.1089 | 51.4553 | 48.5086 | 44.3234 | 38.8891 | 33.648 | 27.6898 | 21.337 | 15.2447 | 10.1682 | 5.4733 | 1.1307 | -2.4094 | -5.663 | -20.4643 | -21.7019 | -13.6465
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Steady Progression | Thermal headroom (MW) | 58.0704 | 57.8582 | 58.1381 | 57.6506 | 56.9751 | 56.278 | 55.3048 | 54.0817 | 52.6846 | 50.9529 | 48.9436 | 46.5098 | 43.6722 | 40.4546 | 36.9173 | 32.721 | 10.7318 | -4.5023 | -9.2621
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | System Transformation | Thermal headroom (MW) | 57.8486 | 57.3849 | 57.3389 | 56.4056 | 55.3389 | 54.0746 | 52.3573 | 50.2735 | 47.9821 | 45.0724 | 41.8786 | 37.64 | 33.1999 | 28.1965 | 22.9507 | 17.7443 | -4.0941 | -11.5387 | -11.2618
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | WPD Best View | Thermal headroom (MW) | 57.6519 | 56.6943 | 56.0417 | 54.3684 | 52.5047 | 50.1324 | 47.1641 | 44.0172 | 40.471 | 36.3386 | 32.2047 | 27.7831 | 23.913 | 20.542 | 17.3116 | 14.3158 | -1.0371 | -6.432 | -2.8473
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Consumer Transformation | Thermal headroom (MW) | 21.4581 | 20.8776 | 20.4521 | 19.9453 | 19.4256 | 18.7886 | 17.6599 | 16.5751 | 15.5772 | 14.3198 | 12.7439 | 10.7123 | 8.5996 | 6.3881 | 4.0715 | 2.0102 | -6.2845 | -9.7052 | -10.5857
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Leading the Way | Thermal headroom (MW) | 21.4248 | 20.8013 | 20.4581 | 19.9821 | 19.5034 | 18.8745 | 17.7639 | 16.6832 | 15.6735 | 14.2185 | 12.4506 | 10.7774 | 8.9384 | 6.7242 | 4.578 | 2.9465 | -2.8452 | -4.1738 | -1.9334
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Steady Progression | Thermal headroom (MW) | 21.5931 | 21.5154 | 21.6175 | 21.5984 | 21.5834 | 21.5514 | 21.4647 | 21.3122 | 21.2065 | 21.0312 | 20.7992 | 20.4613 | 20.0454 | 19.5105 | 18.9377 | 18.4106 | 13.4161 | 7.7774 | 5.7403
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | System Transformation | Thermal headroom (MW) | 21.5154 | 21.3367 | 21.3658 | 21.2921 | 21.2227 | 21.1192 | 20.8937 | 20.5581 | 20.2883 | 19.92 | 19.4852 | 18.953 | 18.2992 | 17.476 | 16.4188 | 15.2067 | 7.9898 | 4.0613 | 3.7869
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | WPD Best View | Thermal headroom (MW) | 21.5102 | 21.3283 | 21.3474 | 21.2617 | 21.1777 | 21.0581 | 20.8143 | 20.4557 | 20.1222 | 19.733 | 19.2941 | 18.7832 | 18.1837 | 17.4408 | 16.2409 | 15.0158 | 7.8896 | 4.0658 | 3.8389
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Consumer Transformation | Thermal headroom (MW) | 5.5122 | 5.3769 | 5.2272 | 5.0255 | 4.7885 | 4.4903 | 4.1366 | 3.7689 | 3.3669 | 2.9018 | 2.4309 | 1.9495 | 1.5054 | 1.1323 | 0.83846 | 0.60272 | -0.42432 | -1.0812 | -1.171
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Leading the Way | Thermal headroom (MW) | 5.5032 | 5.3825 | 5.2428 | 5.0315 | 4.7934 | 4.4937 | 4.1279 | 3.7529 | 3.3041 | 2.7996 | 2.301 | 1.8542 | 1.4788 | 1.2279 | 1.08 | 0.99337 | -0.18825 | -0.21377 | 0.40485
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Steady Progression | Thermal headroom (MW) | 5.5549 | 5.5238 | 5.5043 | 5.4545 | 5.3806 | 5.2977 | 5.1854 | 5.0587 | 4.9036 | 4.7211 | 4.4953 | 4.2382 | 3.9375 | 3.6077 | 3.2424 | 2.8266 | 0.57733 | -0.72521 | -1.2096
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | System Transformation | Thermal headroom (MW) | 5.5404 | 5.4968 | 5.4611 | 5.3788 | 5.2801 | 5.1537 | 4.9872 | 4.7847 | 4.5449 | 4.2498 | 3.9259 | 3.5245 | 3.0561 | 2.5157 | 1.9667 | 1.4237 | -0.55054 | -1.0639 | -1.0949
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | WPD Best View | Thermal headroom (MW) | 5.5102 | 5.3937 | 5.2676 | 5.0726 | 4.8542 | 4.5766 | 4.2359 | 3.8916 | 3.4805 | 3.0174 | 2.5381 | 2.0895 | 1.6829 | 1.3768 | 1.1492 | 0.9714 | -0.033514 | -0.26685 | 0.24853
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Consumer Transformation | Thermal headroom (MW) | 9.6568 | 9.5047 | 9.4461 | 9.1385 | 8.8742 | 8.3685 | 7.6612 | 6.9376 | 6.1467 | 5.3503 | 4.5437 | 3.8992 | 3.1678 | 2.5014 | 1.7732 | 1.134 | -0.97418 | -1.4369 | -1.0341
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Leading the Way | Thermal headroom (MW) | 9.6332 | 9.4683 | 9.4173 | 9.0432 | 8.6889 | 8.1399 | 7.4091 | 6.6857 | 5.8793 | 5.0974 | 4.3989 | 4.0478 | 3.5966 | 3.0936 | 2.5959 | 2.1621 | 1.0647 | 1.2115 | 2.3057
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Steady Progression | Thermal headroom (MW) | 9.7105 | 9.7339 | 9.9001 | 9.8242 | 9.7923 | 9.8131 | 9.7712 | 9.646 | 9.4965 | 9.3166 | 9.1099 | 8.8545 | 8.5705 | 8.2607 | 7.9332 | 7.5726 | 5.9425 | 4.9919 | 4.87
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | System Transformation | Thermal headroom (MW) | 9.6798 | 9.6865 | 9.7943 | 9.628 | 9.5412 | 9.4611 | 9.2996 | 9.0819 | 8.8195 | 8.5005 | 8.0919 | 7.7014 | 7.28 | 6.8476 | 6.4157 | 6.0339 | 4.9244 | 4.6429 | 5.0312
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | WPD Best View | Thermal headroom (MW) | 9.6785 | 9.6844 | 9.7893 | 9.6195 | 9.5281 | 9.3858 | 9.2128 | 8.9801 | 8.6994 | 8.3136 | 7.9008 | 7.5316 | 7.1645 | 6.8124 | 6.4835 | 6.2101 | 5.3204 | 4.8945 | 5.2697
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Consumer Transformation | Thermal headroom (MW) | 12.1762 | 11.9436 | 11.7601 | 11.51 | 11.2441 | 10.661 | 9.9451 | 9.3458 | 8.8889 | 7.999 | 7.5381 | 7.0224 | 6.5705 | 6.2065 | 5.9316 | 5.4819 | 2.9133 | 1.7558 | 1.7054
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Leading the Way | Thermal headroom (MW) | 12.1565 | 11.8758 | 11.661 | 11.3641 | 11.0712 | 10.481 | 9.7324 | 9.1508 | 8.3543 | 7.8416 | 7.4959 | 7.2818 | 7.1418 | 7.0546 | 7.0054 | 6.3096 | 4.9404 | 4.6122 | 5.0582
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Steady Progression | Thermal headroom (MW) | 12.2106 | 12.1652 | 12.1937 | 12.1343 | 12.0716 | 11.9921 | 11.9056 | 11.8398 | 11.7817 | 11.6782 | 11.6052 | 11.5112 | 11.3815 | 11.2206 | 11.0422 | 10.501 | 9.6034 | 8.8138 | 8.843
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | System Transformation | Thermal headroom (MW) | 12.189 | 12.0925 | 12.0653 | 11.9562 | 11.843 | 11.6993 | 11.5493 | 11.4118 | 11.3216 | 11.1447 | 10.9954 | 10.4485 | 10.2288 | 10.0057 | 9.8022 | 9.6067 | 8.6192 | 8.1194 | 8.0157
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | WPD Best View | Thermal headroom (MW) | 12.189 | 12.0925 | 12.0653 | 11.9562 | 11.843 | 11.6993 | 11.5493 | 11.4118 | 11.3216 | 11.1447 | 10.9954 | 10.4485 | 10.2288 | 10.0057 | 9.8022 | 9.6067 | 8.6192 | 8.1194 | 8.0157
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Consumer Transformation | Thermal headroom (MW) | -4.0592 | -4.1924 | -4.3703 | -4.7294 | -5.2565 | -6.078 | -6.9886 | -7.8649 | -8.802 | -9.7716 | -10.654 | -11.5282 | -12.3028 | -12.928 | -13.5072 | -13.9405 | -15.4619 | -15.8903 | -15.3428
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Leading the Way | Thermal headroom (MW) | -4.0687 | -4.1851 | -4.3537 | -4.7656 | -5.3513 | -6.1923 | -7.1368 | -8.066 | -9.0638 | -10.0972 | -10.8759 | -11.469 | -11.8959 | -12.2955 | -12.5482 | -12.6293 | -13.2099 | -12.8298 | -11.6363
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Steady Progression | Thermal headroom (MW) | -3.9981 | -3.941 | -3.8366 | -3.9054 | -4.0762 | -4.2337 | -4.3957 | -4.6172 | -4.8936 | -5.215 | -5.5424 | -5.9621 | -6.4156 | -6.9254 | -7.4956 | -8.0514 | -10.9868 | -12.3147 | -12.5387
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | System Transformation | Thermal headroom (MW) | -4.0178 | -3.9786 | -3.9294 | -4.0816 | -4.3548 | -4.6176 | -4.9261 | -5.2712 | -5.702 | -6.2158 | -6.7488 | -7.3856 | -8.1051 | -8.835 | -9.5674 | -10.2021 | -12.7515 | -12.9955 | -12.5298
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | WPD Best View | Thermal headroom (MW) | -4.0489 | -4.1151 | -4.1828 | -4.4645 | -4.8845 | -5.385 | -5.9977 | -6.6229 | -7.328 | -8.0962 | -8.7389 | -9.3477 | -9.923 | -10.4081 | -10.7864 | -11.2325 | -12.7078 | -12.3422 | -11.4931
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Consumer Transformation | Thermal headroom (MW) | 22.4059 | 22.4042 | 22.5276 | 22.522 | 22.5037 | 22.4706 | 22.3226 | 22.1902 | 22.0434 | 21.526 | 21.3669 | 21.1572 | 20.5928 | 19.9235 | 19.2005 | 18.5169 | 15.651 | 14.5523 | 14.6953
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Leading the Way | Thermal headroom (MW) | 22.391 | 22.396 | 22.5465 | 22.5602 | 22.5547 | 22.517 | 22.378 | 22.2508 | 21.7396 | 21.5569 | 21.3685 | 21.0533 | 20.356 | 19.6212 | 18.9346 | 17.9742 | 16.4741 | 16.6494 | 17.6562
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Steady Progression | Thermal headroom (MW) | 22.4417 | 22.575 | 22.8533 | 22.987 | 23.1067 | 23.2256 | 23.3231 | 23.4157 | 23.503 | 23.5649 | 23.6272 | 23.636 | 23.6513 | 23.6305 | 23.5956 | 23.1894 | 22.0904 | 19.6905 | 19.3572
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | System Transformation | Thermal headroom (MW) | 22.4238 | 22.5395 | 22.798 | 22.9021 | 23.0167 | 23.1139 | 23.1741 | 23.2324 | 23.2597 | 23.2716 | 23.2676 | 22.8561 | 22.7807 | 22.6665 | 22.5431 | 22.3741 | 19.533 | 18.0239 | 18.0159
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | WPD Best View | Thermal headroom (MW) | 22.4238 | 22.5395 | 22.798 | 22.9021 | 23.0167 | 23.1139 | 23.1741 | 23.2324 | 23.2597 | 23.2716 | 23.2676 | 22.8561 | 22.7807 | 22.6665 | 22.5431 | 22.3741 | 19.533 | 18.0239 | 18.0159
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Consumer Transformation | Thermal headroom (MW) | 51.4394 | 49.088 | 46.6242 | 43.8757 | 40.232 | 37.1544 | 32.4518 | 28.5011 | 24.5043 | 20.0688 | 16.5085 | 12.7265 | 8.6076 | 5.4371 | 1.6577 | -1.9078 | -14.2628 | -19.7801 | -19.0255
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Leading the Way | Thermal headroom (MW) | 51.1885 | 48.3042 | 45.4892 | 42.1435 | 37.7161 | 34.7056 | 29.5194 | 25.3074 | 20.5786 | 16.7895 | 13.7507 | 10.8245 | 8.3145 | 5.8735 | 3.9653 | 1.05 | -6.6817 | -6.596 | -0.79912
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Steady Progression | Thermal headroom (MW) | 51.8531 | 51.2837 | 50.7219 | 49.4265 | 47.7199 | 47.2237 | 45.9944 | 44.9468 | 43.5001 | 42.3839 | 41.1232 | 39.5892 | 37.8672 | 36.0141 | 34.0745 | 30.9757 | 19.952 | 10.1491 | 7.716
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | System Transformation | Thermal headroom (MW) | 51.5875 | 50.5505 | 49.1569 | 47.4049 | 44.9325 | 43.7421 | 41.6358 | 39.9442 | 38.1282 | 36.3245 | 34.2758 | 31.1272 | 28.5026 | 25.941 | 22.8959 | 19.4929 | 8.5224 | 2.9682 | 3.7881
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | WPD Best View | Thermal headroom (MW) | 51.6149 | 49.8392 | 47.9236 | 45.6345 | 42.5407 | 40.225 | 36.4263 | 33.3354 | 30.0319 | 26.5005 | 23.5244 | 20.3291 | 17.055 | 14.4352 | 11.7758 | 8.518 | -3.0464 | -8.5084 | -7.5657
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Consumer Transformation | Thermal headroom (MW) | 2.7528 | 1.7441 | 0.73743 | -0.17419 | -0.81723 | -2.0324 | -3.3431 | -4.5798 | -5.7668 | -7.2636 | -8.3526 | -9.4028 | -10.6705 | -11.37 | -13.0254 | -14.2609 | -19.3921 | -21.0189 | -20.7914
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Leading the Way | Thermal headroom (MW) | 2.6816 | 1.4878 | 0.29708 | -0.7966 | -1.495 | -2.7098 | -4.0408 | -5.3021 | -6.8449 | -7.8996 | -8.792 | -9.7597 | -10.1245 | -11.2474 | -12.2323 | -13.4325 | -16.0352 | -16.096 | -14.6465
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Steady Progression | Thermal headroom (MW) | 2.8722 | 2.6368 | 2.2402 | 1.7823 | 1.5775 | 1.3437 | 1.1114 | 0.81912 | 0.12948 | -0.20236 | -0.57569 | -1.0176 | -1.486 | -1.979 | -2.51 | -3.425 | -6.6686 | -8.9247 | -9.5886
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | System Transformation | Thermal headroom (MW) | 2.7886 | 2.3951 | 1.6847 | 1.0774 | 0.76653 | 0.085069 | -0.31252 | -0.8279 | -1.3332 | -1.8944 | -2.4627 | -3.4763 | -4.1671 | -4.8672 | -5.8918 | -6.8476 | -9.6792 | -11.8541 | -11.83
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | WPD Best View | Thermal headroom (MW) | 2.7675 | 1.8182 | 0.88401 | 0.043502 | -0.50681 | -1.5978 | -2.7776 | -3.9087 | -4.9876 | -6.4037 | -7.4332 | -8.4499 | -9.7238 | -10.5087 | -11.6282 | -12.7503 | -17.8692 | -19.5512 | -19.2284
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Consumer Transformation | Thermal headroom (MW) | 26.4553 | 26.3848 | 26.159 | 25.8713 | 25.5687 | 25.6011 | 25.12 | 24.9186 | 24.8097 | 24.7343 | 24.6346 | 24.5099 | 24.3765 | 24.2722 | 24.1531 | 23.768 | 23.5639 | 23.3946 | 23.6258
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Leading the Way | Thermal headroom (MW) | 26.4553 | 26.3167 | 25.9687 | 25.5326 | 25.0921 | 25.14 | 24.4509 | 24.1181 | 23.999 | 23.8847 | 23.8043 | 23.7607 | 23.6773 | 23.6465 | 23.6226 | 23.2333 | 23.2202 | 23.5855 | 24.3113
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Steady Progression | Thermal headroom (MW) | 26.4562 | 26.4502 | 26.37 | 26.1611 | 25.9772 | 26.042 | 25.7857 | 25.7146 | 25.6952 | 25.6813 | 25.6729 | 25.6551 | 25.6303 | 25.5819 | 25.557 | 25.3755 | 25.2703 | 24.5898 | 24.594
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | System Transformation | Thermal headroom (MW) | 26.4562 | 26.409 | 26.2027 | 25.9083 | 25.6319 | 25.7119 | 25.2624 | 25.1031 | 25.0227 | 24.9996 | 24.9589 | 24.8947 | 24.8187 | 24.7797 | 24.7044 | 24.3464 | 24.1037 | 23.889 | 24.1864
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | WPD Best View | Thermal headroom (MW) | 26.4553 | 26.3848 | 26.159 | 25.8713 | 25.5687 | 25.6011 | 25.12 | 24.9186 | 24.8097 | 24.7343 | 24.6346 | 24.5099 | 24.3765 | 24.2722 | 24.1531 | 23.768 | 23.5639 | 23.3946 | 23.6258
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Consumer Transformation | Thermal headroom (MW) | 0.62227 | -0.045844 | -0.79095 | -1.6223 | -3.2886 | -4.7121 | -6.2922 | -7.7693 | -9.4296 | -10.9503 | -12.3576 | -13.7544 | -14.9436 | -16.0339 | -16.9035 | -17.5739 | -19.872 | -21.0346 | -20.7239
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Leading the Way | Thermal headroom (MW) | 0.52803 | -0.26938 | -1.009 | -1.9473 | -3.9459 | -5.3716 | -6.9746 | -8.4622 | -10.1257 | -11.6821 | -12.8544 | -13.6894 | -14.5398 | -15.0385 | -15.2509 | -15.3237 | -17.5018 | -17.4083 | -15.884
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Steady Progression | Thermal headroom (MW) | 0.77201 | 0.51795 | 0.29185 | -0.10128 | -1.0194 | -1.3901 | -1.7968 | -2.2848 | -2.8324 | -3.4105 | -4.0524 | -4.7557 | -5.5239 | -6.3288 | -7.1733 | -8.0776 | -12.4574 | -15.2726 | -16.1262
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | System Transformation | Thermal headroom (MW) | 0.67996 | 0.29986 | -0.095835 | -0.58577 | -1.8555 | -2.3708 | -2.976 | -3.6074 | -4.4387 | -5.2949 | -6.2249 | -7.2757 | -8.3482 | -9.4265 | -10.4842 | -11.4534 | -15.1664 | -16.0866 | -15.8114
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | WPD Best View | Thermal headroom (MW) | 0.69222 | 0.15425 | -0.42352 | -1.0745 | -2.5259 | -3.6265 | -4.9027 | -6.0874 | -7.4842 | -8.7804 | -10.0415 | -11.3843 | -12.6496 | -13.7659 | -14.7537 | -15.6899 | -18.9215 | -19.5795 | -18.9831
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Consumer Transformation | Thermal headroom (MW) | 11.7655 | 10.3945 | 9.6613 | 8.8068 | 8.0298 | 7.2361 | 6.0058 | 4.755 | 3.4652 | 1.8482 | 0.61866 | -1.032 | -3.8185 | -5.8503 | -8.5532 | -10.6108 | -19.727 | -23.3456 | -23.9471
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Leading the Way | Thermal headroom (MW) | 11.5866 | 9.9909 | 9.1828 | 8.2279 | 7.3335 | 6.6088 | 5.3573 | 4.1781 | 2.5902 | 1.3562 | 0.22257 | -1.8347 | -3.8368 | -5.9756 | -7.9025 | -9.7704 | -14.8748 | -16.2734 | -13.9264
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Steady Progression | Thermal headroom (MW) | 11.9904 | 11.6523 | 11.6404 | 11.3674 | 11.1687 | 11.0826 | 10.9626 | 10.7856 | 10.2653 | 10.0727 | 9.8152 | 9.3798 | 8.8299 | 8.2698 | 7.6433 | 6.6422 | 2.2991 | -2.2097 | -3.7125
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | System Transformation | Thermal headroom (MW) | 11.8218 | 11.2629 | 11.0063 | 10.6258 | 10.3543 | 9.78 | 9.5659 | 9.2473 | 8.8909 | 8.5206 | 7.9685 | 6.9392 | 6.0389 | 5.218 | 3.9222 | 2.7472 | -2.9199 | -6.971 | -7.0044
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | WPD Best View | Thermal headroom (MW) | 11.9358 | 11.4176 | 11.2614 | 10.849 | 10.5331 | 10.3192 | 10.0335 | 9.705 | 9.0154 | 8.6639 | 8.2048 | 7.6785 | 7.0635 | 6.5256 | 5.9707 | 5.0887 | 0.64231 | -4.2073 | -5.4718
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Consumer Transformation | Thermal headroom (MW) | 8.7317 | 8.6266 | 8.553 | 8.4118 | 8.2369 | 8.0257 | 7.6814 | 7.344 | 6.9811 | 6.2516 | 5.8971 | 5.5104 | 5.184 | 4.9186 | 4.7414 | 4.5082 | 2.6771 | 1.5152 | 1.5073
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Leading the Way | Thermal headroom (MW) | 8.7235 | 8.6089 | 8.5902 | 8.4588 | 8.2896 | 8.0873 | 7.7384 | 7.4097 | 6.6743 | 6.2835 | 5.9423 | 5.6676 | 5.487 | 5.4066 | 5.2981 | 4.847 | 3.7284 | 3.5721 | 4.0136
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Steady Progression | Thermal headroom (MW) | 8.7829 | 8.8563 | 9.0338 | 9.095 | 9.1494 | 9.1842 | 9.2036 | 9.1878 | 9.1566 | 9.0973 | 9.0165 | 8.876 | 8.7079 | 8.5229 | 8.3041 | 7.7089 | 6.3384 | 4.7909 | 4.488
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | System Transformation | Thermal headroom (MW) | 8.7596 | 8.8081 | 8.9396 | 8.9876 | 9.0081 | 9.0089 | 8.9422 | 8.8488 | 8.7265 | 8.5708 | 8.3784 | 7.7524 | 7.4587 | 7.128 | 6.7851 | 6.4572 | 4.8517 | 4.03 | 3.8764
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | WPD Best View | Thermal headroom (MW) | 8.7368 | 8.6383 | 8.6103 | 8.4635 | 8.3098 | 8.1244 | 7.8112 | 7.5015 | 7.1734 | 6.4707 | 6.1492 | 5.7778 | 5.4657 | 5.201 | 5.0062 | 4.8398 | 2.9562 | 1.7797 | 1.8256
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Consumer Transformation | Thermal headroom (MW) | 11.6687 | 10.9345 | 10.3827 | 9.6855 | 8.919 | 8.1129 | 6.7902 | 5.4678 | 4.1634 | 2.8625 | 1.5953 | 0.13721 | -1.2471 | -3.4023 | -5.652 | -7.8681 | -16.0252 | -19.2777 | -19.7701
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Leading the Way | Thermal headroom (MW) | 11.6053 | 10.796 | 10.3759 | 9.7338 | 9.0102 | 8.2332 | 6.9079 | 5.6715 | 4.3873 | 3.0822 | 1.8525 | 0.8776 | -0.51987 | -2.4734 | -4.3652 | -6.0522 | -11.1999 | -12.4855 | -9.9506
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Steady Progression | Thermal headroom (MW) | 11.8763 | 11.8951 | 12.1868 | 12.1935 | 12.1937 | 12.2533 | 12.2549 | 12.2147 | 12.1432 | 12.0274 | 11.7923 | 11.3479 | 10.8514 | 10.3026 | 9.6921 | 9.0366 | 5.1556 | 1.5898 | -0.47532
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | System Transformation | Thermal headroom (MW) | 11.7547 | 11.6459 | 11.7709 | 11.7294 | 11.6062 | 11.5167 | 11.2823 | 11.0091 | 10.6806 | 10.1809 | 9.6299 | 8.8863 | 8.0332 | 7.123 | 6.1931 | 5.2649 | 1.6012 | -2.3977 | -2.528
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | WPD Best View | Thermal headroom (MW) | 11.8713 | 11.8821 | 12.162 | 12.1523 | 12.135 | 12.1697 | 12.1443 | 12.0747 | 11.9654 | 11.7382 | 11.4629 | 10.9814 | 10.4654 | 9.9196 | 9.3392 | 8.7279 | 5.2877 | 1.3556 | -0.6524
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Consumer Transformation | Thermal headroom (MW) | 28.2933 | 27.3405 | 27.068 | 26.1574 | 24.0754 | 21.9857 | 20.0623 | 18.8883 | 17.4474 | 15.3466 | 13.9386 | 12.0975 | 9.8529 | 8.4148 | 6.2135 | 4.7549 | -1.549 | -3.2805 | -2.6438
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Leading the Way | Thermal headroom (MW) | 28.2103 | 27.1047 | 27.0695 | 25.9444 | 23.2612 | 20.7576 | 18.5808 | 17.2979 | 15.0575 | 13.5022 | 11.9426 | 9.8944 | 8.6384 | 6.7062 | 5.55 | 3.9621 | 1.3705 | 1.9072 | 4.2095
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Steady Progression | Thermal headroom (MW) | 28.4567 | 28.6119 | 29.0336 | 28.6513 | 27.5337 | 26.7652 | 26.2636 | 26.1142 | 25.1588 | 24.8553 | 24.5153 | 24.0658 | 23.5946 | 23.1072 | 22.5623 | 21.2356 | 16.2841 | 10.5835 | 9.1148
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | System Transformation | Thermal headroom (MW) | 28.3485 | 28.4671 | 28.6016 | 28.1336 | 26.4781 | 24.483 | 23.6627 | 23.3162 | 22.7876 | 22.1508 | 21.517 | 19.9656 | 19.1642 | 18.3584 | 16.7691 | 15.0028 | 8.3737 | 4.6654 | 5.1128
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | WPD Best View | Thermal headroom (MW) | 28.4567 | 28.6119 | 29.0336 | 28.6513 | 27.5337 | 26.7652 | 26.2636 | 26.1142 | 25.1588 | 24.8553 | 24.5153 | 24.0658 | 23.5946 | 23.1072 | 22.5623 | 21.2356 | 16.2841 | 10.5835 | 9.1148
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Consumer Transformation | Thermal headroom (MW) | 6.592 | 6.0625 | 5.911 | 5.4049 | 4.2477 | 3.0863 | 2.0173 | 1.3648 | 0.56398 | -0.60358 | -1.3862 | -2.4094 | -3.6569 | -4.4562 | -5.6797 | -6.4904 | -9.994 | -10.9563 | -10.6024
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Leading the Way | Thermal headroom (MW) | 6.5459 | 5.9314 | 5.9119 | 5.2865 | 3.7953 | 2.4038 | 1.1939 | 0.48089 | -0.76426 | -1.6287 | -2.4955 | -3.6339 | -4.3319 | -5.4059 | -6.0484 | -6.931 | -8.3714 | -8.073 | -6.7935
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Steady Progression | Thermal headroom (MW) | 6.6829 | 6.7691 | 7.0035 | 6.791 | 6.1698 | 5.7427 | 5.4639 | 5.3809 | 4.8499 | 4.6812 | 4.4923 | 4.2424 | 3.9806 | 3.7097 | 3.4068 | 2.6694 | -0.082526 | -3.2509 | -4.0672
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | System Transformation | Thermal headroom (MW) | 6.6227 | 6.6886 | 6.7634 | 6.5033 | 5.5831 | 4.4743 | 4.0184 | 3.8258 | 3.532 | 3.1781 | 2.8258 | 1.9636 | 1.5182 | 1.0703 | 0.18703 | -0.79466 | -4.4791 | -6.5401 | -6.2914
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | WPD Best View | Thermal headroom (MW) | 6.6829 | 6.7691 | 7.0035 | 6.791 | 6.1698 | 5.7427 | 5.4639 | 5.3809 | 4.8499 | 4.6812 | 4.4923 | 4.2424 | 3.9806 | 3.7097 | 3.4068 | 2.6694 | -0.082526 | -3.2509 | -4.0672
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Consumer Transformation | Thermal headroom (MW) | 8.2984 | 8.1351 | 8.1635 | 7.9225 | 7.6103 | 6.9469 | 5.9178 | 4.8498 | 3.7401 | 2.2102 | 0.90766 | -0.66296 | -2.3719 | -3.945 | -5.5818 | -7.1491 | -12.9889 | -15.0684 | -14.9828
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Leading the Way | Thermal headroom (MW) | 8.2824 | 8.1013 | 8.173 | 7.9402 | 7.6325 | 6.8408 | 5.7432 | 4.5243 | 2.9294 | 1.6167 | 0.1593 | -1.238 | -2.7042 | -4.1345 | -5.4838 | -6.9566 | -10.022 | -10.005 | -7.8137
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Steady Progression | Thermal headroom (MW) | 8.3745 | 8.5932 | 9.0344 | 9.2433 | 9.4009 | 9.4408 | 9.4872 | 9.539 | 9.4727 | 9.3426 | 9.2631 | 9.0349 | 8.7401 | 8.3726 | 7.944 | 7.1418 | 3.2842 | -1.4253 | -2.4279
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | System Transformation | Thermal headroom (MW) | 8.3649 | 8.5436 | 8.9787 | 9.1577 | 9.2337 | 9.1874 | 8.9745 | 8.7252 | 8.4383 | 8.1742 | 7.7546 | 6.9262 | 6.309 | 5.565 | 4.736 | 3.7988 | -1.6741 | -4.6401 | -4.4932
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | WPD Best View | Thermal headroom (MW) | 8.2854 | 8.1007 | 8.1585 | 7.9319 | 7.6229 | 6.8321 | 5.7359 | 4.5566 | 2.9791 | 1.7082 | 0.28112 | -1.0567 | -2.4888 | -3.8591 | -5.2226 | -6.6946 | -10.2025 | -10.599 | -8.8258
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Consumer Transformation | Thermal headroom (MW) | 7.8305 | 6.5424 | 5.6021 | 4.4661 | 2.4419 | 0.12344 | -3.8766 | -7.8993 | -12.1855 | -17.0345 | -21.673 | -27.9869 | -33.4272 | -38.6138 | -45.1761 | -50.4345 | -69.5929 | -75.681 | -74.5467
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Leading the Way | Thermal headroom (MW) | 7.6547 | 6.1361 | 5.2759 | 3.3581 | 2.169 | -0.34442 | -4.5926 | -8.7398 | -13.7221 | -18.4963 | -23.3137 | -28.5119 | -32.7783 | -37.6755 | -43.0763 | -47.1474 | -57.8211 | -58.7084 | -52.3618
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Steady Progression | Thermal headroom (MW) | 8.156 | 8.2281 | 8.8738 | 9.0286 | 9.214 | 9.2041 | 9.0058 | 8.5171 | 7.9372 | 7.2176 | 6.261 | 4.1981 | 2.8541 | 1.213 | -0.5129 | -2.811 | -14.0473 | -25.5512 | -28.9076
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | System Transformation | Thermal headroom (MW) | 7.9895 | 7.8477 | 8.1198 | 8.1574 | 8.3267 | 7.956 | 7.0435 | 5.9244 | 3.7393 | 2.285 | 0.59595 | -1.9279 | -4.3448 | -7.8093 | -10.5216 | -13.2205 | -27.6266 | -36.3951 | -36.5381
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | WPD Best View | Thermal headroom (MW) | 7.6558 | 6.1675 | 5.3199 | 3.4254 | 2.2583 | -0.22047 | -4.4339 | -8.5434 | -13.4509 | -18.1418 | -22.9436 | -28.2011 | -32.7097 | -37.1869 | -42.544 | -46.5865 | -57.5277 | -58.7485 | -52.6013
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Consumer Transformation | Thermal headroom (MW) | 18.3994 | 18.1391 | 17.9144 | 17.7037 | 17.4736 | 17.0072 | 16.3285 | 15.6883 | 14.9555 | 13.7859 | 12.7404 | 11.5088 | 10.2464 | 9.1155 | 7.9442 | 6.7483 | 2.2641 | 0.51114 | 0.37657
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Leading the Way | Thermal headroom (MW) | 18.3576 | 18.0053 | 17.8614 | 17.6965 | 17.4048 | 16.9018 | 16.1913 | 15.5899 | 14.4824 | 13.5931 | 12.4788 | 11.3271 | 10.1722 | 9.1134 | 8.1062 | 6.8604 | 4.4151 | 4.3092 | 5.774
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Steady Progression | Thermal headroom (MW) | 18.4795 | 18.5366 | 18.7631 | 18.8159 | 18.9025 | 18.9732 | 19.0528 | 19.0624 | 19.0609 | 19.0232 | 18.8881 | 18.6932 | 18.4567 | 18.1615 | 17.841 | 17.0565 | 14.0262 | 10.2654 | 9.3272
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | System Transformation | Thermal headroom (MW) | 18.4505 | 18.4748 | 18.5977 | 18.6446 | 18.755 | 18.7366 | 18.6341 | 18.5507 | 18.4224 | 18.2064 | 17.9264 | 17.1323 | 16.6544 | 16.1039 | 15.4432 | 14.7072 | 10.3796 | 7.8949 | 7.7661
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | WPD Best View | Thermal headroom (MW) | 18.3576 | 18.0053 | 17.8614 | 17.6965 | 17.4048 | 16.9018 | 16.1913 | 15.5899 | 14.4824 | 13.5931 | 12.4788 | 11.3271 | 10.1722 | 9.1134 | 8.1062 | 6.8604 | 4.4151 | 4.3092 | 5.774
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Consumer Transformation | Thermal headroom (MW) | 2.6553 | 2.3578 | 2.2364 | 1.9348 | 1.2596 | 0.78881 | -0.32709 | -1.393 | -2.5203 | -3.6632 | -4.7736 | -6.6576 | -8.1954 | -9.5601 | -11.3384 | -12.6002 | -17.7182 | -19.3334 | -18.998
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Leading the Way | Thermal headroom (MW) | 2.6233 | 2.3498 | 2.299 | 1.6973 | 1.4303 | 0.9185 | -0.23007 | -1.2592 | -2.4019 | -3.5964 | -4.7653 | -6.1725 | -7.2448 | -8.3314 | -9.7055 | -10.5352 | -13.414 | -14.1005 | -12.3737
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Steady Progression | Thermal headroom (MW) | 2.729 | 2.8551 | 3.1754 | 3.3217 | 3.4323 | 3.5595 | 3.6313 | 3.6412 | 3.6523 | 3.6335 | 3.5602 | 3.0289 | 2.8967 | 2.6569 | 2.3812 | 2.0964 | -0.46248 | -3.5358 | -4.3907
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | System Transformation | Thermal headroom (MW) | 2.7002 | 2.8112 | 3.0521 | 3.1813 | 3.3115 | 3.3424 | 3.2723 | 3.1956 | 2.6818 | 2.5369 | 2.3194 | 2.0498 | 1.6722 | 0.89699 | 0.42466 | -0.094101 | -4.0778 | -6.4238 | -6.4377
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | WPD Best View | Thermal headroom (MW) | 2.6233 | 2.3498 | 2.299 | 1.6973 | 1.4303 | 0.9185 | -0.23007 | -1.2592 | -2.4019 | -3.5964 | -4.7653 | -6.1725 | -7.2448 | -8.3314 | -9.7055 | -10.5352 | -13.414 | -14.1005 | -12.3737
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Consumer Transformation | Thermal headroom (MW) | 4.1354 | 3.6397 | 3.2236 | 2.804 | 2.0416 | 1.0879 | -0.40147 | -1.992 | -3.6452 | -5.3062 | -6.9507 | -9.0335 | -10.7112 | -12.474 | -14.9091 | -16.7603 | -22.9035 | -24.5474 | -23.825
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Leading the Way | Thermal headroom (MW) | 4.0659 | 3.4547 | 2.959 | 2.1502 | 1.7355 | 0.70035 | -0.92486 | -2.6856 | -4.5128 | -6.3394 | -8.0052 | -9.7181 | -10.9962 | -12.8548 | -14.8989 | -16.1563 | -19.6052 | -19.5764 | -17.55
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Steady Progression | Thermal headroom (MW) | 4.248 | 4.1342 | 4.1325 | 4.0698 | 4.0313 | 3.8383 | 3.5379 | 3.1319 | 2.6634 | 2.1467 | 1.5865 | 0.62736 | -0.087429 | -0.8821 | -1.6866 | -2.4858 | -6.106 | -8.7575 | -9.7237
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | System Transformation | Thermal headroom (MW) | 4.1706 | 3.9329 | 3.8084 | 3.6742 | 3.5818 | 3.2775 | 2.7177 | 1.9816 | 0.84484 | 0.034334 | -0.83356 | -1.8164 | -2.9225 | -4.4241 | -5.5 | -6.4496 | -10.0169 | -12.4055 | -12.381
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | WPD Best View | Thermal headroom (MW) | 4.0667 | 3.4797 | 2.9939 | 2.2036 | 1.8064 | 0.79863 | -0.79903 | -2.5299 | -4.2978 | -6.0583 | -7.7117 | -9.4717 | -10.9418 | -12.4673 | -14.4768 | -15.7116 | -19.3726 | -19.6082 | -17.7399
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Consumer Transformation | Thermal headroom (MW) | 122.1928 | 117.841 | 115.4812 | 112.1039 | 107.9071 | 100.5235 | 91.6266 | 83.8987 | 75.8314 | 64.8821 | 56.1614 | 45.6209 | 35.904 | 26.4324 | 14.3401 | 1.8828 | -47.9974 | -66.5949 | -65.3461
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Leading the Way | Thermal headroom (MW) | 121.3298 | 115.6511 | 114.0509 | 109.8669 | 105.9139 | 98.2111 | 89.1334 | 81.6108 | 70.7772 | 61.9857 | 53.0681 | 45.0371 | 37.6322 | 28.3909 | 17.4699 | 4.9911 | -24.2709 | -26.697 | -10.5885
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Steady Progression | Thermal headroom (MW) | 123.2836 | 122.8118 | 124.7587 | 124.1121 | 124.1552 | 123.4368 | 123.4174 | 123.1596 | 122.3683 | 121.2226 | 119.6402 | 116.7343 | 114.1134 | 110.9912 | 107.4336 | 100.8971 | 76.4166 | 49.217 | 41.9382
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | System Transformation | Thermal headroom (MW) | 122.5226 | 120.9401 | 121.549 | 121.0509 | 120.4656 | 118.7851 | 117.3464 | 115.8096 | 113.2521 | 110.4722 | 106.7679 | 99.9531 | 95.3071 | 89.3435 | 83.429 | 77.3944 | 44.9713 | 25.9625 | 25.8878
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | WPD Best View | Thermal headroom (MW) | 121.5684 | 116.4536 | 114.7563 | 110.9391 | 107.0192 | 99.5312 | 90.6167 | 82.9616 | 73.496 | 63.2752 | 54.2244 | 44.8483 | 36.0906 | 26.6903 | 15.0635 | 2.6764 | -35.8022 | -45.255 | -34.6559
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Consumer Transformation | Thermal headroom (MW) | 12.5491 | 12.1538 | 11.7467 | 11.3089 | 10.8804 | 10.3573 | 9.4977 | 8.6631 | 7.8585 | 7.0412 | 6.2318 | 5.3151 | 4.493 | 3.784 | 2.4121 | 0.69056 | -4.477 | -6.6396 | -6.9286
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Leading the Way | Thermal headroom (MW) | 12.518 | 11.9981 | 11.7308 | 11.2908 | 10.8915 | 10.3678 | 9.498 | 8.6941 | 7.8858 | 7.0403 | 6.2358 | 5.6015 | 5.0768 | 4.1713 | 2.5888 | 1.0298 | -2.3498 | -3.0254 | -1.433
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Steady Progression | Thermal headroom (MW) | 12.6604 | 12.6734 | 12.8168 | 12.6893 | 12.6985 | 12.6939 | 12.6692 | 12.6118 | 12.5313 | 12.3554 | 12.1593 | 11.8301 | 11.4621 | 11.0583 | 10.5109 | 9.9051 | 7.2305 | 5.1114 | 4.2096
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | System Transformation | Thermal headroom (MW) | 12.5936 | 12.5455 | 12.5001 | 12.4028 | 12.3491 | 12.2839 | 12.1217 | 11.9245 | 11.6298 | 11.2938 | 10.8646 | 10.3445 | 9.7548 | 9.0855 | 8.2446 | 7.4033 | 4.7298 | 3.2379 | 3.1937
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | WPD Best View | Thermal headroom (MW) | 12.5426 | 12.0422 | 11.7596 | 11.3353 | 10.9209 | 10.3987 | 9.5307 | 8.6974 | 7.8856 | 7.0464 | 6.2378 | 5.3864 | 4.6277 | 3.9628 | 2.2514 | 0.45574 | -4.2167 | -5.7688 | -5.612
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Consumer Transformation | Thermal headroom (MW) | 4.1516 | 3.6218 | 2.9526 | 2.4665 | 2.2809 | 1.4725 | 0.70657 | -0.12594 | -0.69412 | -1.3577 | -2.1402 | -3.0226 | -3.9271 | -4.7647 | -5.6216 | -6.4831 | -9.2799 | -9.7569 | -9.2708
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Leading the Way | Thermal headroom (MW) | 3.691 | 2.9498 | 2.5302 | 1.8711 | 1.6541 | 0.79866 | 0.055263 | -0.79518 | -1.4207 | -2.0648 | -2.8684 | -3.6341 | -4.4266 | -5.2558 | -6.0683 | -6.721 | -8.05 | -7.1816 | -5.1329
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Steady Progression | Thermal headroom (MW) | 4.335 | 4.3118 | 4.0551 | 3.3877 | 3.4302 | 3.4172 | 3.4254 | 3.2745 | 3.2143 | 3.1252 | 2.9525 | 2.7789 | 2.5524 | 2.2575 | 1.9328 | 1.5093 | -1.454 | -4.8834 | -5.6325
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | System Transformation | Thermal headroom (MW) | 4.1865 | 3.8208 | 3.3377 | 3.011 | 3.0369 | 2.9317 | 2.7429 | 2.4079 | 2.3044 | 2.0756 | 1.7652 | 1.391 | 0.92037 | 0.36356 | -0.27256 | -0.98704 | -4.7921 | -6.6053 | -6.0815
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | WPD Best View | Thermal headroom (MW) | 3.691 | 2.9498 | 2.5302 | 1.8711 | 1.6541 | 0.79866 | 0.055263 | -0.79518 | -1.4207 | -2.0648 | -2.8684 | -3.6341 | -4.4266 | -5.2558 | -6.0683 | -6.721 | -8.05 | -7.1816 | -5.1329
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Consumer Transformation | Thermal headroom (MW) | 17.3914 | 16.8696 | 16.4915 | 15.9312 | 15.3872 | 14.6177 | 13.3533 | 12.1502 | 10.9024 | 8.931 | 7.6943 | 6.2027 | 4.8364 | 3.6053 | 2.4794 | 0.61982 | -7.9104 | -12.3583 | -13.3954
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Leading the Way | Thermal headroom (MW) | 17.378 | 16.7568 | 16.427 | 15.8385 | 15.2845 | 14.5335 | 13.2424 | 12.0537 | 10.1071 | 8.8334 | 7.6734 | 6.7277 | 5.943 | 5.3618 | 4.3451 | 2.0197 | -3.9112 | -5.711 | -4.6245
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Steady Progression | Thermal headroom (MW) | 17.4588 | 17.4109 | 17.5856 | 17.4778 | 17.4118 | 17.3582 | 17.3027 | 17.2179 | 17.0899 | 16.8798 | 16.5853 | 16.1782 | 15.7309 | 15.2147 | 14.6081 | 13.2136 | 9.8449 | 6.8602 | 5.9739
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | System Transformation | Thermal headroom (MW) | 17.4253 | 17.293 | 17.3323 | 17.136 | 17.0165 | 16.9114 | 16.7377 | 16.5371 | 16.239 | 15.8105 | 15.3087 | 13.9657 | 13.2631 | 12.4774 | 11.6175 | 10.7678 | 6.8409 | 4.4703 | 3.779
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | WPD Best View | Thermal headroom (MW) | 17.3801 | 16.7705 | 16.4767 | 15.9485 | 15.4342 | 14.6859 | 13.4214 | 12.2687 | 10.6978 | 9.0609 | 7.823 | 6.6382 | 5.5618 | 4.6462 | 3.6989 | 1.6712 | -5.1953 | -8.7129 | -8.4558
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Consumer Transformation | Thermal headroom (MW) | 4.5841 | 4.1911 | 4.0189 | 3.733 | 3.4235 | 2.8351 | 2.3348 | 1.9053 | 1.4755 | 0.65745 | 0.21605 | -0.30342 | -0.76093 | -1.1543 | -1.8472 | -2.5797 | -5.5311 | -6.7731 | -6.6504
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Leading the Way | Thermal headroom (MW) | 4.5481 | 4.0604 | 3.916 | 3.6242 | 3.2859 | 2.6828 | 2.1655 | 1.7727 | 0.99683 | 0.56332 | 0.16206 | -0.12837 | -0.32998 | -0.71211 | -1.2592 | -2.1259 | -3.7647 | -4.0155 | -3.4439
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Steady Progression | Thermal headroom (MW) | 4.6431 | 4.5238 | 4.6184 | 4.5689 | 4.5155 | 4.3778 | 4.3746 | 4.3263 | 4.2678 | 4.1915 | 4.0936 | 3.9658 | 3.7992 | 3.6373 | 3.4486 | 2.8956 | 1.8391 | 0.89268 | 0.73856
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | System Transformation | Thermal headroom (MW) | 4.6028 | 4.4036 | 4.4315 | 4.3431 | 4.2554 | 4.0309 | 3.9674 | 3.8711 | 3.7623 | 3.6203 | 3.4272 | 2.8383 | 2.6 | 2.3408 | 2.0705 | 1.7944 | 0.6204 | -0.25935 | -0.47949
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | WPD Best View | Thermal headroom (MW) | 4.5841 | 4.1911 | 4.0189 | 3.733 | 3.4235 | 2.8351 | 2.3348 | 1.9053 | 1.4755 | 0.65745 | 0.21605 | -0.30342 | -0.76093 | -1.1543 | -1.8472 | -2.5797 | -5.5311 | -6.7731 | -6.6504
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Consumer Transformation | Thermal headroom (MW) | 5.0017 | 5.117 | 5.3705 | 5.4836 | 5.5639 | 5.6091 | 5.5758 | 5.5573 | 5.5095 | 5.4246 | 5.3001 | 5.0945 | 4.8872 | 4.652 | 4.375 | 4.1304 | 3.2241 | 3.0496 | 3.4126
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Leading the Way | Thermal headroom (MW) | 5.0007 | 5.1177 | 5.3939 | 5.4879 | 5.5711 | 5.5883 | 5.5606 | 5.4962 | 5.4525 | 5.3099 | 5.0874 | 4.8868 | 4.6463 | 4.3698 | 4.0895 | 3.8597 | 3.4769 | 3.834 | 4.9535
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Steady Progression | Thermal headroom (MW) | 5.0244 | 5.1832 | 5.5327 | 5.7016 | 5.8655 | 6.0237 | 6.1481 | 6.2875 | 6.3975 | 6.5008 | 6.6046 | 6.6514 | 6.7009 | 6.74 | 6.7614 | 6.7418 | 6.2413 | 5.5827 | 5.7577
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | System Transformation | Thermal headroom (MW) | 5.0177 | 5.1882 | 5.5144 | 5.6583 | 5.8159 | 5.9326 | 6.0642 | 6.1735 | 6.257 | 6.2989 | 6.3399 | 6.3397 | 6.3171 | 6.2254 | 6.1093 | 5.9944 | 5.1198 | 4.8416 | 5.3341
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | WPD Best View | Thermal headroom (MW) | 5.0007 | 5.1177 | 5.3939 | 5.4879 | 5.5711 | 5.5883 | 5.5606 | 5.4962 | 5.4525 | 5.3099 | 5.0874 | 4.8868 | 4.6463 | 4.3698 | 4.0895 | 3.8597 | 3.4769 | 3.834 | 4.9535
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Consumer Transformation | Thermal headroom (MW) | 11.5071 | 11.4589 | 11.4595 | 11.5272 | 11.5162 | 11.4939 | 11.3524 | 11.2229 | 11.0791 | 10.4946 | 10.3572 | 9.9496 | 9.7558 | 9.3338 | 9.1978 | 9.0779 | 6.2954 | 4.9208 | 4.8968
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Leading the Way | Thermal headroom (MW) | 11.4821 | 11.3771 | 11.3265 | 11.3944 | 11.3798 | 11.3477 | 11.2033 | 11.0931 | 10.61 | 10.3479 | 10.2165 | 9.8085 | 9.7333 | 9.3452 | 9.2935 | 8.4955 | 6.8032 | 6.7508 | 7.897
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Steady Progression | Thermal headroom (MW) | 11.5571 | 11.654 | 11.8803 | 12.0501 | 12.2058 | 12.3671 | 12.5166 | 12.6523 | 12.7661 | 12.8057 | 12.9053 | 12.807 | 12.8258 | 12.6506 | 12.6206 | 12.2069 | 11.4415 | 10.5437 | 10.6017
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | System Transformation | Thermal headroom (MW) | 11.5215 | 11.5731 | 11.689 | 11.8681 | 11.9991 | 12.1509 | 12.2304 | 12.3169 | 12.3833 | 12.335 | 12.3474 | 11.7393 | 11.6723 | 11.3121 | 11.1612 | 10.9746 | 9.9013 | 8.8814 | 8.7945
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | WPD Best View | Thermal headroom (MW) | 11.4821 | 11.3764 | 11.3247 | 11.3948 | 11.3806 | 11.3496 | 11.2054 | 11.0991 | 10.618 | 10.3591 | 10.2249 | 9.8072 | 9.7172 | 9.3035 | 9.2029 | 8.5456 | 6.7903 | 6.6589 | 7.7334
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Consumer Transformation | Thermal headroom (MW) | 5.5929 | 5.0599 | 4.7394 | 4.1888 | 3.5648 | 1.466 | -0.70527 | -2.3658 | -4.5505 | -7.0044 | -9.2863 | -11.2218 | -13.278 | -15.0408 | -16.8174 | -18.569 | -25.6608 | -27.3578 | -26.5718
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Leading the Way | Thermal headroom (MW) | 5.4588 | 4.8007 | 4.443 | 3.7507 | 2.9785 | 0.66161 | -1.6629 | -3.4078 | -6.2122 | -8.6403 | -11.1171 | -12.7632 | -14.5001 | -16.0832 | -17.5333 | -19.13 | -22.9509 | -22.3978 | -20.0646
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Steady Progression | Thermal headroom (MW) | 5.7425 | 5.5897 | 5.6364 | 5.4641 | 5.2815 | 4.6622 | 4.2787 | 4.0261 | 3.3636 | 2.6907 | 1.9852 | 1.4655 | 0.87322 | 0.28277 | -0.43152 | -1.518 | -6.4762 | -11.702 | -12.9274
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | System Transformation | Thermal headroom (MW) | 5.6158 | 5.3113 | 5.2457 | 5.0003 | 4.6662 | 3.872 | 3.1252 | 2.5749 | 1.6294 | 0.6266 | -0.6002 | -1.737 | -2.7301 | -3.7082 | -4.8306 | -5.9777 | -12.6148 | -15.4271 | -15.2477
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | WPD Best View | Thermal headroom (MW) | 5.5111 | 4.9007 | 4.6164 | 3.9918 | 3.2986 | 1.0768 | -1.2005 | -2.9122 | -5.6757 | -8.0644 | -10.4413 | -12.0455 | -13.7148 | -15.1924 | -16.5892 | -18.1622 | -22.8665 | -22.8431 | -21.1195
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Consumer Transformation | Thermal headroom (MW) | 6.6528 | 6.5749 | 6.6985 | 6.7055 | 6.7025 | 6.6232 | 6.4896 | 6.4038 | 6.3134 | 6.2225 | 6.0909 | 5.9737 | 5.8704 | 5.6448 | 5.1405 | 4.5877 | 2.4844 | 1.9476 | 2.1862
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Leading the Way | Thermal headroom (MW) | 6.5662 | 6.4275 | 6.5844 | 6.5919 | 6.5851 | 6.5196 | 6.4488 | 6.3922 | 6.2964 | 6.1896 | 6.0397 | 5.9139 | 5.737 | 5.1084 | 4.5392 | 4.0147 | 2.7813 | 3.287 | 4.5285
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Steady Progression | Thermal headroom (MW) | 6.7512 | 6.7894 | 7.0284 | 7.1186 | 7.2326 | 7.3357 | 7.4291 | 7.5235 | 7.5946 | 7.6501 | 7.7036 | 7.7096 | 7.7057 | 7.6769 | 7.6352 | 7.5651 | 6.6901 | 4.341 | 3.6226
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | System Transformation | Thermal headroom (MW) | 6.6696 | 6.6774 | 6.8849 | 6.9841 | 7.0786 | 7.1275 | 7.1661 | 7.1896 | 7.2127 | 7.2183 | 7.1894 | 7.1159 | 7.0247 | 6.8995 | 6.7302 | 6.5267 | 4.3946 | 3.0109 | 3.2602
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | WPD Best View | Thermal headroom (MW) | 6.5662 | 6.4275 | 6.5844 | 6.5919 | 6.5851 | 6.5196 | 6.4488 | 6.3922 | 6.2964 | 6.1896 | 6.0397 | 5.9139 | 5.737 | 5.1084 | 4.5392 | 4.0147 | 2.7813 | 3.287 | 4.5285
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Consumer Transformation | Thermal headroom (MW) | 3.7947 | 2.6487 | 2.1372 | 1.5223 | 0.17339 | -1.5024 | -3.3097 | -4.8573 | -6.2789 | -7.7395 | -9.3979 | -11.6571 | -13.7682 | -16.2236 | -19.1172 | -21.4273 | -30.3428 | -33.2744 | -32.7966
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Leading the Way | Thermal headroom (MW) | 3.7054 | 2.224 | 1.8529 | 0.8712 | -0.24992 | -2.0499 | -3.9038 | -5.3688 | -6.7429 | -8.2003 | -9.7726 | -11.5312 | -13.5961 | -15.6961 | -18.2144 | -19.8421 | -24.9844 | -25.8408 | -22.9669
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Steady Progression | Thermal headroom (MW) | 3.9578 | 3.5584 | 3.7935 | 3.6737 | 3.3884 | 2.9428 | 2.7761 | 2.5922 | 2.389 | 2.1627 | 1.7515 | 0.84656 | 0.27539 | -0.42432 | -1.1704 | -1.8716 | -5.718 | -9.4783 | -11.2629
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | System Transformation | Thermal headroom (MW) | 3.8481 | 3.1969 | 3.2189 | 3.1152 | 2.6309 | 1.9661 | 1.5603 | 1.1548 | 0.40203 | -0.083603 | -0.8357 | -1.8284 | -2.7355 | -4.0699 | -5.0781 | -5.9676 | -10.5812 | -14.503 | -14.4016
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | WPD Best View | Thermal headroom (MW) | 3.7938 | 2.649 | 2.1348 | 1.5219 | 0.16299 | -1.508 | -3.317 | -4.8656 | -6.3188 | -7.8064 | -9.476 | -11.7375 | -14.0218 | -16.4985 | -19.4187 | -21.7303 | -30.3021 | -32.872 | -31.9628
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Consumer Transformation | Thermal headroom (MW) | 5.66 | 5.1858 | 4.9302 | 4.414 | 3.5222 | 2.6052 | 1.1457 | -0.13774 | -1.4541 | -2.8632 | -4.4385 | -6.8056 | -8.8488 | -10.8007 | -13.2058 | -15.2454 | -23.5919 | -26.9697 | -27.4312
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Leading the Way | Thermal headroom (MW) | 5.5918 | 5.1049 | 4.9084 | 4.0929 | 3.5183 | 2.6454 | 1.2194 | -0.027167 | -1.3775 | -2.8837 | -4.584 | -6.5806 | -8.348 | -10.1222 | -12.2395 | -13.7651 | -18.9888 | -20.4552 | -17.6642
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Steady Progression | Thermal headroom (MW) | 5.8343 | 5.8912 | 6.2246 | 6.3061 | 6.3687 | 6.4313 | 6.4435 | 6.3902 | 6.3519 | 6.2441 | 6.1217 | 5.4285 | 5.0905 | 4.6447 | 4.1666 | 3.549 | -1.2884 | -6.8864 | -8.5694
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | System Transformation | Thermal headroom (MW) | 5.7374 | 5.7349 | 5.9759 | 6.0396 | 6.0172 | 5.9606 | 5.7719 | 5.5763 | 4.9593 | 4.6405 | 4.2091 | 3.636 | 2.9558 | 1.7349 | 0.76123 | -0.31806 | -7.326 | -11.344 | -11.5079
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | WPD Best View | Thermal headroom (MW) | 5.5918 | 5.1049 | 4.9084 | 4.0929 | 3.5183 | 2.6454 | 1.2194 | -0.027167 | -1.3775 | -2.8837 | -4.584 | -6.5806 | -8.348 | -10.1222 | -12.2395 | -13.7651 | -18.9888 | -20.4552 | -17.6642
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Consumer Transformation | Thermal headroom (MW) | 19.0947 | 17.7515 | 16.7361 | 15.064 | 13.0477 | 10.8735 | 7.4578 | 4.1255 | 0.82943 | -2.5309 | -5.7532 | -10.064 | -13.6262 | -17.0142 | -20.4351 | -23.3431 | -41.1433 | -48.9735 | -49.7852
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Leading the Way | Thermal headroom (MW) | 18.8982 | 17.3847 | 16.5345 | 14.3605 | 12.7322 | 10.6136 | 7.3008 | 4.0421 | 0.4187 | -2.7753 | -5.8849 | -8.9971 | -11.6003 | -13.7657 | -15.8944 | -18.8708 | -30.8709 | -34.4562 | -29.5324
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Steady Progression | Thermal headroom (MW) | 19.5325 | 19.4735 | 19.9606 | 19.6757 | 19.5539 | 19.475 | 19.3622 | 19.0098 | 18.4962 | 17.9358 | 17.2023 | 15.7199 | 14.4676 | 13.0993 | 11.4544 | 9.4619 | -0.95502 | -9.9366 | -12.8025
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | System Transformation | Thermal headroom (MW) | 19.2742 | 18.9389 | 19.1497 | 18.6679 | 18.2712 | 18.055 | 17.5417 | 16.6919 | 15.2147 | 14.1102 | 12.7411 | 10.7529 | 8.7036 | 6.032 | 3.692 | 1.3212 | -10.442 | -15.8086 | -15.7568
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | WPD Best View | Thermal headroom (MW) | 19.085 | 17.749 | 16.7412 | 15.0645 | 13.0493 | 10.8497 | 7.4434 | 4.1054 | 0.7942 | -2.6057 | -5.8528 | -10.1365 | -13.6526 | -17.0054 | -20.3081 | -23.4466 | -41.0463 | -48.3438 | -48.6383
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Consumer Transformation | Thermal headroom (MW) | 2.7974 | 2.5093 | 2.2554 | 1.8426 | 1.4584 | 0.91313 | 0.11367 | -0.65204 | -1.4031 | -2.1547 | -2.8938 | -3.751 | -4.4871 | -5.2604 | -5.9084 | -6.4633 | -10.3711 | -12.0681 | -12.3106
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Leading the Way | Thermal headroom (MW) | 2.7574 | 2.4135 | 2.2114 | 1.7607 | 1.3825 | 0.85051 | 0.083147 | -0.6644 | -1.422 | -2.163 | -2.8498 | -3.3949 | -3.9652 | -4.4283 | -4.6861 | -5.3757 | -8.0473 | -8.7574 | -7.5686
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Steady Progression | Thermal headroom (MW) | 2.8901 | 2.8568 | 2.9225 | 2.7896 | 2.7344 | 2.6823 | 2.6171 | 2.4954 | 2.3375 | 2.1284 | 1.8842 | 1.5608 | 1.1938 | 0.78718 | 0.34298 | -0.1296 | -2.8853 | -4.8013 | -5.3607
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | System Transformation | Thermal headroom (MW) | 2.8382 | 2.744 | 2.7427 | 2.5739 | 2.4744 | 2.3901 | 2.2358 | 1.9891 | 1.7178 | 1.387 | 0.97736 | 0.47946 | -0.087522 | -0.69536 | -1.3129 | -1.9054 | -4.5392 | -5.4034 | -5.2717
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | WPD Best View | Thermal headroom (MW) | 2.7975 | 2.51 | 2.2573 | 1.8422 | 1.4574 | 0.91045 | 0.11063 | -0.66059 | -1.415 | -2.1719 | -2.9088 | -3.7552 | -4.4698 | -5.2447 | -5.8677 | -6.394 | -10.3381 | -11.9554 | -12.1268
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Consumer Transformation | Thermal headroom (MW) | 2.551 | 2.2876 | 2.2057 | 1.8618 | 1.4436 | 0.88036 | -0.21459 | -1.2257 | -2.7908 | -4.4958 | -6.0004 | -7.9299 | -9.928 | -11.8492 | -13.8925 | -15.8512 | -23.5854 | -26.5666 | -26.484
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Leading the Way | Thermal headroom (MW) | 2.57 | 2.2761 | 2.3532 | 2.0526 | 1.6478 | 1.1113 | 0.0053544 | -0.99712 | -3.217 | -4.6808 | -6.3555 | -8.0265 | -9.7535 | -11.4752 | -13.138 | -14.9326 | -19.386 | -20.1997 | -17.5798
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Steady Progression | Thermal headroom (MW) | 2.7077 | 3.0047 | 3.6031 | 3.8534 | 4.1028 | 4.3097 | 4.4803 | 4.6329 | 4.4776 | 4.5085 | 4.492 | 4.337 | 4.0871 | 3.7832 | 3.2001 | 2.2058 | -1.3834 | -5.6844 | -6.5813
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | System Transformation | Thermal headroom (MW) | 2.6428 | 2.8512 | 3.35 | 3.5884 | 3.7222 | 3.8683 | 3.8948 | 3.8625 | 3.3885 | 3.2056 | 2.8935 | 2.1175 | 1.5421 | 0.68536 | -0.2548 | -1.1439 | -6.5442 | -9.577 | -9.3595
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | WPD Best View | Thermal headroom (MW) | 2.5523 | 2.29 | 2.2111 | 1.87 | 1.4563 | 0.89833 | -0.18948 | -1.1918 | -2.7461 | -4.4388 | -5.9293 | -7.8426 | -9.8246 | -11.7306 | -13.7623 | -15.7104 | -23.4723 | -26.4793 | -26.3724
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Consumer Transformation | Thermal headroom (MW) | 6.2248 | 5.5854 | 5.1032 | 4.4 | 3.3751 | 2.5292 | 1.21 | -0.12633 | -1.1899 | -2.2446 | -3.2891 | -4.9326 | -6.0555 | -6.9984 | -8.1103 | -8.9441 | -15.2621 | -18.2761 | -18.6696
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Leading the Way | Thermal headroom (MW) | 6.1006 | 5.409 | 4.9197 | 3.8006 | 3.1115 | 2.2824 | 1.0114 | -0.29099 | -1.3303 | -2.3653 | -3.3089 | -4.4797 | -5.1228 | -5.5402 | -6.2751 | -7.0367 | -11.5987 | -13.3455 | -11.9956
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Steady Progression | Thermal headroom (MW) | 6.4015 | 6.2594 | 6.3136 | 6.1457 | 6.0037 | 5.9159 | 5.8352 | 5.6348 | 5.4913 | 5.2975 | 5.0246 | 4.2631 | 3.8237 | 3.3672 | 2.8516 | 2.2607 | -1.1442 | -4.2308 | -5.5231
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | System Transformation | Thermal headroom (MW) | 6.2798 | 6.0252 | 5.9815 | 5.6971 | 5.4305 | 5.2979 | 5.0627 | 4.6957 | 4.0084 | 3.6142 | 3.1656 | 2.5148 | 1.8221 | 0.76299 | 0.059489 | -0.73575 | -4.693 | -6.7591 | -7.0225
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | WPD Best View | Thermal headroom (MW) | 6.2154 | 5.581 | 5.1024 | 4.3972 | 3.3722 | 2.5033 | 1.1899 | -0.14713 | -1.2244 | -2.3124 | -3.3894 | -5.033 | -6.1557 | -7.0715 | -8.1211 | -9.2136 | -15.2799 | -17.9238 | -17.972
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Consumer Transformation | Thermal headroom (MW) | 43.1529 | 40.5903 | 37.1616 | 33.0925 | 27.0064 | 18.5995 | 7.8015 | -3.14 | -14.296 | -24.9453 | -34.5431 | -46.8158 | -58.6551 | -69.037 | -80.9691 | -90.2857 | -124.8109 | -136.6691 | -134.6653
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Leading the Way | Thermal headroom (MW) | 43.0021 | 39.6644 | 37.0221 | 31.1092 | 26.167 | 17.384 | 5.8621 | -5.753 | -18.3071 | -29.2034 | -38.4532 | -49.3358 | -58.0587 | -66.522 | -75.6176 | -81.8947 | -102.5916 | -103.8511 | -91.698
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Steady Progression | Thermal headroom (MW) | 43.8075 | 43.5791 | 43.5676 | 41.7502 | 40.4401 | 38.3911 | 35.9434 | 32.8896 | 29.3135 | 25.6221 | 21.784 | 15.8042 | 10.9422 | 5.6269 | 0.057373 | -6.1914 | -36.682 | -56.5234 | -65.581
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | System Transformation | Thermal headroom (MW) | 43.5258 | 42.9636 | 41.7776 | 40.0137 | 38.0299 | 34.8932 | 30.7654 | 25.947 | 19.2382 | 13.7324 | 7.876 | 0.90087 | -6.2925 | -15.2264 | -22.787 | -29.891 | -60.2488 | -76.1003 | -76.7289
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | WPD Best View | Thermal headroom (MW) | 43.2873 | 41.1158 | 38.3056 | 33.4276 | 29.2247 | 21.3447 | 10.9637 | 0.39942 | -10.552 | -20.5943 | -30.3921 | -41.8975 | -51.5404 | -60.8083 | -71.0393 | -78.7546 | -104.9586 | -111.5221 | -103.7823
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Consumer Transformation | Thermal headroom (MW) | 6.2557 | 5.8542 | 5.3185 | 4.9458 | 4.1135 | 3.208 | 2.1186 | 1.2336 | 0.5625 | -0.60707 | -1.6013 | -3.0031 | -3.6787 | -4.4009 | -5.9154 | -7.014 | -11.3077 | -12.5079 | -11.9716
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Leading the Way | Thermal headroom (MW) | 6.16 | 5.5934 | 5.0088 | 4.2372 | 3.7015 | 2.7889 | 1.6756 | 0.77613 | 0.13517 | -1.176 | -2.1826 | -3.3245 | -3.9246 | -4.8445 | -6.1157 | -6.7789 | -8.8278 | -8.9806 | -7.2653
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Steady Progression | Thermal headroom (MW) | 6.3685 | 6.2624 | 6.1886 | 6.0181 | 5.892 | 5.7333 | 5.5896 | 5.419 | 5.2731 | 4.8238 | 4.4106 | 3.6184 | 3.3012 | 2.96 | 2.5936 | 2.2041 | 0.13011 | -1.6878 | -2.6407
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | System Transformation | Thermal headroom (MW) | 6.2753 | 6.0744 | 5.7645 | 5.6021 | 5.3924 | 5.1692 | 4.8821 | 4.6224 | 4.0482 | 3.2819 | 2.6162 | 1.9396 | 1.4725 | 0.65758 | 0.15361 | -0.33081 | -2.7288 | -4.7268 | -4.5895
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | WPD Best View | Thermal headroom (MW) | 6.2608 | 5.8652 | 5.3411 | 4.9814 | 4.1831 | 3.3046 | 2.2461 | 1.3939 | 0.76037 | -0.37754 | -1.3485 | -2.7371 | -3.4199 | -4.2352 | -5.7243 | -6.7954 | -11.0532 | -12.3472 | -11.8272
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Consumer Transformation | Thermal headroom (MW) | -3.3092 | -3.2549 | -3.0647 | -3.0848 | -3.108 | -3.3021 | -3.5649 | -3.7471 | -3.9534 | -4.1804 | -4.3539 | -4.5989 | -4.7969 | -4.9305 | -4.999 | -4.9934 | -4.4276 | -3.9659 | -3.1446
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Leading the Way | Thermal headroom (MW) | -3.3309 | -3.3339 | -3.071 | -3.1065 | -3.1221 | -3.3092 | -3.5681 | -3.7232 | -3.937 | -4.1728 | -4.3006 | -4.3673 | -4.3635 | -4.2737 | -4.096 | -3.8804 | -2.6773 | -2.0528 | -0.67217
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Steady Progression | Thermal headroom (MW) | -3.2645 | -3.0511 | -2.6192 | -2.5047 | -2.3267 | -2.1536 | -1.9731 | -1.8024 | -1.679 | -1.5708 | -1.4829 | -1.4221 | -1.3976 | -1.3924 | -1.4205 | -1.4461 | -1.6192 | -1.1336 | -0.42173
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | System Transformation | Thermal headroom (MW) | -3.2899 | -3.0912 | -2.7439 | -2.6073 | -2.4631 | -2.325 | -2.177 | -2.0632 | -1.9859 | -1.9597 | -1.9271 | -1.9615 | -2.0342 | -2.1153 | -2.2191 | -2.3082 | -2.1786 | -1.364 | -0.39747
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | WPD Best View | Thermal headroom (MW) | -3.3092 | -3.2549 | -3.0647 | -3.0848 | -3.108 | -3.3021 | -3.5649 | -3.7471 | -3.9534 | -4.1804 | -4.3539 | -4.5989 | -4.7969 | -4.9305 | -4.999 | -4.9934 | -4.719 | -4.168 | -3.1446
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Consumer Transformation | Thermal headroom (MW) | 3.6442 | 3.4396 | 3.1703 | 2.4751 | 2.1289 | 1.5899 | 0.96417 | 0.32338 | -0.34003 | -1.3758 | -2.0287 | -2.7488 | -3.3981 | -4.167 | -4.9038 | -5.7205 | -8.7972 | -9.8489 | -9.4609
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Leading the Way | Thermal headroom (MW) | 3.6393 | 3.3772 | 3.1597 | 2.302 | 1.9306 | 1.3927 | 0.73177 | 0.10642 | -0.94479 | -1.6082 | -2.1851 | -2.6426 | -3.0212 | -3.6995 | -4.4468 | -5.4186 | -6.9325 | -6.8885 | -6.2484
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Steady Progression | Thermal headroom (MW) | 3.6854 | 3.6892 | 3.7213 | 3.321 | 3.2537 | 3.1763 | 3.0765 | 2.9344 | 2.7881 | 2.5942 | 2.3995 | 2.1293 | 1.8487 | 1.429 | 1.0706 | 0.36208 | -1.2255 | -2.3518 | -2.5584
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | System Transformation | Thermal headroom (MW) | 3.6698 | 3.6327 | 3.5636 | 3.0455 | 2.9203 | 2.7938 | 2.6304 | 2.3904 | 2.1312 | 1.823 | 1.4861 | 0.74354 | 0.32227 | -0.31363 | -0.80558 | -1.1942 | -2.8156 | -3.4557 | -3.4937
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | WPD Best View | Thermal headroom (MW) | 3.6442 | 3.4396 | 3.1703 | 2.4751 | 2.1289 | 1.5899 | 0.96417 | 0.32338 | -0.34003 | -1.3758 | -2.0287 | -2.7488 | -3.3981 | -4.167 | -4.9038 | -5.7205 | -8.7972 | -9.8489 | -9.4609
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Consumer Transformation | Thermal headroom (MW) | 5.9387 | 5.2361 | 4.7207 | 4.295 | 3.7864 | 2.86 | 1.5254 | 0.25339 | -0.97463 | -2.4387 | -3.3731 | -4.4699 | -5.8166 | -6.7055 | -8.4848 | -9.756 | -15.3693 | -17.6341 | -18.0416
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Leading the Way | Thermal headroom (MW) | 5.9048 | 5.1692 | 4.5061 | 4.1306 | 3.5607 | 2.6073 | 1.225 | -0.0882 | -1.6921 | -2.7803 | -3.5712 | -4.4649 | -4.8518 | -6.026 | -7.0334 | -8.204 | -11.2668 | -12.0422 | -10.8271
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Steady Progression | Thermal headroom (MW) | 6.0114 | 6.012 | 5.9609 | 5.9498 | 5.8087 | 5.6845 | 5.5401 | 5.3457 | 4.8057 | 4.6057 | 4.3781 | 4.0894 | 3.7393 | 3.3537 | 2.9286 | 2.1234 | -0.75829 | -2.8706 | -3.7121
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | System Transformation | Thermal headroom (MW) | 5.9774 | 5.9267 | 5.7409 | 5.629 | 5.4689 | 4.9051 | 4.5787 | 4.2497 | 3.9039 | 3.5442 | 3.1494 | 2.3421 | 1.8197 | 1.2808 | 0.39819 | -0.4521 | -3.2302 | -5.7246 | -6.008
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | WPD Best View | Thermal headroom (MW) | 5.9077 | 5.1761 | 4.5171 | 4.149 | 3.6285 | 2.69 | 1.3341 | 0.057396 | -1.506 | -2.5756 | -3.4407 | -4.4695 | -5.023 | -6.3355 | -7.4156 | -8.6371 | -11.8369 | -12.6772 | -11.3397
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Consumer Transformation | Thermal headroom (MW) | 1.9804 | 1.7602 | 1.4802 | 1.1286 | 0.71454 | 0.12032 | -0.63818 | -1.3997 | -2.2221 | -3.1556 | -4.0982 | -5.0526 | -5.9695 | -6.6883 | -7.2987 | -7.7761 | -9.466 | -10.4322 | -10.3216
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Leading the Way | Thermal headroom (MW) | 1.9782 | 1.7478 | 1.4991 | 1.1254 | 0.70263 | 0.10259 | -0.70836 | -1.5138 | -2.3933 | -3.4564 | -4.4398 | -5.3131 | -6.108 | -6.608 | -6.9015 | -7.0695 | -8.9335 | -8.7859 | -7.6867
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Steady Progression | Thermal headroom (MW) | 2.0519 | 2.002 | 1.9578 | 1.8423 | 1.7073 | 1.5357 | 1.2934 | 1.0275 | 0.71382 | 0.31347 | -0.10851 | -0.6216 | -1.2192 | -1.8334 | -2.5107 | -3.2551 | -7.2275 | -9.2121 | -9.9468
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | System Transformation | Thermal headroom (MW) | 2.0341 | 1.9558 | 1.8645 | 1.7106 | 1.5197 | 1.2822 | 0.89734 | 0.50632 | 0.03642 | -0.59474 | -1.2486 | -2.0132 | -2.8919 | -3.8547 | -4.8666 | -5.8472 | -9.2661 | -9.9637 | -9.8808
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | WPD Best View | Thermal headroom (MW) | 2.0245 | 1.9141 | 1.7928 | 1.564 | 1.3096 | 0.9148 | 0.34019 | -0.21216 | -0.83938 | -1.605 | -2.2976 | -3.0303 | -3.883 | -4.6127 | -5.3006 | -5.9716 | -8.5096 | -9.0681 | -8.9741
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Consumer Transformation | Thermal headroom (MW) | 16.9073 | 16.4489 | 15.7295 | 14.9807 | 13.6934 | 11.8453 | 9.4527 | 6.9693 | 4.4548 | 2.3843 | 0.45229 | -2.146 | -4.8251 | -7.2016 | -9.9131 | -12.0575 | -19.8931 | -22.2928 | -22.0479
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Leading the Way | Thermal headroom (MW) | 16.884 | 16.225 | 15.7282 | 14.5559 | 13.546 | 11.5806 | 9.0054 | 6.3233 | 3.5455 | 1.359 | -0.44201 | -2.8241 | -4.8228 | -6.7486 | -8.9708 | -10.4664 | -14.8452 | -15.3609 | -13.282
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Steady Progression | Thermal headroom (MW) | 17.0138 | 16.9302 | 16.8449 | 16.427 | 16.1073 | 15.5846 | 14.9914 | 14.2441 | 13.4234 | 12.6448 | 11.8557 | 10.6024 | 9.6635 | 8.6519 | 7.6084 | 6.528 | 1.1398 | -2.7948 | -4.9336
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | System Transformation | Thermal headroom (MW) | 16.9674 | 16.8335 | 16.4995 | 16.1707 | 15.7202 | 14.9825 | 14.0249 | 12.8771 | 11.3173 | 10.2482 | 9.1086 | 7.8717 | 6.5174 | 4.8419 | 3.5668 | 2.3928 | -3.2455 | -7.1537 | -7.5736
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | WPD Best View | Thermal headroom (MW) | 16.9195 | 16.4943 | 15.8489 | 14.7917 | 13.9036 | 12.0391 | 9.5954 | 7.0458 | 4.4501 | 2.3587 | 0.15014 | -2.4165 | -4.5433 | -6.5102 | -8.7311 | -10.2406 | -15.0114 | -16.1302 | -14.2433
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Consumer Transformation | Thermal headroom (MW) | 2.9856 | 2.6987 | 2.3924 | 2.0103 | 1.1564 | 0.57717 | -0.16839 | -0.96704 | -1.8211 | -2.7088 | -3.5809 | -4.9873 | -5.9429 | -6.7645 | -7.7599 | -8.2853 | -10.8849 | -12.3886 | -12.2574
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Leading the Way | Thermal headroom (MW) | 2.977 | 2.7088 | 2.4581 | 1.7015 | 1.2154 | 0.63569 | -0.13689 | -0.93856 | -1.8652 | -2.8278 | -3.8619 | -5.1759 | -6.0113 | -6.5877 | -7.282 | -7.4436 | -10.0367 | -10.1579 | -8.4431
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Steady Progression | Thermal headroom (MW) | 3.068 | 3.0808 | 3.1499 | 3.0915 | 3.0157 | 2.8953 | 2.7135 | 2.4885 | 2.1918 | 1.8442 | 1.4228 | 0.50897 | -0.08912 | -0.77337 | -1.5048 | -2.2586 | -7.051 | -9.6379 | -10.7111
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | System Transformation | Thermal headroom (MW) | 3.0301 | 3.0109 | 3.0142 | 2.9175 | 2.7549 | 2.5632 | 2.2303 | 1.8582 | 0.99827 | 0.41241 | -0.29022 | -1.1191 | -2.0575 | -3.4435 | -4.5912 | -5.7663 | -10.826 | -12.1356 | -12.2451
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | WPD Best View | Thermal headroom (MW) | 3.0012 | 2.7714 | 2.5658 | 1.9033 | 1.5081 | 1.0519 | 0.44027 | -0.21856 | -0.93925 | -1.7195 | -2.4957 | -3.6455 | -4.5042 | -5.2603 | -6.2527 | -6.8032 | -9.1299 | -9.8363 | -9.3168
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Consumer Transformation | Thermal headroom (MW) | 8.561 | 8.4666 | 8.396 | 8.2708 | 8.0694 | 7.8335 | 7.5547 | 7.2677 | 6.9503 | 6.6257 | 6.2684 | 5.9146 | 5.5787 | 5.3023 | 5.0853 | 4.903 | 3.7225 | 3.2731 | 3.287
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Leading the Way | Thermal headroom (MW) | 8.5563 | 8.468 | 8.4181 | 8.2989 | 8.11 | 7.8738 | 7.592 | 7.2994 | 6.9564 | 6.5866 | 6.2053 | 5.8466 | 5.5454 | 5.3345 | 5.1717 | 4.7719 | 3.8542 | 3.9633 | 4.4736
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Steady Progression | Thermal headroom (MW) | 8.5939 | 8.6148 | 8.668 | 8.6682 | 8.6852 | 8.6493 | 8.5842 | 8.4797 | 8.3723 | 8.2187 | 8.0625 | 7.8608 | 7.6218 | 7.3515 | 7.0745 | 6.7776 | 4.8679 | 3.5036 | 2.9888
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | System Transformation | Thermal headroom (MW) | 8.5746 | 8.5761 | 8.6064 | 8.5877 | 8.5861 | 8.4956 | 8.3506 | 8.1881 | 7.9758 | 7.7391 | 7.4762 | 7.1415 | 6.7699 | 6.361 | 5.9077 | 5.4516 | 3.7729 | 3.2235 | 3.213
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | WPD Best View | Thermal headroom (MW) | 8.5623 | 8.4694 | 8.402 | 8.2931 | 8.1389 | 7.9302 | 7.6823 | 7.4281 | 7.1482 | 6.8553 | 6.5588 | 6.2352 | 5.9114 | 5.6296 | 5.3858 | 5.1659 | 4.1498 | 3.4709 | 3.4233
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Consumer Transformation | Thermal headroom (MW) | 12.5093 | 12.2223 | 11.5566 | 10.9262 | 10.1396 | 9.1856 | 8.0944 | 7.0069 | 5.8443 | 4.6827 | 3.6304 | 2.6102 | 1.691 | 0.93949 | 0.37483 | -0.078342 | -4.7042 | -5.9811 | -5.9315
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Leading the Way | Thermal headroom (MW) | 12.4399 | 12.0752 | 11.5587 | 10.9319 | 10.2243 | 9.3871 | 8.4106 | 7.4024 | 6.2517 | 5.0272 | 3.938 | 2.9781 | 2.1934 | 1.6888 | 1.4675 | 0.94661 | -2.443 | -2.2509 | -0.60989
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Steady Progression | Thermal headroom (MW) | 12.6055 | 12.5466 | 12.5049 | 12.2322 | 11.9467 | 11.6381 | 11.2384 | 10.8283 | 10.3777 | 9.885 | 9.3711 | 8.7394 | 8.0497 | 7.2484 | 6.3274 | 5.3234 | -1.5646 | -5.1626 | -6.3528
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | System Transformation | Thermal headroom (MW) | 12.5341 | 12.4279 | 12.2617 | 12.0017 | 11.6772 | 11.3207 | 10.8423 | 10.2924 | 9.6442 | 8.9186 | 8.1129 | 7.1508 | 5.9866 | 4.7081 | 3.3754 | 2.0602 | -4.375 | -5.6129 | -5.518
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | WPD Best View | Thermal headroom (MW) | 12.5347 | 12.3422 | 12.0308 | 11.5278 | 10.999 | 10.3493 | 9.5738 | 8.7982 | 8.0039 | 7.2244 | 6.3987 | 5.5238 | 4.6611 | 3.8365 | 3.0698 | 2.3266 | -2.9416 | -5.0708 | -5.4859
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Consumer Transformation | Thermal headroom (MW) | 45.9954 | 43.5271 | 41.6447 | 39.2041 | 36.1766 | 29.2465 | 22.0248 | 14.1709 | 5.9658 | -4.1087 | -13.7469 | -24.7188 | -37.2093 | -47.8987 | -58.9769 | -69.4785 | -104.7017 | -121.0052 | -121.2035
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Leading the Way | Thermal headroom (MW) | 45.7922 | 43.1528 | 41.6544 | 39.1528 | 36.0321 | 27.5858 | 18.2234 | 8.5883 | -3.1909 | -15.1185 | -27.4216 | -41.5202 | -54.4882 | -67.8661 | -78.6753 | -89.4958 | -110.7653 | -110.0333 | -98.7107
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Steady Progression | Thermal headroom (MW) | 46.6384 | 46.8821 | 47.4297 | 46.9128 | 46.2311 | 43.0495 | 40.4608 | 37.4386 | 32.9913 | 28.8678 | 24.2346 | 18.2896 | 12.0263 | 5.3525 | -0.78791 | -8.3525 | -38.7335 | -71.7276 | -87.5241
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | System Transformation | Thermal headroom (MW) | 46.2497 | 46.1819 | 46.0345 | 45.2981 | 44.1133 | 38.4899 | 33.5806 | 27.9761 | 21.7846 | 14.7753 | 6.955 | -3.778 | -14.0409 | -23.8427 | -34.1631 | -44.996 | -82.3247 | -102.617 | -103.3704
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | WPD Best View | Thermal headroom (MW) | 46.0435 | 43.6776 | 41.9541 | 39.6812 | 36.8615 | 30.2082 | 23.255 | 15.7201 | 7.9379 | -1.7333 | -10.9586 | -21.5321 | -33.5489 | -43.8141 | -54.6051 | -65.0255 | -100.8924 | -118.609 | -119.0691
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Consumer Transformation | Thermal headroom (MW) | 19.1375 | 18.6314 | 18.486 | 18.3134 | 18.1085 | 17.8407 | 17.5383 | 17.2403 | 16.9335 | 16.2417 | 15.9091 | 15.611 | 14.9032 | 14.6037 | 13.856 | 13.3711 | 10.4699 | 9.1912 | 8.8436
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Leading the Way | Thermal headroom (MW) | 19.0801 | 18.5729 | 18.4482 | 18.2843 | 18.0914 | 17.8237 | 17.5309 | 17.219 | 16.54 | 16.1978 | 15.8732 | 15.1729 | 14.8694 | 14.0356 | 13.5098 | 12.7122 | 11.2318 | 10.9232 | 11.1693
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Steady Progression | Thermal headroom (MW) | 19.2245 | 19.2291 | 19.2654 | 19.2357 | 19.2082 | 19.1597 | 19.103 | 19.0369 | 18.5921 | 18.4803 | 18.337 | 18.1544 | 17.9469 | 17.7211 | 17.4779 | 16.866 | 14.5405 | 12.5953 | 11.772
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | System Transformation | Thermal headroom (MW) | 19.1625 | 19.1404 | 19.1269 | 19.091 | 19.045 | 18.6089 | 18.4907 | 18.3491 | 18.1689 | 17.9725 | 17.718 | 17.0575 | 16.7441 | 16.389 | 15.6772 | 14.9389 | 12.3197 | 10.5422 | 10.1799
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | WPD Best View | Thermal headroom (MW) | 19.1375 | 18.6314 | 18.486 | 18.3134 | 18.1085 | 17.8407 | 17.5383 | 17.2403 | 16.9335 | 16.2417 | 15.9091 | 15.611 | 14.9032 | 14.6037 | 13.856 | 13.3711 | 10.4699 | 9.1912 | 8.8436
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Consumer Transformation | Thermal headroom (MW) | 4.6494 | 4.6116 | 4.6142 | 4.573 | 4.5228 | 1.8532 | -0.60498 | -3.1842 | -5.8717 | -8.933 | -12.1348 | -16.4327 | -20.9418 | -25.4669 | -29.3653 | -33.465 | -44.6238 | -51.0299 | -51.2744
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Leading the Way | Thermal headroom (MW) | 4.6473 | 4.6122 | 4.6245 | 4.5899 | 4.5521 | 0.92983 | -2.4699 | -6.1903 | -10.2321 | -14.6889 | -19.5933 | -25.2242 | -30.9527 | -36.6682 | -41.2388 | -45.6458 | -52.8916 | -52.5437 | -49.0702
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Steady Progression | Thermal headroom (MW) | 4.67 | 4.7108 | 4.7984 | 4.8236 | 4.8667 | 2.997 | 1.578 | 0.049154 | -1.707 | -3.5919 | -5.5861 | -8.1927 | -10.9358 | -13.8182 | -16.346 | -18.9741 | -27.4591 | -37.4107 | -44.1775
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | System Transformation | Thermal headroom (MW) | 4.6576 | 4.6887 | 4.7634 | 4.7774 | 4.8082 | 2.1935 | -0.1693 | -2.6807 | -5.2977 | -8.2458 | -11.3456 | -15.485 | -19.8304 | -24.2067 | -27.9753 | -31.9471 | -42.9641 | -49.6773 | -50.0243
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | WPD Best View | Thermal headroom (MW) | 4.6494 | 4.6116 | 4.6142 | 4.573 | 4.5228 | 1.8532 | -0.60498 | -3.1842 | -5.8717 | -8.933 | -12.1348 | -16.4327 | -20.9418 | -25.4669 | -29.3653 | -33.465 | -44.6238 | -51.0299 | -51.2744
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Consumer Transformation | Thermal headroom (MW) | 2.5881 | 2.3441 | 2.2174 | 1.9741 | 1.0766 | 0.62577 | 0.00039773 | -0.88731 | -1.4619 | -2.0869 | -3.2576 | -4.3227 | -5.7178 | -6.7157 | -8.1067 | -9.4633 | -14.0781 | -16.0857 | -16.8029
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Leading the Way | Thermal headroom (MW) | 2.5713 | 2.3207 | 2.2297 | 1.996 | 0.8794 | 0.44314 | -0.54146 | -1.0693 | -1.6289 | -2.8803 | -3.7086 | -4.8711 | -5.731 | -6.93 | -8.158 | -8.8391 | -11.7397 | -12.8662 | -11.5991
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Steady Progression | Thermal headroom (MW) | 2.6391 | 2.6414 | 2.7644 | 2.7866 | 2.3176 | 2.2913 | 2.2654 | 2.1813 | 2.0903 | 1.9829 | 1.8609 | 1.7032 | 1.5328 | 0.97063 | 0.75047 | 0.51422 | -2.3134 | -5.8221 | -6.8585
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | System Transformation | Thermal headroom (MW) | 2.6048 | 2.568 | 2.668 | 2.6516 | 1.9745 | 1.8927 | 1.7929 | 1.6651 | 1.4678 | 1.2583 | 0.67165 | 0.41968 | -0.21263 | -0.50719 | -1.1737 | -1.9894 | -6.6567 | -9.2334 | -9.8601
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | WPD Best View | Thermal headroom (MW) | 2.5881 | 2.3441 | 2.2174 | 1.9741 | 1.0766 | 0.62577 | 0.00039773 | -0.88731 | -1.4619 | -2.0869 | -3.2576 | -4.3227 | -5.7178 | -6.7157 | -8.1067 | -9.4633 | -14.0781 | -16.0857 | -16.8029
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Consumer Transformation | Thermal headroom (MW) | 16.1937 | 15.9754 | 15.4236 | 15.1095 | 14.7576 | 14.3255 | 13.7162 | 13.1597 | 12.497 | 11.7973 | 10.9931 | 10.1436 | 9.1509 | 8.2424 | 7.2359 | 6.313 | 2.8492 | 1.9156 | 2.095
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Leading the Way | Thermal headroom (MW) | 16.1768 | 15.9834 | 15.3632 | 15.0325 | 14.7161 | 14.2531 | 13.6279 | 12.9786 | 12.2917 | 11.4959 | 10.5829 | 9.6539 | 8.6595 | 7.5877 | 6.6133 | 5.7581 | 3.7374 | 4.0437 | 5.4989
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Steady Progression | Thermal headroom (MW) | 16.2785 | 16.3032 | 16.1328 | 16.1026 | 16.0589 | 15.9896 | 15.9029 | 15.7573 | 15.633 | 15.4778 | 15.2777 | 15.0036 | 14.6871 | 14.2596 | 13.8051 | 13.3291 | 10.098 | 6.7365 | 5.7948
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | System Transformation | Thermal headroom (MW) | 16.2214 | 16.2119 | 15.9078 | 15.8295 | 15.7255 | 15.5757 | 15.3466 | 15.0834 | 14.8073 | 14.4677 | 14.1089 | 13.6104 | 13.0623 | 12.3885 | 11.6372 | 10.8315 | 6.5653 | 4.6617 | 4.8403
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | WPD Best View | Thermal headroom (MW) | 16.2148 | 16.0529 | 15.5757 | 15.336 | 15.0783 | 14.7825 | 14.3608 | 13.9991 | 13.5976 | 13.1673 | 12.688 | 12.176 | 11.5944 | 11.0197 | 10.381 | 9.735 | 6.3626 | 4.2635 | 4.0238
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Consumer Transformation | Thermal headroom (MW) | 2.8279 | 2.7569 | 2.6744 | 2.5415 | 2.3747 | 2.0591 | 1.7011 | 1.4083 | 1.0832 | 0.75508 | 0.43464 | 0.088933 | -0.28689 | -0.59619 | -0.84086 | -1.0532 | -1.8029 | -2.4277 | -2.5134
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Leading the Way | Thermal headroom (MW) | 2.8285 | 2.7509 | 2.6984 | 2.558 | 2.4016 | 2.0784 | 1.7188 | 1.4051 | 1.0581 | 0.71931 | 0.40963 | 0.064493 | -0.21408 | -0.41702 | -0.52632 | -0.6005 | -1.38 | -1.4728 | -0.92172
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Steady Progression | Thermal headroom (MW) | 2.8568 | 2.8669 | 2.9166 | 2.8869 | 2.8657 | 2.7942 | 2.7201 | 2.6461 | 2.5496 | 2.4305 | 2.2758 | 2.0921 | 1.8893 | 1.6544 | 1.4026 | 1.1319 | -0.5304 | -1.6539 | -1.9781
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | System Transformation | Thermal headroom (MW) | 2.8489 | 2.8519 | 2.8784 | 2.8429 | 2.8006 | 2.6933 | 2.5645 | 2.4326 | 2.2825 | 2.084 | 1.849 | 1.5671 | 1.2423 | 0.89851 | 0.53531 | 0.14631 | -1.3845 | -1.8251 | -1.8023
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | WPD Best View | Thermal headroom (MW) | 2.8381 | 2.7866 | 2.7351 | 2.6375 | 2.5138 | 2.2524 | 1.9563 | 1.729 | 1.4789 | 1.2141 | 0.94021 | 0.63521 | 0.33721 | 0.058428 | -0.23978 | -0.52739 | -1.8185 | -2.5262 | -2.5013
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Consumer Transformation | Thermal headroom (MW) | 0.42006 | 0.28371 | 0.15888 | -0.043887 | -0.25237 | -0.4785 | -0.751 | -1.0249 | -1.3294 | -1.6412 | -1.9528 | -2.2633 | -2.5409 | -2.7796 | -3.0311 | -3.2473 | -4.4087 | -4.7491 | -4.5137
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Leading the Way | Thermal headroom (MW) | 0.41108 | 0.28258 | 0.17019 | -0.039237 | -0.23708 | -0.45854 | -0.74929 | -1.0266 | -1.3436 | -1.6652 | -1.9614 | -2.2271 | -2.4501 | -2.6796 | -2.8108 | -3.026 | -3.9098 | -3.6688 | -2.9987
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Steady Progression | Thermal headroom (MW) | 0.47143 | 0.50032 | 0.57607 | 0.5741 | 0.56787 | 0.56111 | 0.53552 | 0.49524 | 0.41882 | 0.33822 | 0.22273 | 0.046988 | -0.15147 | -0.37413 | -0.61759 | -0.89213 | -2.3142 | -3.3828 | -3.6931
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | System Transformation | Thermal headroom (MW) | 0.44619 | 0.4417 | 0.48377 | 0.43537 | 0.39146 | 0.34283 | 0.23292 | 0.10825 | -0.047047 | -0.23832 | -0.46457 | -0.75713 | -1.0991 | -1.4624 | -1.8376 | -2.1915 | -3.5305 | -3.852 | -3.6531
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | WPD Best View | Thermal headroom (MW) | 0.42514 | 0.29473 | 0.18925 | 0.004115 | -0.18281 | -0.38181 | -0.62342 | -0.86457 | -1.1316 | -1.4117 | -1.7 | -1.9973 | -2.2821 | -2.5216 | -2.7305 | -2.9844 | -4.1542 | -4.5884 | -4.3693
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Consumer Transformation | Thermal headroom (MW) | 14.8915 | 14.4102 | 14.335 | 14.183 | 14.0427 | 13.8619 | 13.5516 | 13.2104 | 12.8585 | 12.163 | 11.8405 | 11.454 | 10.5345 | 9.9127 | 8.8853 | 8.2235 | 4.6751 | 2.882 | 2.2395
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Leading the Way | Thermal headroom (MW) | 14.8673 | 14.3905 | 14.3504 | 14.1792 | 14.0649 | 13.8935 | 13.5863 | 13.2536 | 12.5219 | 12.1859 | 11.8532 | 11.2076 | 10.6481 | 9.7292 | 9.1326 | 8.2425 | 6.3144 | 5.5322 | 5.9271
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Steady Progression | Thermal headroom (MW) | 14.9375 | 14.969 | 15.0727 | 15.0868 | 15.1161 | 15.1467 | 15.1573 | 15.1342 | 14.7641 | 14.7509 | 14.7011 | 14.5947 | 14.4969 | 14.3653 | 14.224 | 13.7041 | 12.0224 | 9.9139 | 9.0366
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | System Transformation | Thermal headroom (MW) | 14.9043 | 14.9159 | 14.9954 | 14.9839 | 14.9948 | 14.6331 | 14.5966 | 14.5333 | 14.4687 | 14.3727 | 14.2361 | 13.7178 | 13.5191 | 13.3112 | 12.7195 | 12.1403 | 9.6513 | 7.3852 | 6.994
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | WPD Best View | Thermal headroom (MW) | 14.8915 | 14.4102 | 14.335 | 14.183 | 14.0427 | 13.8619 | 13.5516 | 13.2104 | 12.8585 | 12.163 | 11.8405 | 11.454 | 10.5345 | 9.9127 | 8.8853 | 8.2235 | 4.6751 | 2.882 | 2.2395
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Consumer Transformation | Thermal headroom (MW) | 2.8541 | 2.5498 | 2.2547 | 1.5145 | 0.73334 | -0.34396 | -1.3724 | -2.7703 | -4.3684 | -6.1015 | -7.8877 | -9.677 | -11.2758 | -12.3533 | -13.483 | -14.6174 | -16.897 | -17.2232 | -16.34
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Leading the Way | Thermal headroom (MW) | 2.8336 | 2.5425 | 2.2947 | 1.4198 | 0.53606 | -0.76136 | -2.4079 | -4.2448 | -6.3855 | -8.6662 | -11.0443 | -13.3036 | -15.1476 | -16.2046 | -17.1357 | -17.798 | -18.3823 | -17.2445 | -15.6705
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Steady Progression | Thermal headroom (MW) | 2.9692 | 2.9858 | 3.0407 | 2.7426 | 2.4258 | 1.9199 | 1.4864 | 0.97428 | 0.36364 | -0.47485 | -1.3796 | -2.3768 | -3.3182 | -3.9602 | -4.6188 | -5.3122 | -7.9343 | -12.5658 | -14.2462
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | System Transformation | Thermal headroom (MW) | 2.9069 | 2.8606 | 2.8495 | 2.3851 | 1.903 | 1.1613 | 0.35955 | -0.81932 | -2.1145 | -3.5354 | -5.02 | -6.6535 | -8.1201 | -9.0247 | -10.0562 | -11.1545 | -14.3342 | -15.7939 | -15.1784
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | WPD Best View | Thermal headroom (MW) | 2.8592 | 2.5646 | 2.2851 | 1.5625 | 0.80289 | -0.24728 | -1.3219 | -2.7299 | -4.3139 | -6.0306 | -7.7977 | -9.5635 | -11.1367 | -12.1875 | -13.292 | -14.3988 | -16.6425 | -17.0625 | -16.1956
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Consumer Transformation | Thermal headroom (MW) | -2.828 | -2.9935 | -3.1398 | -3.3767 | -3.5901 | -3.8241 | -4.0838 | -4.3417 | -4.6156 | -4.8992 | -5.189 | -5.4441 | -5.6927 | -5.9603 | -6.1787 | -6.368 | -7.3173 | -7.564 | -7.3516
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Leading the Way | Thermal headroom (MW) | -2.839 | -2.9951 | -3.1583 | -3.3457 | -3.5419 | -3.775 | -4.0512 | -4.2911 | -4.5796 | -4.8853 | -5.1814 | -5.4205 | -5.7156 | -5.9335 | -6.0672 | -6.2535 | -7.0173 | -6.7646 | -6.2823
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Steady Progression | Thermal headroom (MW) | -2.7655 | -2.7411 | -2.684 | -2.6749 | -2.7229 | -2.7352 | -2.7645 | -2.8125 | -2.8855 | -2.9605 | -3.0748 | -3.2436 | -3.4492 | -3.6657 | -3.9045 | -4.1525 | -5.6207 | -6.8475 | -7.3083
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | System Transformation | Thermal headroom (MW) | -2.7995 | -2.811 | -2.7919 | -2.8597 | -2.9014 | -2.9671 | -3.0979 | -3.2304 | -3.4026 | -3.5913 | -3.8169 | -4.1194 | -4.4612 | -4.8158 | -5.1613 | -5.5062 | -6.8871 | -7.3306 | -7.2176
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | WPD Best View | Thermal headroom (MW) | -2.8229 | -2.9787 | -3.1094 | -3.3287 | -3.5205 | -3.7274 | -3.9562 | -4.1814 | -4.4178 | -4.6697 | -4.9362 | -5.1781 | -5.4311 | -5.6446 | -5.8781 | -6.1051 | -7.0628 | -7.4033 | -7.2073
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Consumer Transformation | Thermal headroom (MW) | 23.672 | 23.1546 | 23.0899 | 22.6735 | 22.4251 | 22.0165 | 21.445 | 20.9084 | 20.3443 | 19.4265 | 18.8873 | 18.3346 | 17.4838 | 17.0598 | 16.4322 | 16.2161 | 13.1675 | 11.9014 | 11.9242
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Leading the Way | Thermal headroom (MW) | 23.6525 | 23.1042 | 22.8357 | 22.6539 | 22.4132 | 21.9897 | 21.4116 | 20.8704 | 19.9357 | 19.3532 | 18.8624 | 18.1405 | 17.8832 | 17.3642 | 17.3875 | 16.7487 | 15.1113 | 14.8909 | 15.5782
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Steady Progression | Thermal headroom (MW) | 23.7425 | 23.8097 | 23.985 | 24.041 | 23.8451 | 23.8466 | 23.8336 | 23.7962 | 23.3746 | 23.2704 | 23.1598 | 22.9796 | 22.7731 | 22.5346 | 22.2811 | 21.6587 | 19.6009 | 18.1934 | 17.6888
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | System Transformation | Thermal headroom (MW) | 23.7043 | 23.7112 | 23.8406 | 23.6322 | 23.6148 | 23.2111 | 23.0923 | 22.945 | 22.7531 | 22.5264 | 22.2611 | 21.5829 | 21.2226 | 20.8402 | 20.1278 | 19.4221 | 17.4744 | 16.1891 | 16.2531
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | WPD Best View | Thermal headroom (MW) | 23.6771 | 23.1656 | 23.1125 | 22.7215 | 22.4946 | 22.1131 | 21.5726 | 21.0688 | 20.5422 | 19.656 | 19.1401 | 18.6006 | 17.7426 | 17.2907 | 16.6126 | 16.3365 | 13.4219 | 12.0621 | 12.0686
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Consumer Transformation | Thermal headroom (MW) | 13.9288 | 13.7484 | 13.6757 | 12.5981 | 11.4813 | 9.6721 | 7.8781 | 5.9847 | 3.7024 | 1.1073 | -1.2249 | -4.0755 | -6.6042 | -8.4859 | -10.4483 | -12.4447 | -20.7336 | -22.4101 | -21.344
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Leading the Way | Thermal headroom (MW) | 13.9133 | 13.697 | 13.7273 | 12.3664 | 10.9646 | 8.6915 | 6.4025 | 3.1877 | -0.39381 | -3.2222 | -6.1433 | -8.9618 | -11.1589 | -12.6044 | -13.8619 | -15.254 | -19.9626 | -19.1608 | -16.3307
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Steady Progression | Thermal headroom (MW) | 14.0173 | 14.2101 | 14.5967 | 14.0877 | 13.6003 | 12.7277 | 12.069 | 11.2871 | 10.5954 | 10.0575 | 9.5009 | 8.7411 | 7.8612 | 7.0269 | 6.1677 | 4.9335 | -0.56426 | -6.9028 | -8.4945
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | System Transformation | Thermal headroom (MW) | 13.9644 | 14.1037 | 14.3766 | 13.634 | 12.8488 | 11.5482 | 10.3305 | 8.9589 | 7.8452 | 6.6821 | 5.1796 | 2.8297 | 1.1884 | -0.017141 | -1.2759 | -2.7057 | -10.1055 | -12.3958 | -11.6446
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | WPD Best View | Thermal headroom (MW) | 13.9339 | 13.7594 | 13.6983 | 12.6337 | 11.5046 | 9.5523 | 7.6735 | 5.6789 | 3.7569 | 1.1781 | -1.135 | -3.9619 | -6.4651 | -8.3201 | -10.2573 | -12.2261 | -20.4791 | -22.2494 | -21.1996
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Consumer Transformation | Thermal headroom (MW) | 24.9897 | 20.5714 | 16.5502 | 11.5953 | 6.0817 | -0.44483 | -8.6148 | -16.6783 | -25.2002 | -37.3715 | -46.2874 | -56.4888 | -65.553 | -73.4913 | -80.8963 | -87.2423 | -120.5774 | -135.1923 | -133.7743
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Leading the Way | Thermal headroom (MW) | 24.6059 | 19.1463 | 15.2526 | 10.4352 | 5.3424 | -1.3706 | -9.8879 | -17.9321 | -30.1117 | -39.713 | -49.0306 | -58.1963 | -65.5911 | -71.6105 | -77.9281 | -86.719 | -110.5134 | -110.1467 | -99.9565
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Steady Progression | Thermal headroom (MW) | 27.5539 | 25.01 | 25.1279 | 23.6792 | 22.0034 | 20.486 | 18.7047 | 16.6115 | 13.8735 | 10.662 | 6.7914 | 1.6322 | -3.4728 | -9.1996 | -15.3169 | -25.1521 | -62.628 | -89.4146 | -98.2923
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | System Transformation | Thermal headroom (MW) | 25.3968 | 23.5795 | 22.348 | 20.0985 | 18.5572 | 16.0406 | 12.7639 | 9.003 | 3.9773 | -1.479 | -7.4943 | -18.0358 | -26.0604 | -35.0671 | -44.3145 | -53.4785 | -91.9502 | -105.8523 | -108.0725
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | WPD Best View | Thermal headroom (MW) | 26.7907 | 21.5153 | 18.5584 | 14.8981 | 9.5836 | 4.1745 | -2.6242 | -9.4135 | -16.6178 | -25.6779 | -33.4263 | -42.4306 | -50.947 | -58.7302 | -66.5402 | -75.4464 | -106.058 | -123.454 | -124.2747
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Consumer Transformation | Thermal headroom (MW) | 2.4925 | 2.2661 | 2.0203 | 1.711 | 1.3815 | 0.94824 | 0.39469 | -0.18064 | -0.79313 | -1.7353 | -2.2961 | -2.9902 | -3.6061 | -4.1353 | -4.5553 | -4.8958 | -6.5847 | -7.9091 | -8.0157
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Leading the Way | Thermal headroom (MW) | 2.4788 | 2.2427 | 2.0211 | 1.6859 | 1.3586 | 0.92044 | 0.36576 | -0.21727 | -1.2043 | -1.832 | -2.4266 | -3.0244 | -3.5185 | -3.855 | -4.0384 | -4.5032 | -5.9694 | -6.0984 | -5.6322
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Steady Progression | Thermal headroom (MW) | 2.553 | 2.5121 | 2.4956 | 2.4096 | 2.3364 | 2.2294 | 2.0935 | 1.9304 | 1.7347 | 1.514 | 1.2392 | 0.89899 | 0.54056 | 0.13125 | -0.30917 | -1.1323 | -3.919 | -5.9589 | -6.5756
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | System Transformation | Thermal headroom (MW) | 2.5281 | 2.4507 | 2.4024 | 2.2668 | 2.1624 | 2.0042 | 1.792 | 1.5357 | 1.2083 | 0.84414 | 0.43906 | -0.42691 | -0.98821 | -1.5827 | -2.2482 | -2.9164 | -5.7391 | -6.7772 | -7.1398
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | WPD Best View | Thermal headroom (MW) | 2.5302 | 2.4361 | 2.3441 | 2.1828 | 2.0184 | 1.8005 | 1.5472 | 1.2514 | 0.919 | 0.57679 | 0.2143 | -0.16883 | -0.59665 | -1.0172 | -1.4072 | -2.1519 | -3.9714 | -5.3489 | -5.6527
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Consumer Transformation | Thermal headroom (MW) | 3.5842 | 3.3568 | 2.9022 | 2.6629 | 2.4194 | 2.1718 | 1.8478 | 1.451 | 1.03 | 0.23299 | -0.2044 | -0.53954 | -0.8885 | -1.2261 | -1.4862 | -1.8287 | -3.8569 | -4.4568 | -4.0717
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Leading the Way | Thermal headroom (MW) | 3.5502 | 3.0364 | 2.9386 | 2.7301 | 2.514 | 2.2302 | 1.8816 | 1.5061 | 0.68356 | 0.21674 | -0.21707 | -0.55971 | -0.93307 | -1.287 | -1.8951 | -2.777 | -3.7622 | -3.2814 | -2.7158
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Steady Progression | Thermal headroom (MW) | 3.6646 | 3.7269 | 3.8513 | 3.6052 | 3.6507 | 3.6899 | 3.745 | 3.7429 | 3.6306 | 3.5013 | 3.3139 | 3.0547 | 2.7668 | 2.4491 | 2.1027 | 1.3756 | -0.70036 | -2.4414 | -2.9878
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | System Transformation | Thermal headroom (MW) | 3.6107 | 3.6207 | 3.3793 | 3.4002 | 3.396 | 3.3681 | 3.2518 | 3.1255 | 2.8485 | 2.5383 | 2.1907 | 1.3936 | 0.91179 | 0.39341 | -0.12185 | -0.61884 | -2.9347 | -3.7069 | -3.8401
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | WPD Best View | Thermal headroom (MW) | 3.5842 | 3.3568 | 2.9022 | 2.6629 | 2.4194 | 2.1718 | 1.8478 | 1.451 | 1.03 | 0.23299 | -0.2044 | -0.53954 | -0.8885 | -1.2261 | -1.4862 | -1.8287 | -3.8569 | -4.4568 | -4.0717
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Consumer Transformation | Thermal headroom (MW) | 14.2169 | 13.9164 | 13.6205 | 13.2176 | 12.3764 | 11.8555 | 11.1442 | 10.4117 | 9.6279 | 8.8116 | 8.0445 | 6.7429 | 5.8612 | 5.0887 | 4.1055 | 3.6075 | 1.0284 | -0.51868 | -0.47271
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Leading the Way | Thermal headroom (MW) | 14.2082 | 13.9256 | 13.6534 | 12.8627 | 12.4179 | 11.8965 | 11.1335 | 10.4129 | 9.5986 | 8.7062 | 7.8443 | 6.6445 | 5.9352 | 5.4106 | 4.7259 | 4.5651 | 2.1432 | 1.744 | 3.1296
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Steady Progression | Thermal headroom (MW) | 14.2817 | 14.2726 | 14.3111 | 14.2294 | 14.1403 | 14.0079 | 13.8473 | 13.6666 | 13.4159 | 13.113 | 12.75 | 11.9265 | 11.4145 | 10.855 | 10.2382 | 9.5772 | 5.4396 | 2.9286 | 1.8661
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | System Transformation | Thermal headroom (MW) | 14.2579 | 14.214 | 14.1892 | 14.0528 | 13.8825 | 13.7028 | 13.4513 | 13.1137 | 12.3438 | 11.842 | 11.2485 | 10.5413 | 9.7678 | 8.5425 | 7.5858 | 6.604 | 2.1332 | 0.77616 | 0.55191
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | WPD Best View | Thermal headroom (MW) | 14.2169 | 13.9164 | 13.6205 | 13.2176 | 12.3764 | 11.8555 | 11.1442 | 10.4117 | 9.6279 | 8.8116 | 8.0445 | 6.7429 | 5.8612 | 5.0887 | 4.1055 | 3.6075 | 1.0284 | -0.51868 | -0.47271
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Consumer Transformation | Thermal headroom (MW) | 14.3785 | 14.0093 | 13.6833 | 13.4074 | 13.0758 | 12.4983 | 11.8698 | 11.2203 | 10.5428 | 9.857 | 9.1497 | 8.4468 | 7.836 | 7.3248 | 6.9731 | 6.7357 | 5.115 | 5.0417 | 5.7219
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Leading the Way | Thermal headroom (MW) | 14.2375 | 13.7548 | 13.3014 | 12.9481 | 12.5044 | 11.9218 | 11.2582 | 10.5758 | 9.8592 | 9.1428 | 8.4992 | 7.9747 | 7.5862 | 7.3264 | 7.0961 | 6.6893 | 5.8347 | 6.4005 | 7.3492
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Steady Progression | Thermal headroom (MW) | 14.5009 | 14.2823 | 14.1319 | 13.9757 | 13.7776 | 13.5886 | 13.3977 | 13.181 | 12.9271 | 12.6273 | 12.2953 | 11.9389 | 11.5714 | 11.1716 | 10.7748 | 10.398 | 8.7534 | 8.0415 | 8.0297
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | System Transformation | Thermal headroom (MW) | 14.3959 | 14.0728 | 13.8079 | 13.5973 | 13.3544 | 13.112 | 12.8383 | 12.5244 | 12.1512 | 11.7366 | 11.2754 | 10.7676 | 10.2374 | 9.7 | 9.2104 | 8.7888 | 7.6785 | 7.6597 | 8.1675
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | WPD Best View | Thermal headroom (MW) | 14.3785 | 14.0093 | 13.6621 | 13.3631 | 13.0182 | 12.4604 | 11.8578 | 11.2203 | 10.5428 | 9.857 | 9.1497 | 8.4468 | 7.836 | 7.3179 | 6.7884 | 6.3658 | 5.115 | 5.0417 | 5.7219
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Consumer Transformation | Thermal headroom (MW) | 5.5676 | 5.2289 | 4.9086 | 4.2036 | 3.6405 | 2.7522 | 1.5181 | 0.28918 | -0.99082 | -2.5761 | -3.8154 | -5.5885 | -7.6834 | -9.5943 | -11.6025 | -13.5693 | -22.3666 | -25.3759 | -25.3807
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Leading the Way | Thermal headroom (MW) | 5.5305 | 5.1283 | 4.9278 | 4.1194 | 3.5374 | 2.6143 | 1.3136 | 0.069654 | -1.6845 | -2.9882 | -4.2322 | -5.9222 | -7.6779 | -9.3801 | -11.0381 | -12.8687 | -18.799 | -19.6475 | -18.0657
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Steady Progression | Thermal headroom (MW) | 5.6514 | 5.6713 | 5.8186 | 5.5019 | 5.3751 | 5.1944 | 5.0156 | 4.7878 | 4.521 | 4.1985 | 3.8294 | 3.3586 | 2.8321 | 2.2324 | 1.6241 | 0.60431 | -3.3415 | -7.1163 | -8.4591
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | System Transformation | Thermal headroom (MW) | 5.6028 | 5.5734 | 5.5932 | 5.1981 | 4.974 | 4.7059 | 4.3688 | 3.9741 | 3.51 | 2.9623 | 2.3551 | 1.2802 | 0.48059 | -0.32553 | -1.1498 | -1.9656 | -7.6136 | -10.7732 | -11.0668
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | WPD Best View | Thermal headroom (MW) | 5.5676 | 5.2289 | 4.9086 | 4.2036 | 3.6405 | 2.7522 | 1.5181 | 0.28918 | -0.99082 | -2.5761 | -3.8154 | -5.5885 | -7.6834 | -9.5943 | -11.6025 | -13.5693 | -22.3666 | -25.3759 | -25.3807
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Consumer Transformation | Thermal headroom (MW) | 8.7391 | 7.6153 | 6.9312 | 6.2831 | 5.4925 | 4.3991 | 2.9373 | 1.7372 | 0.27126 | -1.6313 | -3.2834 | -5.1983 | -7.4617 | -9.1906 | -11.3229 | -13.0014 | -19.1973 | -20.9124 | -20.3299
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Leading the Way | Thermal headroom (MW) | 8.5816 | 7.2581 | 6.4114 | 5.6349 | 4.6211 | 3.4173 | 1.8286 | 0.51795 | -1.3889 | -3.0548 | -4.752 | -6.6593 | -8.2114 | -9.9991 | -11.3613 | -12.8155 | -15.5855 | -15.3254 | -12.721
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Steady Progression | Thermal headroom (MW) | 8.9544 | 8.7152 | 8.6153 | 8.4435 | 8.1909 | 7.9366 | 7.6439 | 7.4688 | 6.8172 | 6.5061 | 6.1878 | 5.7702 | 5.3226 | 4.8133 | 4.2692 | 3.324 | -0.99629 | -5.6508 | -6.4081
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | System Transformation | Thermal headroom (MW) | 8.8127 | 8.3171 | 7.9857 | 7.6851 | 7.3173 | 6.4876 | 5.9652 | 5.5515 | 5.0932 | 4.5453 | 3.8901 | 2.8307 | 2.0523 | 1.2274 | -0.10437 | -1.4361 | -7.0485 | -9.8192 | -9.1507
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | WPD Best View | Thermal headroom (MW) | 8.7404 | 7.6182 | 6.9372 | 6.2928 | 5.5071 | 4.4204 | 2.9671 | 1.7776 | 0.32577 | -1.5604 | -3.1935 | -5.0848 | -7.3226 | -9.0248 | -11.1319 | -12.7828 | -18.9429 | -20.7516 | -20.1855
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Consumer Transformation | Thermal headroom (MW) | 2.1735 | 1.9832 | 1.745 | 1.4858 | 1.161 | 0.74265 | 0.1977 | -0.32707 | -0.88671 | -1.5125 | -2.1424 | -2.7822 | -3.3637 | -3.8642 | -4.2528 | -4.5632 | -5.8132 | -6.6173 | -6.6772
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Leading the Way | Thermal headroom (MW) | 2.1696 | 1.9797 | 1.7806 | 1.5143 | 1.2049 | 0.77978 | 0.20368 | -0.33537 | -0.94323 | -1.6434 | -2.2919 | -2.9006 | -3.3931 | -3.7457 | -3.9304 | -4.0329 | -5.5485 | -5.5333 | -4.7021
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Steady Progression | Thermal headroom (MW) | 2.2303 | 2.1927 | 2.1679 | 2.0995 | 2.0165 | 1.8951 | 1.734 | 1.5579 | 1.3453 | 1.0989 | 0.80135 | 0.43653 | 0.036321 | -0.42364 | -0.9367 | -1.4979 | -4.4239 | -5.9038 | -6.5119
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | System Transformation | Thermal headroom (MW) | 2.2076 | 2.1537 | 2.0929 | 1.9935 | 1.8834 | 1.7021 | 1.4557 | 1.1609 | 0.81518 | 0.42293 | -0.026695 | -0.56655 | -1.2322 | -1.946 | -2.6895 | -3.418 | -5.9833 | -6.56 | -6.568
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | WPD Best View | Thermal headroom (MW) | 2.1804 | 1.9981 | 1.7754 | 1.5338 | 1.2306 | 0.83933 | 0.32528 | -0.16671 | -0.68483 | -1.2557 | -1.8508 | -2.4617 | -3.0309 | -3.5369 | -3.9523 | -4.3003 | -5.6596 | -6.4445 | -6.5409
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Consumer Transformation | Thermal headroom (MW) | 4.3712 | 4.2172 | 4.0852 | 3.7842 | 3.4495 | 3.0497 | 2.6282 | 2.2244 | 1.7931 | 1.0119 | 0.61074 | 0.17002 | -0.21091 | -0.52579 | -0.88202 | -1.4846 | -3.9466 | -4.9285 | -4.7854
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Leading the Way | Thermal headroom (MW) | 4.3569 | 4.196 | 4.1119 | 3.7834 | 3.4143 | 2.9834 | 2.5564 | 2.1588 | 1.3413 | 0.90543 | 0.53024 | 0.23097 | 0.0083567 | -0.27862 | -0.81829 | -1.6243 | -2.8488 | -2.9113 | -2.455
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Steady Progression | Thermal headroom (MW) | 4.4201 | 4.4494 | 4.5425 | 4.4728 | 4.3902 | 4.2943 | 4.239 | 4.1668 | 4.0715 | 3.9425 | 3.8264 | 3.6584 | 3.4621 | 3.2275 | 2.9804 | 2.3627 | 1.0744 | -0.13586 | -0.40666
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | System Transformation | Thermal headroom (MW) | 4.3912 | 4.3977 | 4.4576 | 4.3391 | 4.1927 | 4.0085 | 3.8906 | 3.7551 | 3.5728 | 3.3586 | 3.1372 | 2.4827 | 2.1622 | 1.8138 | 1.4607 | 1.1236 | -0.47373 | -1.1326 | -1.2924
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | WPD Best View | Thermal headroom (MW) | 4.3712 | 4.2172 | 4.0852 | 3.7842 | 3.4495 | 3.0497 | 2.6282 | 2.2244 | 1.7931 | 1.0119 | 0.61074 | 0.17002 | -0.21091 | -0.52579 | -0.88202 | -1.4846 | -3.9466 | -4.9285 | -4.7854
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Consumer Transformation | Thermal headroom (MW) | 7.6794 | 7.2125 | 6.9088 | 6.4488 | 6.0649 | 5.6048 | 5.0383 | 4.4781 | 3.88 | 2.9188 | 2.2848 | 1.626 | 1.0407 | 0.52545 | 0.12323 | -0.23405 | -2.9532 | -3.9956 | -3.9204
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Leading the Way | Thermal headroom (MW) | 7.6631 | 7.044 | 6.6638 | 6.4241 | 6.057 | 5.5887 | 5.0031 | 4.4681 | 3.4995 | 2.8594 | 2.1722 | 1.5747 | 1.0779 | 0.72608 | 0.23014 | -0.75852 | -2.5163 | -2.4143 | -1.9328
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Steady Progression | Thermal headroom (MW) | 8.1576 | 7.5915 | 7.6145 | 7.5196 | 7.3023 | 7.1955 | 7.0597 | 6.9019 | 6.7051 | 6.4809 | 6.1929 | 5.8491 | 5.4665 | 5.0451 | 4.6048 | 3.7617 | 0.92937 | -1.2047 | -1.9164
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | System Transformation | Thermal headroom (MW) | 7.701 | 7.4465 | 7.3479 | 7.0953 | 7.0409 | 6.8634 | 6.5988 | 6.3028 | 5.9506 | 5.5531 | 5.1224 | 4.218 | 3.6367 | 3.0066 | 2.3141 | 1.6219 | -1.263 | -2.3194 | -2.6623
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | WPD Best View | Thermal headroom (MW) | 8.1299 | 7.3765 | 7.2781 | 7.0834 | 6.6606 | 6.3697 | 6.001 | 5.6209 | 5.2068 | 4.7806 | 4.3357 | 3.8074 | 3.2797 | 2.7836 | 2.3386 | 1.5466 | -0.34697 | -2.1026 | -2.499
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Consumer Transformation | Thermal headroom (MW) | 4.4329 | 4.1911 | 3.945 | 3.6557 | 3.3272 | 2.9549 | 2.4915 | 2.0224 | 1.5092 | 0.63023 | 0.12142 | -0.4552 | -0.98046 | -1.4445 | -1.8049 | -2.1142 | -3.7764 | -4.9295 | -4.9378
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Leading the Way | Thermal headroom (MW) | 4.4151 | 4.1918 | 3.972 | 3.674 | 3.3701 | 2.9824 | 2.5035 | 2.0384 | 1.1473 | 0.59846 | 0.024596 | -0.49911 | -0.94915 | -1.2658 | -1.4535 | -1.9025 | -3.3658 | -3.3411 | -2.9037
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Steady Progression | Thermal headroom (MW) | 4.5066 | 4.489 | 4.4951 | 4.4582 | 4.4049 | 4.3292 | 4.2278 | 4.0965 | 3.9413 | 3.7526 | 3.5025 | 3.1992 | 2.866 | 2.4884 | 2.0837 | 1.2895 | -1.391 | -3.5823 | -4.2457
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | System Transformation | Thermal headroom (MW) | 4.473 | 4.414 | 4.3856 | 4.2986 | 4.205 | 4.0737 | 3.8713 | 3.6279 | 3.3343 | 2.9877 | 2.5971 | 1.7671 | 1.2235 | 0.65545 | 0.022442 | -0.63412 | -3.3783 | -4.4699 | -4.8006
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | WPD Best View | Thermal headroom (MW) | 4.443 | 4.2207 | 4.0057 | 3.7517 | 3.4663 | 3.1483 | 2.7467 | 2.3432 | 1.9049 | 1.0893 | 0.63069 | 0.18593 | -0.31491 | -0.78986 | -1.2038 | -1.5884 | -3.4696 | -4.6094 | -4.6652
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Consumer Transformation | Thermal headroom (MW) | 37.2712 | 35.7789 | 35.2646 | 33.8126 | 33.4587 | 30.8499 | 27.8977 | 23.9571 | 19.7622 | 14.537 | 9.8084 | 4.5 | -1.3147 | -6.8997 | -13.1902 | -19.3084 | -36.9291 | -47.4343 | -48.6703
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Leading the Way | Thermal headroom (MW) | 37.2295 | 34.884 | 34.4881 | 33.2501 | 32.9264 | 29.6044 | 25.225 | 19.9555 | 13.5346 | 7.3697 | 0.79326 | -5.5698 | -11.7099 | -18.2468 | -24.4711 | -30.993 | -43.7483 | -44.8716 | -39.2219
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Steady Progression | Thermal headroom (MW) | 37.4077 | 36.9954 | 37.5785 | 36.8361 | 36.6014 | 35.2545 | 34.2093 | 33.078 | 31.014 | 28.8961 | 26.5355 | 23.992 | 21.3241 | 18.4161 | 15.3331 | 11.4603 | 1.0566 | -13.8726 | -22.1469
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | System Transformation | Thermal headroom (MW) | 37.3408 | 36.5779 | 36.5651 | 35.647 | 35.863 | 33.5234 | 31.6037 | 28.8145 | 25.6394 | 22.0765 | 18.3328 | 13.5633 | 9.1699 | 4.6348 | -0.44078 | -5.7238 | -20.2972 | -31.3161 | -32.2645
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | WPD Best View | Thermal headroom (MW) | 37.2712 | 35.7789 | 35.2646 | 33.8126 | 33.4587 | 30.7377 | 27.578 | 23.9571 | 19.7622 | 14.537 | 9.8084 | 4.5 | -1.3147 | -6.8997 | -13.1902 | -19.3084 | -36.9291 | -47.4343 | -48.6703
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Consumer Transformation | Thermal headroom (MW) | 5.6046 | 4.659 | 4.5718 | 4.3768 | 4.1969 | 3.9101 | 3.3276 | 2.8374 | 2.3513 | 1.4899 | 0.97678 | 0.30448 | -0.66571 | -1.5269 | -2.9636 | -4.0205 | -9.2169 | -11.7562 | -12.5238
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Leading the Way | Thermal headroom (MW) | 5.5996 | 4.502 | 4.4671 | 4.2872 | 4.135 | 3.8728 | 3.2776 | 2.8382 | 2.0118 | 1.4867 | 0.96023 | 0.19407 | -0.22773 | -1.4559 | -2.2853 | -3.3756 | -6.3781 | -7.7264 | -6.8087
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Steady Progression | Thermal headroom (MW) | 5.656 | 5.4771 | 5.7325 | 5.82 | 5.9213 | 5.992 | 6.0547 | 6.1139 | 5.7779 | 5.8114 | 5.8082 | 5.7497 | 5.6846 | 5.5531 | 5.3894 | 4.8636 | 3.0607 | 1.4125 | 0.51259
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | System Transformation | Thermal headroom (MW) | 5.6294 | 5.3138 | 5.4916 | 5.5738 | 5.6792 | 5.3359 | 5.3196 | 5.2841 | 5.2424 | 5.1827 | 5.1077 | 4.6056 | 4.3937 | 4.1366 | 3.5088 | 2.8843 | 0.82757 | -1.6791 | -1.9701
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | WPD Best View | Thermal headroom (MW) | 5.6046 | 4.659 | 4.5718 | 4.3768 | 4.1969 | 3.9101 | 3.3276 | 2.8374 | 2.3513 | 1.4899 | 0.97678 | 0.30448 | -0.66571 | -1.5269 | -2.9636 | -4.0205 | -9.2169 | -11.7562 | -12.5238
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Consumer Transformation | Thermal headroom (MW) | 9.3646 | 9.183 | 9.0897 | 8.5451 | 8.3541 | 6.357 | 4.3689 | 1.4795 | -1.6137 | -5.0353 | -8.5871 | -12.4537 | -16.5269 | -20.5046 | -24.6382 | -28.9514 | -39.3077 | -46.1738 | -47.0012
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Leading the Way | Thermal headroom (MW) | 9.3567 | 9.1425 | 8.6752 | 8.5194 | 8.3499 | 5.6822 | 2.5145 | -1.6113 | -6.0415 | -10.8802 | -16.0655 | -20.8622 | -25.684 | -30.3336 | -34.9336 | -39.3326 | -47.8875 | -48.0532 | -44.2262
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Steady Progression | Thermal headroom (MW) | 9.4223 | 9.437 | 9.5677 | 9.6159 | 9.2684 | 7.9764 | 6.9906 | 5.9123 | 4.344 | 2.4235 | 0.34067 | -1.835 | -4.1281 | -6.5468 | -9.0997 | -11.7082 | -19.3001 | -30.317 | -37.0567
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | System Transformation | Thermal headroom (MW) | 9.3883 | 9.3677 | 9.445 | 9.0902 | 9.0997 | 7.2681 | 5.5539 | 3.1689 | 0.44646 | -2.595 | -5.7979 | -9.2663 | -12.9079 | -16.6136 | -20.4882 | -24.5808 | -35.0546 | -42.4346 | -43.1322
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | WPD Best View | Thermal headroom (MW) | 9.3646 | 9.183 | 9.0897 | 8.5451 | 8.3541 | 6.2597 | 4.0915 | 1.4795 | -1.6137 | -5.0353 | -8.5871 | -12.4537 | -16.5269 | -20.5046 | -24.6382 | -28.9514 | -39.3077 | -46.1738 | -47.0012
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Consumer Transformation | Thermal headroom (MW) | 9.7543 | 9.2706 | 8.9572 | 8.336 | 8.347 | 8.277 | 8.1002 | 7.9011 | 7.6807 | 7.1356 | 6.9308 | 6.6439 | 6.3313 | 6.0482 | 5.7081 | 5.4359 | 4.0526 | 3.5503 | 3.8651
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Leading the Way | Thermal headroom (MW) | 9.7277 | 8.5985 | 8.7578 | 7.907 | 7.902 | 7.8694 | 7.6394 | 7.4918 | 6.8896 | 6.738 | 6.5761 | 6.376 | 6.1517 | 5.9795 | 5.745 | 5.2139 | 4.7778 | 4.9239 | 5.3867
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Steady Progression | Thermal headroom (MW) | 9.7808 | 9.5155 | 9.7262 | 8.9169 | 8.9952 | 9.0747 | 9.1125 | 9.1721 | 9.1865 | 9.2506 | 9.2907 | 9.3017 | 9.3281 | 9.3154 | 9.3081 | 8.8971 | 8.7149 | 7.8784 | 8.0853
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | System Transformation | Thermal headroom (MW) | 9.775 | 9.3239 | 9.0951 | 8.5588 | 8.6706 | 8.7164 | 8.7812 | 8.7709 | 8.768 | 8.7601 | 8.7686 | 8.4279 | 8.4053 | 8.3536 | 8.2586 | 8.2021 | 7.4213 | 6.9678 | 7.0524
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | WPD Best View | Thermal headroom (MW) | 9.7543 | 9.2706 | 8.9572 | 8.336 | 8.347 | 8.277 | 8.1002 | 7.9011 | 7.6807 | 7.1356 | 6.9308 | 6.6439 | 6.3313 | 6.0482 | 5.7081 | 5.4359 | 4.0526 | 3.5503 | 3.8651
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Consumer Transformation | Thermal headroom (MW) | 45.3302 | 43.8669 | 42.9534 | 41.7711 | 40.0257 | 38.3369 | 35.7117 | 33.405 | 31.1858 | 28.5086 | 26.1906 | 23.1525 | 20.4167 | 17.463 | 13.5745 | 9.5577 | -11.6661 | -17.6353 | -17.5169
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Leading the Way | Thermal headroom (MW) | 45.1475 | 43.2531 | 42.7943 | 41.438 | 39.9565 | 38.2788 | 35.6991 | 33.4174 | 30.814 | 28.5428 | 26.1758 | 24.0002 | 21.7341 | 18.646 | 15.2185 | 11.5904 | -2.8814 | -4.465 | 0.55374
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Steady Progression | Thermal headroom (MW) | 45.7696 | 45.8661 | 46.7349 | 46.7637 | 46.8256 | 47.0774 | 47.3462 | 47.437 | 47.5107 | 47.4397 | 47.2238 | 46.2644 | 45.4624 | 44.5225 | 43.5391 | 41.9333 | 31.4112 | 22.5324 | 18.7856
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | System Transformation | Thermal headroom (MW) | 45.4834 | 45.2376 | 45.5878 | 45.7131 | 45.4994 | 45.4911 | 45.2441 | 44.8522 | 44.0878 | 43.4339 | 42.5297 | 40.8322 | 39.3404 | 37.4778 | 35.891 | 34.1642 | 20.3265 | 13.732 | 13.7316
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | WPD Best View | Thermal headroom (MW) | 45.2235 | 43.6035 | 42.7958 | 41.3697 | 39.8135 | 38.1363 | 35.5254 | 33.2673 | 31.0843 | 28.357 | 26.0092 | 23.1231 | 20.3501 | 16.9053 | 13.0526 | 9.1765 | -9.5337 | -13.6746 | -11.4903
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Consumer Transformation | Thermal headroom (MW) | 13.0169 | 12.4728 | 12.0434 | 11.4329 | 10.8053 | 9.921 | 8.6363 | 7.3805 | 6.2413 | 5.1139 | 3.9783 | 2.6694 | 1.3956 | -0.14252 | -2.1036 | -4.1009 | -12.695 | -15.9112 | -16.4875
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Leading the Way | Thermal headroom (MW) | 12.9806 | 12.3941 | 12.0381 | 11.4462 | 10.8645 | 9.9559 | 8.6448 | 7.3841 | 6.231 | 5.1005 | 3.9699 | 3.1253 | 1.9803 | 0.26091 | -1.4349 | -3.0187 | -8.581 | -9.7515 | -7.4292
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Steady Progression | Thermal headroom (MW) | 13.1707 | 13.213 | 13.4121 | 13.3964 | 13.3846 | 13.3461 | 13.3137 | 13.2325 | 13.1196 | 12.9233 | 12.6554 | 12.1998 | 11.6673 | 11.1018 | 10.4941 | 9.8237 | 5.3012 | 1.9592 | -0.038591
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | System Transformation | Thermal headroom (MW) | 13.0899 | 13.0371 | 13.1199 | 13.0249 | 12.9214 | 12.7843 | 12.5347 | 12.2425 | 11.8782 | 11.4217 | 10.8784 | 10.1322 | 9.24 | 8.3676 | 7.4818 | 6.6085 | 2.1603 | -1.6523 | -1.9424
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | WPD Best View | Thermal headroom (MW) | 13.0154 | 12.4686 | 12.0413 | 11.4385 | 10.8151 | 9.9268 | 8.6436 | 7.3645 | 6.2376 | 5.0932 | 3.9445 | 2.6705 | 1.4272 | -0.24352 | -2.1807 | -4.1405 | -12.4325 | -15.4128 | -15.6445
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Consumer Transformation | Thermal headroom (MW) | 9.3877 | 9.07 | 8.6936 | 8.3637 | 8.0512 | 7.5015 | 6.5956 | 5.9005 | 5.2365 | 4.1651 | 3.4191 | 2.441 | 1.3895 | 0.48262 | -0.49585 | -1.5742 | -5.735 | -7.4953 | -7.4358
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Leading the Way | Thermal headroom (MW) | 9.356 | 8.8168 | 8.6993 | 8.4176 | 8.1378 | 7.5934 | 6.7227 | 5.9942 | 4.9737 | 4.2914 | 3.5239 | 2.8394 | 2.128 | 1.3971 | 0.69064 | -0.48044 | -2.699 | -3.3131 | -2.5099
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Steady Progression | Thermal headroom (MW) | 9.4814 | 9.5703 | 9.7703 | 9.6611 | 9.7393 | 9.8099 | 9.9024 | 9.9222 | 9.9384 | 9.889 | 9.8052 | 9.5806 | 9.327 | 9.0237 | 8.7133 | 7.9571 | 5.7879 | 3.8874 | 3.3965
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | System Transformation | Thermal headroom (MW) | 9.4252 | 9.4287 | 9.3817 | 9.4392 | 9.4786 | 9.4675 | 9.4297 | 9.3405 | 9.2108 | 9.02 | 8.7376 | 7.9909 | 7.5552 | 7.0974 | 6.648 | 6.1072 | 3.922 | 2.7674 | 2.6721
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | WPD Best View | Thermal headroom (MW) | 9.3877 | 9.0702 | 8.694 | 8.3635 | 8.0508 | 7.5005 | 6.594 | 5.8965 | 5.2296 | 4.1526 | 3.3995 | 2.4138 | 1.3546 | 0.44017 | -0.54362 | -1.6244 | -5.7221 | -7.4035 | -7.2721
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Consumer Transformation | Thermal headroom (MW) | 13.9479 | 13.2557 | 12.7397 | 12.0919 | 10.3714 | 9.5988 | 8.5243 | 7.5235 | 6.4335 | 5.3266 | 4.2094 | 2.6944 | 1.6408 | 0.2348 | -1.9169 | -3.8402 | -23.1825 | -25.7498 | -25.566
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Leading the Way | Thermal headroom (MW) | 13.8404 | 13.1465 | 12.771 | 11.8373 | 10.3092 | 9.5351 | 8.4833 | 7.5184 | 6.4459 | 5.2432 | 4.0621 | 2.8142 | 1.4769 | -0.16645 | -2.2342 | -3.7834 | -20.1232 | -20.8605 | -18.3922
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Steady Progression | Thermal headroom (MW) | 14.2001 | 14.2965 | 14.6195 | 14.7168 | 14.2981 | 14.3506 | 14.4244 | 14.4197 | 14.3828 | 14.3153 | 14.1416 | 13.3739 | 12.8969 | 12.3894 | 11.8657 | 11.2588 | 0.56755 | -4.0049 | -6.8494
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | System Transformation | Thermal headroom (MW) | 14.0261 | 13.9944 | 14.1685 | 14.1814 | 13.443 | 13.4178 | 13.1962 | 12.9577 | 12.2357 | 11.7846 | 11.2512 | 10.5339 | 9.7351 | 8.5295 | 7.6614 | 6.7645 | -8.497 | -12.518 | -12.7502
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | WPD Best View | Thermal headroom (MW) | 13.8507 | 13.1474 | 12.754 | 11.8148 | 10.2773 | 9.5075 | 8.4741 | 7.5113 | 6.461 | 5.2841 | 4.1555 | 2.8604 | 1.7349 | 0.095771 | -1.9618 | -3.5739 | -20.4396 | -21.6039 | -19.7422
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Consumer Transformation | Thermal headroom (MW) | -6.1197 | -7.2204 | -7.1451 | -7.4218 | -8.08 | -8.4901 | -9.0742 | -9.5104 | -9.9063 | -10.2872 | -10.6829 | -11.3963 | -11.7117 | -12.4331 | -14.3077 | -15.8623 | -21.5493 | -22.3026 | -20.8651
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Leading the Way | Thermal headroom (MW) | -6.2896 | -7.8151 | -7.5889 | -8.2035 | -8.5359 | -8.9111 | -9.4949 | -9.7902 | -10.1172 | -10.4885 | -10.875 | -11.45 | -11.8213 | -13.4778 | -15.3207 | -16.6331 | -19.3229 | -17.6397 | -13.7929
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Steady Progression | Thermal headroom (MW) | -5.8077 | -6.0476 | -5.1878 | -4.9285 | -4.6127 | -4.2449 | -3.9264 | -3.6131 | -3.3278 | -3.0513 | -2.8226 | -3.1278 | -3.0772 | -3.1247 | -3.1634 | -3.2675 | -5.2197 | -12.4677 | -14.8493
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | System Transformation | Thermal headroom (MW) | -6.0358 | -6.6093 | -5.987 | -5.7267 | -5.5108 | -5.3282 | -5.3368 | -5.3035 | -5.6478 | -5.6387 | -5.6702 | -5.8443 | -6.0765 | -6.7765 | -7.0603 | -7.4395 | -13.6871 | -17.6836 | -17.0107
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | WPD Best View | Thermal headroom (MW) | -6.2896 | -7.8151 | -7.5889 | -8.2035 | -8.5359 | -8.9111 | -9.4949 | -9.7902 | -10.1172 | -10.4885 | -10.875 | -11.45 | -11.8213 | -13.4778 | -15.3207 | -16.6331 | -19.3229 | -17.6397 | -13.7929
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Consumer Transformation | Thermal headroom (MW) | 5.2938 | 4.9258 | 4.8722 | 4.4443 | 4.0797 | 3.3836 | 2.1467 | 1.0996 | -0.044018 | -1.901 | -3.2412 | -5.0643 | -6.9124 | -8.8074 | -10.6777 | -12.6431 | -20.2518 | -23.7134 | -24.3449
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Leading the Way | Thermal headroom (MW) | 5.2258 | 4.8714 | 4.8304 | 4.565 | 4.2162 | 3.5398 | 2.3009 | 1.2425 | -0.25854 | -1.998 | -3.4904 | -4.8793 | -6.4089 | -8.1448 | -9.6589 | -11.3867 | -15.9073 | -17.3551 | -14.9129
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Steady Progression | Thermal headroom (MW) | 5.4326 | 5.6052 | 6.1245 | 6.3537 | 6.4699 | 6.6382 | 6.7633 | 6.9111 | 6.994 | 6.8711 | 6.8917 | 6.7456 | 6.5549 | 6.2165 | 5.8839 | 5.1389 | 1.8917 | -2.3635 | -3.2476
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | System Transformation | Thermal headroom (MW) | 5.3365 | 5.4454 | 5.915 | 5.9818 | 6.1893 | 6.2345 | 6.2553 | 6.2448 | 6.1575 | 5.7439 | 5.5158 | 4.7912 | 4.3204 | 3.6031 | 2.8771 | 2.0388 | -2.845 | -5.859 | -5.8227
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | WPD Best View | Thermal headroom (MW) | 5.2258 | 4.8714 | 4.8304 | 4.565 | 4.2162 | 3.5398 | 2.3009 | 1.2425 | -0.25854 | -1.998 | -3.4904 | -4.8793 | -6.4089 | -8.1448 | -9.6589 | -11.3867 | -15.9073 | -17.3551 | -14.9129
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Consumer Transformation | Thermal headroom (MW) | 49.1455 | 47.8011 | 46.8669 | 45.753 | 44.1528 | 42.4129 | 39.2838 | 36.3661 | 33.2768 | 28.9091 | 25.9082 | 21.4563 | 17.4603 | 13.6586 | 9.3608 | 4.6479 | -17.12 | -27.8502 | -29.977
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Leading the Way | Thermal headroom (MW) | 49.0477 | 47.3556 | 46.8189 | 45.4439 | 44.2217 | 42.4221 | 39.2695 | 36.4035 | 31.95 | 28.7938 | 25.6536 | 22.2891 | 19.4372 | 16.0476 | 12.0577 | 6.9173 | -6.4766 | -11.5018 | -7.6223
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Steady Progression | Thermal headroom (MW) | 49.4323 | 49.5584 | 50.4017 | 50.4358 | 50.5981 | 50.6812 | 50.8714 | 50.9922 | 50.9852 | 50.9006 | 50.6283 | 49.3933 | 48.3027 | 46.9869 | 45.6362 | 42.7687 | 34.2674 | 25.9954 | 23.3598
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | System Transformation | Thermal headroom (MW) | 49.2775 | 49.1639 | 49.5669 | 49.7238 | 49.7191 | 49.6423 | 49.4889 | 49.2074 | 48.6255 | 48.0167 | 46.9938 | 44.056 | 42.2493 | 39.8722 | 37.7973 | 35.8225 | 25.5355 | 18.5246 | 17.1615
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | WPD Best View | Thermal headroom (MW) | 49.1015 | 47.5501 | 46.8145 | 45.7602 | 44.2106 | 42.4255 | 39.2796 | 36.4296 | 32.2816 | 28.9112 | 25.8251 | 22.1007 | 18.8589 | 15.4931 | 11.6209 | 6.5391 | -10.0616 | -17.3904 | -15.7374
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Consumer Transformation | Thermal headroom (MW) | 0.10648 | -0.25807 | -0.4698 | -0.81374 | -1.1424 | -1.5489 | -2.2945 | -3.0908 | -3.84 | -4.5637 | -5.2996 | -6.2392 | -7.0977 | -7.9025 | -8.5715 | -9.6898 | -15.0813 | -17.5876 | -18.2136
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Leading the Way | Thermal headroom (MW) | 0.054504 | -0.31248 | -0.50603 | -0.84523 | -1.156 | -1.554 | -2.285 | -3.0805 | -3.8205 | -4.5625 | -5.3047 | -5.9106 | -6.4317 | -6.8493 | -7.5616 | -8.5294 | -12.1449 | -13.5558 | -12.1656
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Steady Progression | Thermal headroom (MW) | 0.2042 | 0.24943 | 0.47553 | 0.53879 | 0.61798 | 0.68945 | 0.75584 | 0.741 | 0.78034 | 0.78606 | 0.76634 | 0.62182 | 0.42657 | 0.19359 | -0.067739 | -0.36906 | -2.2007 | -3.659 | -4.193
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | System Transformation | Thermal headroom (MW) | 0.13793 | 0.1235 | 0.27928 | 0.28361 | 0.31732 | 0.34021 | 0.34837 | 0.19425 | 0.13495 | 0.038718 | -0.18055 | -0.47716 | -0.85109 | -1.2616 | -1.7111 | -2.1457 | -3.7305 | -4.6905 | -4.4853
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | WPD Best View | Thermal headroom (MW) | 0.096547 | -0.26366 | -0.47702 | -0.82937 | -1.1702 | -1.5762 | -2.3281 | -3.135 | -3.8995 | -4.6459 | -5.4127 | -6.3436 | -7.1847 | -7.9665 | -8.6772 | -9.9911 | -14.9503 | -17.0829 | -17.1322
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Consumer Transformation | Thermal headroom (MW) | 7.7665 | 7.5993 | 7.3412 | 7.1927 | 7.0009 | 6.8007 | 6.2399 | 5.7612 | 5.216 | 4.2676 | 3.7468 | 2.8757 | 2.0083 | 1.2122 | 0.34251 | -0.51863 | -4.1192 | -5.6965 | -5.7338
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Leading the Way | Thermal headroom (MW) | 7.7506 | 7.4389 | 7.3552 | 7.2122 | 7.0668 | 6.8657 | 6.2744 | 5.8215 | 4.925 | 4.3157 | 3.7253 | 3.036 | 2.4053 | 1.6935 | 0.9493 | -0.00067194 | -1.9736 | -2.5026 | -1.7203
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Steady Progression | Thermal headroom (MW) | 7.7974 | 7.9076 | 8.1387 | 8.082 | 8.1522 | 8.2597 | 8.3685 | 8.4738 | 8.5193 | 8.5888 | 8.5533 | 8.3685 | 8.1697 | 7.9252 | 7.6569 | 7.0042 | 5.4214 | 4.1109 | 3.8805
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | System Transformation | Thermal headroom (MW) | 7.7769 | 7.8638 | 7.8963 | 7.986 | 8.0312 | 8.1255 | 8.1617 | 8.2012 | 8.2505 | 8.143 | 7.9156 | 7.26 | 6.9198 | 6.5347 | 6.1117 | 5.7377 | 3.9473 | 3.1328 | 3.0162
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | WPD Best View | Thermal headroom (MW) | 7.7504 | 7.4381 | 7.3492 | 7.2102 | 7.0613 | 6.8618 | 6.2891 | 5.8362 | 4.9603 | 4.3632 | 3.7964 | 3.1453 | 2.497 | 1.8134 | 1.1163 | 0.14672 | -2.0507 | -2.7624 | -2.2115
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Consumer Transformation | Thermal headroom (MW) | 11.7426 | 10.9947 | 10.6162 | 10.2425 | 9.618 | 8.6096 | 7.4423 | 6.3908 | 5.2324 | 3.8416 | 2.853 | 1.3489 | -0.012685 | -1.4091 | -3.2225 | -5.2934 | -12.9512 | -16.7569 | -17.5736
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Leading the Way | Thermal headroom (MW) | 11.6755 | 10.5473 | 10.4013 | 10.0162 | 9.3042 | 8.2295 | 7.0342 | 6.0531 | 4.5362 | 3.4758 | 2.524 | 1.4113 | 0.39597 | -1.5772 | -3.444 | -5.5589 | -10.2113 | -11.3826 | -9.6534
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Steady Progression | Thermal headroom (MW) | 11.8444 | 11.5917 | 11.8436 | 11.6757 | 11.509 | 11.3054 | 11.2215 | 11.1639 | 11.0265 | 10.8975 | 10.6778 | 10.1715 | 9.5872 | 8.8716 | 8.2254 | 7.1587 | 3.825 | 0.91702 | -0.0055782
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | System Transformation | Thermal headroom (MW) | 11.7798 | 11.3694 | 11.3442 | 11.3287 | 11.088 | 10.7093 | 10.5151 | 10.3576 | 10.0937 | 9.7804 | 9.3395 | 8.1502 | 7.2464 | 6.1153 | 5.1982 | 4.2776 | 0.75151 | -1.8085 | -2.0252
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | WPD Best View | Thermal headroom (MW) | 11.6956 | 10.7991 | 10.4635 | 10.1066 | 9.4141 | 8.3598 | 7.185 | 6.2094 | 4.7053 | 3.6454 | 2.6695 | 1.5825 | 0.59854 | -0.72127 | -2.3642 | -4.2921 | -9.5779 | -11.7802 | -10.4078
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Consumer Transformation | Thermal headroom (MW) | 2.3714 | 2.0623 | 1.8719 | 1.5555 | 0.85214 | 0.43564 | -0.47785 | -1.3631 | -2.2848 | -3.4765 | -4.2654 | -5.6503 | -6.5847 | -7.4297 | -8.493 | -9.5432 | -16.4268 | -20.0368 | -21.0132
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Leading the Way | Thermal headroom (MW) | 2.3541 | 2.065 | 1.9431 | 1.3096 | 1.0159 | 0.58948 | -0.33812 | -1.1916 | -2.4573 | -3.3215 | -4.1415 | -5.1356 | -5.6804 | -6.1083 | -7.0799 | -8.4068 | -12.7944 | -15.128 | -14.2889
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Steady Progression | Thermal headroom (MW) | 2.4453 | 2.5359 | 2.7744 | 2.8605 | 2.9414 | 2.98 | 3.0123 | 3.0264 | 3.0176 | 2.9558 | 2.8297 | 2.2411 | 1.9951 | 1.7032 | 1.3824 | 0.67122 | -1.8135 | -4.5912 | -5.5658
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | System Transformation | Thermal headroom (MW) | 2.4097 | 2.4557 | 2.6654 | 2.7252 | 2.7581 | 2.7781 | 2.7377 | 2.6784 | 2.1772 | 1.9734 | 1.7013 | 0.99933 | 0.58595 | -0.23091 | -0.71207 | -1.1768 | -4.7482 | -6.9965 | -7.7792
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | WPD Best View | Thermal headroom (MW) | 2.3639 | 2.0734 | 1.9345 | 1.667 | 0.99876 | 0.58606 | -0.33459 | -1.193 | -2.4609 | -3.3115 | -4.1126 | -5.2157 | -5.8793 | -6.4392 | -7.3575 | -8.5843 | -13.8475 | -16.5292 | -16.1553
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Consumer Transformation | Thermal headroom (MW) | 3.619 | 3.2555 | 2.9943 | 2.6209 | 2.2424 | 1.7473 | 0.78316 | -0.073835 | -0.99992 | -2.6836 | -3.7926 | -5.2117 | -6.6858 | -8.1006 | -9.6493 | -11.1914 | -17.854 | -21.2315 | -21.7815
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Leading the Way | Thermal headroom (MW) | 3.6213 | 3.2316 | 3.0316 | 2.649 | 2.3307 | 1.8126 | 0.87415 | -0.029181 | -1.6972 | -2.7737 | -3.9738 | -5.1684 | -6.3747 | -7.6811 | -8.9954 | -10.7912 | -14.7971 | -16.2015 | -15.3856
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Steady Progression | Thermal headroom (MW) | 3.7191 | 3.8141 | 4.0209 | 4.1075 | 4.2109 | 4.2504 | 4.3473 | 4.4262 | 4.4448 | 4.4149 | 4.4127 | 4.1352 | 3.8052 | 3.4127 | 3.0037 | 1.8283 | -0.7653 | -3.6775 | -4.6619
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | System Transformation | Thermal headroom (MW) | 3.6828 | 3.7086 | 3.8605 | 3.9092 | 3.9683 | 4.0055 | 3.9482 | 3.8506 | 3.8115 | 3.6713 | 3.3995 | 2.2141 | 1.6797 | 1.0777 | 0.43394 | -0.16244 | -3.7446 | -6.7938 | -7.6039
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | WPD Best View | Thermal headroom (MW) | 3.6304 | 3.2469 | 2.9726 | 2.6092 | 2.2721 | 1.7483 | 0.79354 | -0.079423 | -1.3713 | -2.7417 | -3.8804 | -5.2133 | -6.534 | -7.8832 | -9.3171 | -10.973 | -16.3398 | -18.765 | -18.605
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Consumer Transformation | Thermal headroom (MW) | 50.0348 | 47.5019 | 45.0566 | 42.5905 | 38.7184 | 35.382 | 31.3989 | 27.828 | 24.0018 | 19.092 | 15.5525 | 10.4516 | 6.68 | 3.1069 | -2.2061 | -6.3411 | -30.0313 | -35.6543 | -33.1856
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Leading the Way | Thermal headroom (MW) | 49.855 | 46.8739 | 44.4843 | 40.5838 | 38.0341 | 34.7245 | 30.6151 | 27.0853 | 22.6281 | 17.7782 | 14.2906 | 9.7186 | 6.6977 | 3.3612 | -1.4946 | -5.7518 | -19.4065 | -19.1357 | -12.8398
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Steady Progression | Thermal headroom (MW) | 50.6416 | 50.3193 | 50.4826 | 50.0808 | 49.7861 | 49.5298 | 49.0477 | 48.5923 | 47.8757 | 46.6469 | 45.6607 | 42.8402 | 41.202 | 39.3142 | 37.2408 | 34.5769 | 18.2847 | 2.5148 | -2.8634
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | System Transformation | Thermal headroom (MW) | 50.2714 | 49.3904 | 48.7531 | 47.9891 | 47.2639 | 46.4786 | 45.0842 | 43.6974 | 40.5999 | 38.0576 | 36.0662 | 33.0757 | 30.2833 | 25.9038 | 22.8074 | 19.736 | -1.6964 | -10.896 | -11.234
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | WPD Best View | Thermal headroom (MW) | 50.5077 | 50.0794 | 50.0117 | 49.5711 | 49.1284 | 48.7378 | 47.9636 | 47.1803 | 45.9168 | 44.331 | 43.0166 | 39.8352 | 37.7481 | 35.2136 | 32.7886 | 30.119 | 13.309 | -0.46058 | -4.2999
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Consumer Transformation | Thermal headroom (MW) | 2.9369 | 2.5648 | 2.2033 | 1.7409 | 1.2891 | 0.64414 | -0.082645 | -0.73669 | -1.3857 | -2.0879 | -2.65 | -3.2023 | -3.6987 | -4.2114 | -5.0915 | -5.8941 | -8.7794 | -9.5706 | -9.301
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Leading the Way | Thermal headroom (MW) | 2.9023 | 2.5187 | 2.2176 | 1.7603 | 1.3411 | 0.68469 | -0.054345 | -0.68034 | -1.3539 | -2.1107 | -2.6413 | -3.0297 | -3.384 | -4.2022 | -4.9925 | -5.6755 | -7.4024 | -7.2744 | -6.2727
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Steady Progression | Thermal headroom (MW) | 3.0531 | 3.064 | 3.1432 | 3.0968 | 3.0628 | 2.9831 | 2.9 | 2.8014 | 2.6627 | 2.4644 | 2.2751 | 2.003 | 1.697 | 1.3621 | 1.0064 | 0.6257 | -1.5131 | -3.5563 | -4.3072
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | System Transformation | Thermal headroom (MW) | 2.9828 | 2.9272 | 2.9217 | 2.7943 | 2.6917 | 2.5198 | 2.2724 | 1.9827 | 1.6776 | 1.2487 | 0.9 | 0.44555 | -0.056382 | -0.58178 | -1.1027 | -1.6117 | -3.6087 | -4.6925 | -4.65
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | WPD Best View | Thermal headroom (MW) | 3.0102 | 2.9875 | 3.011 | 2.9314 | 2.8596 | 2.7395 | 2.5755 | 2.3813 | 2.1704 | 1.8332 | 1.556 | 1.2036 | 0.80247 | 0.37058 | -0.075963 | -0.52751 | -2.6122 | -4.0729 | -4.3419
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Consumer Transformation | Thermal headroom (MW) | 4.1253 | 3.3741 | 2.6812 | 2.3792 | 2.0727 | 1.5892 | 1.0412 | 0.56426 | 0.12575 | -0.30002 | -0.68686 | -1.0281 | -1.3336 | -1.6605 | -2.1315 | -2.5899 | -7.1182 | -7.1387 | -6.5776
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Leading the Way | Thermal headroom (MW) | 4.098 | 3.134 | 2.3269 | 2.0079 | 1.6974 | 1.2156 | 0.64981 | 0.20413 | -0.18824 | -0.58022 | -0.90643 | -1.0925 | -1.296 | -1.6959 | -2.0524 | -2.4173 | -4.7521 | -4.3561 | -3.5771
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Steady Progression | Thermal headroom (MW) | 4.2084 | 3.855 | 3.5908 | 3.5292 | 3.4743 | 3.3836 | 3.3014 | 3.219 | 3.1318 | 3.0238 | 2.8863 | 2.7019 | 2.5109 | 2.2987 | 2.0825 | 1.8539 | -0.68836 | -1.8457 | -2.2224
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | System Transformation | Thermal headroom (MW) | 4.156 | 3.6093 | 3.1424 | 3.0439 | 2.9599 | 2.8053 | 2.5647 | 2.3679 | 2.1663 | 1.9269 | 1.7086 | 1.4208 | 1.1132 | 0.79506 | 0.49337 | 0.19631 | -3.3767 | -3.9852 | -3.6779
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | WPD Best View | Thermal headroom (MW) | 4.2085 | 3.853 | 3.5661 | 3.5019 | 3.4424 | 3.3409 | 3.2477 | 3.1546 | 3.0533 | 2.9479 | 2.8096 | 2.6014 | 2.3837 | 2.1466 | 1.9099 | 1.6657 | -0.76632 | -1.9192 | -2.2551
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Consumer Transformation | Thermal headroom (MW) | 1.1981 | 1.0099 | 0.82273 | 0.59 | -0.041372 | -0.3791 | -0.74497 | -1.1201 | -1.5228 | -1.9425 | -2.3507 | -3.0632 | -3.4656 | -3.8306 | -4.4789 | -4.7316 | -7.006 | -7.8965 | -7.7078
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Leading the Way | Thermal headroom (MW) | 1.1844 | 0.99736 | 0.8307 | 0.2487 | -0.014797 | -0.35535 | -0.72957 | -1.1111 | -1.5454 | -1.9962 | -2.4091 | -3.1677 | -3.5429 | -3.8257 | -4.349 | -4.827 | -6.3329 | -6.4714 | -5.8726
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Steady Progression | Thermal headroom (MW) | 1.2639 | 1.2772 | 1.314 | 1.3 | 1.2593 | 1.2091 | 1.1259 | 1.0382 | 0.91988 | 0.77873 | 0.60602 | 0.019055 | -0.26894 | -0.5628 | -0.90205 | -1.2387 | -3.7283 | -6.1601 | -7.1607
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | System Transformation | Thermal headroom (MW) | 1.2274 | 1.2098 | 1.2024 | 1.1486 | 1.066 | 0.94313 | 0.76917 | 0.57485 | -0.026219 | -0.30489 | -0.6375 | -1.0283 | -1.4704 | -2.2939 | -2.7634 | -3.2498 | -6.3286 | -7.7191 | -8.0135
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | WPD Best View | Thermal headroom (MW) | 1.247 | 1.2493 | 1.2673 | 1.2402 | 1.1851 | 1.1161 | 0.99172 | 0.85994 | 0.69399 | 0.49796 | 0.27087 | -0.37499 | -0.72458 | -1.0752 | -1.4745 | -1.8517 | -4.3118 | -6.3673 | -7.1103
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Consumer Transformation | Thermal headroom (MW) | 9.3439 | 9.1895 | 8.35 | 7.6905 | 7.016 | 6.4863 | 5.5483 | 4.7769 | 3.6236 | 1.8198 | 0.89739 | -0.17477 | -1.2404 | -2.2813 | -3.2963 | -4.2188 | -8.0437 | -8.9101 | -8.2203
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Leading the Way | Thermal headroom (MW) | 9.3242 | 9.0977 | 8.1151 | 7.3178 | 6.4873 | 5.9749 | 4.9923 | 4.1259 | 2.4919 | 0.78992 | -0.17554 | -1.0664 | -1.9668 | -2.7694 | -3.488 | -4.4123 | -6.0924 | -5.6473 | -4.4189
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Steady Progression | Thermal headroom (MW) | 9.4068 | 9.4761 | 9.1977 | 8.8414 | 8.565 | 8.5478 | 8.3519 | 8.2281 | 7.9258 | 7.4037 | 7.2161 | 6.9409 | 6.6545 | 6.3062 | 5.9587 | 5.2133 | 2.6371 | -0.27397 | -0.66868
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | System Transformation | Thermal headroom (MW) | 9.3679 | 9.4058 | 8.8266 | 8.3835 | 7.958 | 7.8855 | 7.5716 | 7.3189 | 6.7246 | 5.8838 | 5.4816 | 4.7401 | 4.2852 | 3.743 | 3.1397 | 2.5498 | -0.85761 | -2.2489 | -2.1103
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | WPD Best View | Thermal headroom (MW) | 9.4068 | 9.4761 | 9.1977 | 8.8414 | 8.565 | 8.5478 | 8.3519 | 8.2281 | 7.9258 | 7.4037 | 7.2161 | 6.9409 | 6.6545 | 6.3062 | 5.9587 | 5.2133 | 2.6371 | -0.27397 | -0.66868
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Consumer Transformation | Thermal headroom (MW) | 9.2507 | 8.9876 | 8.7012 | 8.3402 | 7.5718 | 6.8725 | 5.9798 | 5.182 | 4.4067 | 3.2766 | 2.605 | 1.4737 | 0.78295 | 0.18032 | -0.76649 | -1.747 | -6.3384 | -8.3066 | -8.2328
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Leading the Way | Thermal headroom (MW) | 9.226 | 8.8736 | 8.7379 | 8.0259 | 7.6315 | 6.9242 | 5.9962 | 5.2197 | 4.0623 | 3.2704 | 2.6514 | 1.8355 | 1.4752 | 1.2453 | 0.17577 | -0.94741 | -3.4542 | -4.2746 | -3.5599
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Steady Progression | Thermal headroom (MW) | 9.3271 | 9.3838 | 9.5362 | 9.445 | 9.4006 | 9.3305 | 9.2429 | 9.1379 | 9.0102 | 8.8624 | 8.6815 | 8.0863 | 7.8281 | 7.5243 | 7.2058 | 6.4881 | 4.3313 | 1.9686 | 1.1747
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | System Transformation | Thermal headroom (MW) | 9.2828 | 9.3025 | 9.3157 | 9.2455 | 9.1481 | 8.991 | 8.7744 | 8.557 | 7.9347 | 7.6356 | 7.331 | 6.5898 | 6.1744 | 5.3492 | 4.9092 | 4.4727 | 1.5939 | -0.17194 | -0.67007
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | WPD Best View | Thermal headroom (MW) | 9.3246 | 9.376 | 9.4252 | 9.4293 | 9.3728 | 9.2915 | 9.1838 | 9.0567 | 8.8886 | 8.7118 | 8.5038 | 7.5 | 7.1975 | 6.8349 | 6.4715 | 6.0776 | 3.7374 | 1.4963 | 0.51049
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Consumer Transformation | Thermal headroom (MW) | 7.688 | 6.996 | 6.8684 | 6.6317 | 5.9884 | 5.4673 | 4.7718 | 4.1835 | 3.615 | 2.4914 | 1.8526 | 0.35095 | -0.89764 | -2.1171 | -3.7624 | -5.0254 | -10.3748 | -12.3539 | -12.4681
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Leading the Way | Thermal headroom (MW) | 7.667 | 6.7812 | 6.7048 | 6.1177 | 5.8101 | 5.3169 | 4.5658 | 4.0154 | 3.4726 | 2.1224 | 1.43 | -0.1214 | -1.1821 | -2.2802 | -3.6025 | -4.4973 | -7.5275 | -8.3294 | -6.7282
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Steady Progression | Thermal headroom (MW) | 7.7535 | 7.4531 | 7.6459 | 7.6631 | 7.6552 | 7.6378 | 7.5927 | 7.5529 | 7.5166 | 7.1177 | 7.0052 | 6.4074 | 6.2037 | 5.9313 | 5.6176 | 5.2977 | 3.0562 | -0.85829 | -2.0689
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | System Transformation | Thermal headroom (MW) | 7.7166 | 7.2517 | 7.3727 | 7.3734 | 7.3484 | 7.2351 | 7.0905 | 6.9708 | 6.4723 | 5.7655 | 5.5455 | 5.1615 | 4.7742 | 3.9863 | 3.5139 | 3.0717 | -1.2865 | -3.9369 | -4.0975
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | WPD Best View | Thermal headroom (MW) | 7.7537 | 7.4511 | 7.6437 | 7.6575 | 7.648 | 7.6257 | 7.576 | 7.5306 | 7.4844 | 7.0737 | 6.9489 | 6.3339 | 6.0833 | 5.7793 | 5.445 | 5.1095 | 2.9788 | -0.93074 | -2.1
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Consumer Transformation | Thermal headroom (MW) | -4.4092 | -4.6036 | -4.6889 | -4.9832 | -5.5554 | -5.8046 | -6.0562 | -6.2737 | -6.5365 | -6.8433 | -7.1539 | -7.8195 | -8.1878 | -8.4841 | -9.2069 | -9.5534 | -12.8021 | -13.076 | -12.4723
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Leading the Way | Thermal headroom (MW) | -4.4392 | -4.6246 | -4.6938 | -5.3744 | -5.5503 | -5.7782 | -6.0311 | -6.2628 | -6.5586 | -6.9131 | -7.2622 | -7.9663 | -8.3415 | -8.7448 | -9.4791 | -9.7621 | -12.3498 | -12.0189 | -11.0948
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Steady Progression | Thermal headroom (MW) | -4.3194 | -4.223 | -4.0117 | -4.0144 | -3.937 | -3.8532 | -3.813 | -3.7365 | -3.6918 | -3.6666 | -3.6617 | -4.0728 | -4.114 | -4.2312 | -4.4174 | -4.6189 | -6.9887 | -9.2099 | -10.011
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | System Transformation | Thermal headroom (MW) | -4.3812 | -4.3384 | -4.1786 | -4.2662 | -4.275 | -4.2303 | -4.3049 | -4.373 | -4.7873 | -4.8984 | -5.0024 | -5.1863 | -5.4053 | -6.0376 | -6.3552 | -6.6602 | -10.6165 | -12.0151 | -11.993
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | WPD Best View | Thermal headroom (MW) | -4.3719 | -4.3192 | -4.15 | -4.1935 | -4.1958 | -4.142 | -4.1989 | -4.2445 | -4.6313 | -4.6997 | -4.7957 | -4.9322 | -5.1276 | -5.7215 | -5.975 | -6.2103 | -9.7365 | -11.3348 | -11.5118
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Consumer Transformation | Thermal headroom (MW) | 26.6295 | 25.1848 | 24.081 | 22.2702 | 20.6985 | 18.5224 | 15.79 | 13.2176 | 10.4608 | 6.4063 | 3.4553 | 0.20604 | -2.8614 | -5.7869 | -8.6051 | -10.9592 | -22.4847 | -27.7078 | -27.0408
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Leading the Way | Thermal headroom (MW) | 26.456 | 24.8681 | 23.8772 | 22.1601 | 20.6651 | 18.4481 | 15.6237 | 13.0662 | 9.1443 | 6.0077 | 2.8281 | 0.10354 | -2.45 | -4.9357 | -7.1246 | -9.994 | -18.0295 | -17.8222 | -13.4867
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Steady Progression | Thermal headroom (MW) | 27.082 | 27.0496 | 27.5623 | 27.3628 | 27.1397 | 26.8573 | 26.4837 | 26.0675 | 25.5078 | 24.7565 | 23.8597 | 22.5788 | 21.1373 | 19.3441 | 17.2724 | 14.1251 | 1.4478 | -9.0773 | -12.2703
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | System Transformation | Thermal headroom (MW) | 26.8097 | 26.4842 | 26.6615 | 26.1206 | 25.8397 | 25.1876 | 24.2324 | 23.2582 | 22.0422 | 20.4483 | 18.737 | 15.517 | 13.0254 | 9.9625 | 6.7039 | 3.6523 | -9.7273 | -15.3 | -15.6065
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | WPD Best View | Thermal headroom (MW) | 26.7008 | 25.4866 | 24.6637 | 23.1562 | 21.8975 | 20.1058 | 17.7081 | 15.4558 | 13.0079 | 10.0818 | 7.4026 | 3.6056 | 0.58235 | -2.5004 | -5.5899 | -8.4232 | -21.9613 | -27.93 | -28.0549
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Consumer Transformation | Thermal headroom (MW) | 8.749 | 8.2589 | 7.7724 | 7.3116 | 6.8559 | 6.2933 | 5.4211 | 4.6521 | 3.8023 | 2.8833 | 1.9374 | 0.75258 | -0.46032 | -1.6764 | -2.9311 | -4.0525 | -7.9941 | -9.2138 | -8.8631
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Leading the Way | Thermal headroom (MW) | 8.6872 | 8.13 | 7.8098 | 7.4066 | 7.0011 | 6.5011 | 5.6242 | 4.8448 | 3.9961 | 3.0391 | 2.0319 | 1.0557 | 0.026149 | -1.0987 | -2.2266 | -3.0665 | -5.4022 | -5.5199 | -3.924
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Steady Progression | Thermal headroom (MW) | 8.8689 | 8.9057 | 9.059 | 9.0247 | 9.0569 | 9.1202 | 9.1073 | 9.0816 | 9.053 | 8.9885 | 8.938 | 8.7347 | 8.4875 | 8.2018 | 7.8338 | 7.466 | 4.7615 | 1.8044 | 0.90043
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | System Transformation | Thermal headroom (MW) | 8.7815 | 8.7411 | 8.7089 | 8.7132 | 8.7102 | 8.654 | 8.4922 | 8.3297 | 8.1469 | 7.8867 | 7.6043 | 7.2206 | 6.7855 | 6.1742 | 5.4782 | 4.8458 | 1.379 | -0.48855 | -0.2678
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | WPD Best View | Thermal headroom (MW) | 8.749 | 8.2589 | 7.7724 | 7.3116 | 6.8559 | 6.2933 | 5.4211 | 4.6521 | 3.8023 | 2.8833 | 1.9374 | 0.75258 | -0.46032 | -1.6764 | -2.9311 | -4.0525 | -7.9941 | -9.2138 | -8.8631
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Consumer Transformation | Thermal headroom (MW) | 1.603 | 1.3481 | 1.0921 | 0.72149 | 0.3873 | -0.0022007 | -0.45523 | -0.91417 | -1.4073 | -2.2737 | -2.8024 | -3.3502 | -3.8423 | -4.2694 | -4.6095 | -4.8901 | -6.3398 | -7.4197 | -7.435
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Leading the Way | Thermal headroom (MW) | 1.5956 | 1.3402 | 1.0489 | 0.73657 | 0.42019 | 0.011361 | -0.44439 | -0.8997 | -1.7772 | -2.3126 | -2.9058 | -3.4275 | -3.8866 | -4.1835 | -4.3495 | -4.808 | -6.113 | -6.0493 | -5.7023
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Steady Progression | Thermal headroom (MW) | 1.6792 | 1.6578 | 1.6598 | 1.6132 | 1.4893 | 1.4065 | 1.2976 | 1.1667 | 1.0077 | 0.8127 | 0.57099 | 0.2674 | -0.0738 | -0.46311 | -0.88203 | -1.6703 | -4.4137 | -6.7157 | -7.4633
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | System Transformation | Thermal headroom (MW) | 1.6458 | 1.5753 | 1.534 | 1.378 | 1.2677 | 1.1314 | 0.91882 | 0.66382 | 0.35958 | 0.0078321 | -0.39388 | -1.2357 | -1.785 | -2.3867 | -3.0401 | -3.71 | -6.4671 | -7.6067 | -7.9774
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | WPD Best View | Thermal headroom (MW) | 1.6314 | 1.4736 | 1.3323 | 1.0872 | 0.8798 | 0.64713 | 0.32708 | -0.0061218 | -0.3789 | -0.76731 | -1.1869 | -1.9756 | -2.4557 | -2.9692 | -3.452 | -3.9239 | -6.2348 | -7.5888 | -7.967
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Consumer Transformation | Thermal headroom (MW) | 12.9432 | 12.7498 | 12.8623 | 12.8955 | 12.9191 | 12.6802 | 12.4842 | 12.4086 | 12.3216 | 12.207 | 12.0656 | 11.8643 | 11.6301 | 11.3728 | 11.101 | 10.8287 | 9.6433 | 9.3219 | 9.3949
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Leading the Way | Thermal headroom (MW) | 12.865 | 12.5996 | 12.712 | 12.7531 | 12.7645 | 12.4666 | 12.2034 | 12.122 | 12.0353 | 11.9192 | 11.7252 | 11.5598 | 11.3154 | 11.0537 | 10.7936 | 10.5708 | 9.7439 | 9.7642 | 10.5124
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Steady Progression | Thermal headroom (MW) | 13.012 | 12.932 | 13.0952 | 13.1751 | 13.223 | 13.117 | 13.0853 | 13.1126 | 13.124 | 13.1504 | 13.1526 | 13.147 | 13.1519 | 13.1042 | 12.9607 | 12.8095 | 11.9247 | 11.3186 | 11.2569
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | System Transformation | Thermal headroom (MW) | 12.9499 | 12.8039 | 12.9576 | 13.0452 | 13.1075 | 12.9311 | 12.821 | 12.8605 | 12.8805 | 12.857 | 12.8331 | 12.7819 | 12.667 | 12.4565 | 12.2447 | 12.0391 | 11.1393 | 10.634 | 10.7887
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | WPD Best View | Thermal headroom (MW) | 12.9445 | 12.7521 | 12.8677 | 12.9038 | 12.9318 | 12.6981 | 12.5093 | 12.4425 | 12.3664 | 12.264 | 12.1367 | 11.9516 | 11.7543 | 11.5745 | 11.345 | 11.0865 | 9.8182 | 9.4086 | 9.5058
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Consumer Transformation | Thermal headroom (MW) | 2.9182 | -0.2963 | -2.6241 | -5.847 | -9.1314 | -13.3043 | -18.5779 | -24.2721 | -30.6418 | -36.877 | -43.0859 | -48.93 | -55.6653 | -62.0118 | -69.9602 | -75.9729 | -101.4051 | -111.287 | -110.788
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Leading the Way | Thermal headroom (MW) | 2.5081 | -0.93701 | -3.0863 | -5.9943 | -9.3079 | -13.4892 | -19.5685 | -24.4904 | -32.2189 | -38.7896 | -44.3704 | -50.5971 | -55.577 | -62.4863 | -69.1846 | -73.9584 | -91.8975 | -92.3776 | -83.5498
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Steady Progression | Thermal headroom (MW) | 3.906 | 3.8542 | 4.7646 | 4.6391 | 4.1854 | 3.9565 | 3.4699 | 2.7874 | 1.04 | -0.10477 | -1.4758 | -3.6853 | -6.1962 | -10.1374 | -13.7188 | -17.7573 | -41.6429 | -63.8277 | -72.3287
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | System Transformation | Thermal headroom (MW) | 3.2257 | 2.5938 | 2.7526 | 2.0555 | 1.27 | 0.022021 | -1.6652 | -3.5114 | -6.8734 | -9.5057 | -13.2386 | -17.892 | -22.8742 | -28.0709 | -34.9999 | -40.9703 | -68.6052 | -82.7283 | -83.5388
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | WPD Best View | Thermal headroom (MW) | 3.1698 | 2.414 | 2.3622 | 1.4937 | 0.47731 | -1.0155 | -2.9831 | -5.0906 | -8.6415 | -11.3979 | -15.1224 | -19.5652 | -24.1219 | -28.8676 | -35.3533 | -40.7582 | -66.6484 | -81.4946 | -82.7832
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Consumer Transformation | Thermal headroom (MW) | -1.3499 | -1.7265 | -2.1517 | -2.5032 | -2.8739 | -3.359 | -3.9581 | -4.5355 | -5.1193 | -5.7163 | -6.2715 | -6.8162 | -7.2884 | -7.8547 | -8.3544 | -8.6767 | -10.9312 | -11.7081 | -11.5717
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Leading the Way | Thermal headroom (MW) | -1.41 | -1.851 | -2.2264 | -2.5778 | -2.9352 | -3.4074 | -3.9865 | -4.5437 | -5.1175 | -5.7071 | -6.2362 | -6.6469 | -7.0704 | -7.4863 | -7.8012 | -8.1448 | -9.9073 | -9.8353 | -9.0895
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Steady Progression | Thermal headroom (MW) | -1.234 | -1.3232 | -1.3631 | -1.459 | -1.5266 | -1.6057 | -1.7121 | -1.8477 | -1.9888 | -2.1702 | -2.3939 | -2.6772 | -3.0032 | -3.3976 | -3.8401 | -4.2453 | -6.6946 | -8.4588 | -9.1665
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | System Transformation | Thermal headroom (MW) | -1.3093 | -1.4644 | -1.6285 | -1.7348 | -1.8524 | -1.993 | -2.216 | -2.4828 | -2.7764 | -3.118 | -3.4991 | -3.9706 | -4.4788 | -5.0671 | -5.6989 | -6.2074 | -8.5363 | -9.3028 | -9.2031
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | WPD Best View | Thermal headroom (MW) | -1.3278 | -1.5427 | -1.7879 | -1.9715 | -2.1806 | -2.4319 | -2.7728 | -3.1516 | -3.5401 | -3.9682 | -4.3867 | -4.8459 | -5.2848 | -5.7609 | -6.3013 | -6.7146 | -8.4333 | -9.0963 | -8.9843
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Consumer Transformation | Thermal headroom (MW) | 1.9121 | 1.4347 | 1.0738 | 0.49287 | 0.041273 | -0.74435 | -1.722 | -2.9454 | -3.869 | -4.8693 | -6.2793 | -7.4354 | -9.0199 | -10.4811 | -12.3859 | -13.8203 | -18.4213 | -19.9124 | -19.7839
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Leading the Way | Thermal headroom (MW) | 1.7961 | 1.3235 | 0.93778 | 0.49208 | 0.019537 | -0.77157 | -2.0853 | -2.9692 | -3.9078 | -5.2626 | -6.2997 | -7.6551 | -8.6438 | -10.4803 | -12.4042 | -13.2394 | -15.8195 | -16.0754 | -14.4274
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Steady Progression | Thermal headroom (MW) | 2.105 | 2.1424 | 2.31 | 2.3415 | 2.3087 | 2.3057 | 2.2861 | 2.2126 | 2.1902 | 2.1003 | 2.0081 | 1.8039 | 1.5042 | 0.6651 | 0.11113 | -0.27111 | -4.0778 | -8.2058 | -9.6236
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | System Transformation | Thermal headroom (MW) | 1.9325 | 1.8785 | 1.9354 | 1.848 | 1.8052 | 1.6834 | 1.4786 | 1.2293 | 0.99898 | 0.71745 | 0.023654 | -0.44722 | -1.2942 | -2.179 | -3.5506 | -4.5922 | -9.7331 | -12.6359 | -12.9205
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | WPD Best View | Thermal headroom (MW) | 1.9324 | 1.8791 | 1.936 | 1.8495 | 1.8072 | 1.6868 | 1.4834 | 1.2358 | 1.0087 | 0.7313 | 0.042495 | -0.42102 | -1.2585 | -2.1318 | -3.4897 | -4.5143 | -9.5926 | -12.5634 | -12.8895
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Consumer Transformation | Thermal headroom (MW) | 3.8279 | 3.5118 | 3.2785 | 2.7399 | 2.3797 | 1.9946 | 1.4518 | 0.59564 | -0.013415 | -0.55637 | -1.4292 | -2.1124 | -3.1169 | -3.581 | -4.9404 | -6.2466 | -11.8506 | -14.1804 | -14.8088
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Leading the Way | Thermal headroom (MW) | 3.7919 | 3.4622 | 3.1643 | 2.8051 | 2.4778 | 2.1039 | 1.1966 | 0.72537 | 0.085637 | -0.85891 | -1.3685 | -2.3799 | -3.0407 | -4.3197 | -5.751 | -6.5217 | -10.6657 | -11.4661 | -10.0674
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Steady Progression | Thermal headroom (MW) | 3.9551 | 4.0452 | 4.2777 | 4.3162 | 4.2411 | 4.2978 | 4.322 | 4.3156 | 4.2467 | 4.2 | 4.1099 | 3.8168 | 3.4809 | 2.8528 | 2.5415 | 2.2188 | -1.3483 | -4.6154 | -6.4936
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | System Transformation | Thermal headroom (MW) | 3.8689 | 3.8912 | 4.0275 | 3.86 | 3.8757 | 3.851 | 3.7132 | 3.5609 | 3.275 | 3.0169 | 2.3865 | 1.8358 | 0.86653 | 0.39126 | -0.48419 | -1.3058 | -5.9566 | -9.4734 | -10.2885
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | WPD Best View | Thermal headroom (MW) | 3.8687 | 3.8952 | 4.032 | 3.8711 | 3.8953 | 3.8838 | 3.7583 | 3.6213 | 3.3623 | 3.1364 | 2.5398 | 2.0368 | 1.1208 | 0.69538 | -0.13907 | -0.92944 | -5.6747 | -9.3275 | -10.2248
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Consumer Transformation | Thermal headroom (MW) | 9.4392 | 9.0457 | 8.8917 | 8.4844 | 8.0666 | 7.5436 | 6.9914 | 6.5681 | 4.9757 | 4.0888 | 3.6109 | 3.1013 | 2.5516 | 1.6621 | 0.39641 | -0.76149 | -4.0996 | -5.2805 | -4.8164
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Leading the Way | Thermal headroom (MW) | 9.4058 | 8.9069 | 8.8178 | 8.3442 | 7.871 | 7.3035 | 6.7117 | 6.3233 | 3.9123 | 3.2765 | 2.7801 | 2.4042 | 1.7755 | 1.1791 | 0.0071233 | -1.3741 | -3.0324 | -2.7643 | -1.8115
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Steady Progression | Thermal headroom (MW) | 9.5189 | 9.4433 | 9.6107 | 9.4891 | 9.3891 | 9.279 | 9.2405 | 9.2348 | 8.5146 | 8.4022 | 8.2806 | 8.1022 | 7.904 | 7.6695 | 7.2891 | 6.5426 | 5.3158 | 3.1067 | 2.2809
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | System Transformation | Thermal headroom (MW) | 9.4664 | 9.2935 | 9.3716 | 9.1896 | 8.9953 | 8.7705 | 8.6045 | 8.5218 | 7.2468 | 7.0035 | 6.7698 | 6.1527 | 5.8165 | 5.3997 | 4.7929 | 4.2537 | 2.0845 | 0.51353 | 0.53271
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | WPD Best View | Thermal headroom (MW) | 9.4664 | 9.2935 | 9.3716 | 9.1896 | 8.9953 | 8.7705 | 8.6045 | 8.5218 | 7.2468 | 7.0035 | 6.7698 | 6.1527 | 5.8165 | 5.3997 | 4.7929 | 4.2537 | 2.0845 | 0.51353 | 0.53271
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Consumer Transformation | Thermal headroom (MW) | 3.3998 | 3.0758 | 2.9337 | 2.6198 | 2.303 | 1.6697 | 0.62554 | -0.35616 | -1.6381 | -3.4012 | -4.9765 | -6.9093 | -8.5535 | -10.6905 | -12.8723 | -14.3615 | -20.0816 | -21.8497 | -21.0389
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Leading the Way | Thermal headroom (MW) | 3.3633 | 3.0499 | 2.9214 | 2.6626 | 2.3754 | 1.7632 | 0.73483 | -0.22907 | -1.9789 | -3.5148 | -5.2969 | -7.0421 | -8.4211 | -10.512 | -12.5647 | -13.9744 | -16.7225 | -16.4609 | -14.3876
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Steady Progression | Thermal headroom (MW) | 3.4749 | 3.594 | 3.947 | 4.0646 | 4.1914 | 4.3098 | 4.3454 | 4.3996 | 4.3238 | 4.1227 | 3.8512 | 3.4701 | 3.2131 | 2.5543 | 1.8834 | 1.0553 | -2.0716 | -5.6207 | -6.3574
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | System Transformation | Thermal headroom (MW) | 3.4288 | 3.501 | 3.7608 | 3.8621 | 3.9548 | 3.9522 | 3.8724 | 3.8347 | 3.534 | 3.0941 | 2.4666 | 1.4012 | 0.91165 | -0.24387 | -1.496 | -2.2721 | -6.8393 | -9.0634 | -8.6101
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | WPD Best View | Thermal headroom (MW) | 3.4275 | 3.4987 | 3.7554 | 3.8538 | 3.9422 | 3.9342 | 3.8473 | 3.8008 | 3.4892 | 3.0371 | 2.3955 | 1.3139 | 0.80828 | -0.36241 | -1.6261 | -2.4128 | -6.9523 | -9.1506 | -8.7218
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Consumer Transformation | Thermal headroom (MW) | 8.6441 | 8.2007 | 8.3216 | 8.3385 | 8.0838 | 8.028 | 7.7615 | 7.4678 | 7.139 | 6.6144 | 6.4602 | 6.2979 | 5.8061 | 5.7187 | 5.3298 | 5.3228 | 3.0436 | 1.715 | 1.1713
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Leading the Way | Thermal headroom (MW) | 8.6306 | 8.141 | 8.264 | 8.2832 | 7.9491 | 7.8928 | 7.562 | 7.1833 | 6.4297 | 6.1935 | 6.043 | 5.586 | 5.5434 | 5.2336 | 5.3635 | 5.1428 | 3.0222 | 2.4528 | 3.0356
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Steady Progression | Thermal headroom (MW) | 8.6803 | 8.7116 | 8.9344 | 9.0391 | 8.9667 | 9.0605 | 9.027 | 8.9672 | 8.5311 | 8.5155 | 8.4985 | 8.4436 | 8.3693 | 8.2831 | 8.1735 | 7.7015 | 5.5239 | 4.1735 | 3.7041
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | System Transformation | Thermal headroom (MW) | 8.6605 | 8.6479 | 8.833 | 8.9294 | 8.791 | 8.5029 | 8.3687 | 8.2154 | 7.9793 | 7.9101 | 7.8139 | 7.3092 | 7.1305 | 6.953 | 6.4066 | 5.8804 | 3.1929 | 1.8711 | 1.6479
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | WPD Best View | Thermal headroom (MW) | 8.6603 | 8.6499 | 8.8353 | 8.935 | 8.7982 | 8.5193 | 8.3913 | 8.2456 | 8.0229 | 7.9698 | 7.8906 | 7.4097 | 7.2576 | 7.1051 | 6.5792 | 6.0685 | 3.2709 | 1.8483 | 1.5501
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Consumer Transformation | Thermal headroom (MW) | 2.5105 | 2.323 | 2.13 | 1.9121 | 1.6641 | 1.3904 | 1.0905 | 0.79427 | 0.47673 | 0.15163 | -0.16422 | -0.47259 | -0.7759 | -1.0345 | -1.2376 | -1.4014 | -2.1339 | -2.5382 | -2.4829
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Leading the Way | Thermal headroom (MW) | 2.4992 | 2.318 | 2.1529 | 1.9387 | 1.705 | 1.4305 | 1.1318 | 0.82986 | 0.50257 | 0.1516 | -0.20034 | -0.52388 | -0.79736 | -0.99655 | -1.0902 | -1.1615 | -2.0205 | -1.8902 | -1.4386
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Steady Progression | Thermal headroom (MW) | 2.5792 | 2.5745 | 2.5936 | 2.5802 | 2.5457 | 2.5051 | 2.4436 | 2.3675 | 2.2724 | 2.1567 | 2.0225 | 1.814 | 1.5863 | 1.3398 | 1.0801 | 0.80188 | -0.99166 | -2.5124 | -3.1062
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | System Transformation | Thermal headroom (MW) | 2.5424 | 2.5039 | 2.4886 | 2.4336 | 2.3623 | 2.27 | 2.1179 | 1.9449 | 1.7346 | 1.491 | 1.2357 | 0.9123 | 0.54128 | 0.16723 | -0.23817 | -0.66751 | -2.2711 | -2.8796 | -2.8799
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | WPD Best View | Thermal headroom (MW) | 2.5371 | 2.4945 | 2.4642 | 2.4006 | 2.3123 | 2.2061 | 2.0354 | 1.845 | 1.624 | 1.381 | 1.1362 | 0.84728 | 0.53676 | 0.20816 | -0.14147 | -0.48248 | -1.9125 | -2.6954 | -2.7781
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Consumer Transformation | Thermal headroom (MW) | 18.0383 | 15.4424 | 12.362 | 8.7474 | 4.2613 | -0.14787 | -5.9108 | -11.8865 | -18.3299 | -25.6072 | -32.4456 | -40.5179 | -47.2104 | -53.6731 | -60.2846 | -65.2942 | -89.358 | -100.8356 | -101.2353
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Leading the Way | Thermal headroom (MW) | 17.8835 | 15.1111 | 12.242 | 7.6376 | 4.248 | -0.12459 | -6.0366 | -12.0319 | -19.2219 | -26.6435 | -33.8234 | -41.0029 | -46.8694 | -51.9882 | -56.8434 | -60.3304 | -80.6297 | -82.2212 | -72.2362
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Steady Progression | Thermal headroom (MW) | 18.7908 | 18.4325 | 18.3275 | 17.3926 | 16.6178 | 15.6942 | 14.3765 | 12.7217 | 10.7302 | 8.2511 | 5.2661 | 0.65777 | -3.4324 | -8.2362 | -13.5422 | -19.3079 | -50.8709 | -71.2477 | -79.2111
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | System Transformation | Thermal headroom (MW) | 18.487 | 17.7028 | 16.9237 | 15.4645 | 14.3483 | 12.781 | 10.5008 | 7.6604 | 3.3119 | -0.8714 | -5.6517 | -11.6843 | -18.3582 | -26.579 | -34.2915 | -41.7533 | -72.6468 | -83.1925 | -84.1027
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | WPD Best View | Thermal headroom (MW) | 18.2859 | 16.647 | 14.7287 | 12.2264 | 9.0713 | 6.0589 | 1.8576 | -2.75 | -7.7788 | -13.6778 | -19.7561 | -27.2434 | -33.9341 | -41.0926 | -49.2333 | -56.1272 | -84.9857 | -94.8965 | -94.3597
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Consumer Transformation | Thermal headroom (MW) | 9.7103 | 9.4125 | 9.0893 | 8.4198 | 7.9892 | 7.443 | 6.6952 | 5.9318 | 5.1393 | 4.2422 | 3.4622 | 2.6598 | 1.9329 | 1.1455 | 0.30458 | -0.26864 | -4.5271 | -6.1364 | -6.0369
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Leading the Way | Thermal headroom (MW) | 9.6767 | 9.3487 | 9.085 | 8.305 | 7.8842 | 7.3564 | 6.5913 | 5.8591 | 5.0457 | 4.0983 | 3.3594 | 2.8053 | 2.3619 | 1.6198 | 0.82246 | -0.047971 | -3.0278 | -3.1131 | -1.7667
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Steady Progression | Thermal headroom (MW) | 9.8023 | 9.8088 | 9.8975 | 9.6424 | 9.5901 | 9.5251 | 9.4198 | 9.2797 | 9.0956 | 8.8218 | 8.5541 | 8.2008 | 7.8041 | 7.25 | 6.6493 | 6.1147 | 3.1995 | 1.2268 | 0.46663
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | System Transformation | Thermal headroom (MW) | 9.747 | 9.7031 | 9.7031 | 9.3308 | 9.2151 | 9.0848 | 8.8655 | 8.5968 | 8.2571 | 7.7515 | 7.2874 | 6.7328 | 6.1181 | 5.2512 | 4.3825 | 3.712 | 0.84687 | -0.068215 | 0.17468
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | WPD Best View | Thermal headroom (MW) | 9.7155 | 9.4244 | 9.1167 | 8.4603 | 8.049 | 7.5232 | 6.8003 | 6.0619 | 5.2935 | 4.412 | 3.6383 | 2.8254 | 2.0721 | 1.2387 | 0.41448 | -0.22137 | -4.4072 | -6.0421 | -5.9184
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Consumer Transformation | Thermal headroom (MW) | 6.2283 | 5.3904 | 4.5189 | 3.6745 | 3.0453 | 2.1785 | 0.75406 | -0.71615 | -2.2327 | -3.7765 | -5.3901 | -7.0916 | -8.876 | -11.234 | -13.6015 | -16.062 | -25.0347 | -27.943 | -28.1157
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Leading the Way | Thermal headroom (MW) | 6.1959 | 5.2636 | 4.333 | 3.4091 | 2.8486 | 2.0164 | 0.57314 | -0.89581 | -2.4339 | -3.9975 | -5.6334 | -6.9701 | -9.1234 | -11.2943 | -13.4536 | -15.3371 | -20.9264 | -21.7174 | -19.095
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Steady Progression | Thermal headroom (MW) | 6.366 | 6.1537 | 5.997 | 5.7961 | 5.7688 | 5.6722 | 5.4887 | 5.2122 | 4.833 | 4.3822 | 3.7946 | 3.0712 | 2.2706 | 1.3659 | 0.41853 | -0.62077 | -6.3568 | -9.8607 | -11.2018
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | System Transformation | Thermal headroom (MW) | 6.292 | 5.926 | 5.5742 | 5.2292 | 5.1495 | 4.9603 | 4.5642 | 3.9732 | 3.3056 | 2.5195 | 1.5611 | 0.44808 | -0.76963 | -2.088 | -3.442 | -4.7247 | -10.3718 | -13.4279 | -13.4437
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | WPD Best View | Thermal headroom (MW) | 6.2502 | 5.5239 | 4.7906 | 4.0697 | 3.5973 | 2.9561 | 1.7307 | 0.44652 | -0.91594 | -2.3187 | -3.8468 | -5.5363 | -7.148 | -9.2602 | -11.5541 | -13.8798 | -22.9455 | -26.1773 | -26.3368
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Consumer Transformation | Thermal headroom (MW) | 6.2202 | 5.9326 | 5.5555 | 5.1525 | 4.7009 | 4.1648 | 3.5094 | 2.8196 | 2.034 | 1.1681 | 0.29911 | -0.57905 | -1.3884 | -2.0815 | -2.6274 | -3.0768 | -5.1253 | -6.3392 | -6.4985
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Leading the Way | Thermal headroom (MW) | 6.2118 | 5.9267 | 5.5537 | 5.1735 | 4.7478 | 4.2069 | 3.5236 | 2.8237 | 1.9622 | 1.0231 | 0.11115 | -0.72347 | -1.4013 | -1.8938 | -2.1643 | -2.3352 | -4.6716 | -4.7422 | -3.655
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Steady Progression | Thermal headroom (MW) | 6.3034 | 6.2358 | 6.1567 | 6.0596 | 5.9049 | 5.7446 | 5.5491 | 5.2944 | 5.0169 | 4.6703 | 4.2552 | 3.765 | 3.2238 | 2.5878 | 1.877 | 1.1366 | -2.9616 | -5.3019 | -6.2286
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | System Transformation | Thermal headroom (MW) | 6.2828 | 6.1745 | 6.0417 | 5.8686 | 5.7 | 5.4515 | 5.1452 | 4.7659 | 4.3119 | 3.7727 | 3.1428 | 2.3844 | 1.4833 | 0.51542 | -0.49683 | -1.5047 | -5.1095 | -6.0529 | -6.1303
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | WPD Best View | Thermal headroom (MW) | 6.2619 | 6.1391 | 5.9621 | 5.7465 | 5.5196 | 5.208 | 4.8271 | 4.3669 | 3.8374 | 3.2283 | 2.5089 | 1.7259 | 0.88573 | 0.044923 | -0.77781 | -1.5689 | -4.3247 | -5.1345 | -5.1402
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Consumer Transformation | Thermal headroom (MW) | 0.73846 | 0.64997 | 0.62613 | 0.46863 | 0.25865 | 0.0016244 | -0.35336 | -0.72504 | -1.1147 | -1.8985 | -2.2845 | -2.6761 | -3.0026 | -3.2307 | -3.4677 | -3.6893 | -4.5932 | -4.8817 | -4.454
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Leading the Way | Thermal headroom (MW) | 0.73337 | 0.65296 | 0.66788 | 0.51279 | 0.30951 | 0.059873 | -0.29238 | -0.67286 | -1.442 | -1.9007 | -2.3094 | -2.5946 | -2.8005 | -2.9678 | -3.0756 | -3.4566 | -3.5142 | -3.2337 | -2.4953
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Steady Progression | Thermal headroom (MW) | 0.80238 | 0.90158 | 1.1279 | 1.2156 | 1.2643 | 1.3041 | 1.314 | 1.3023 | 1.2561 | 1.1744 | 1.0528 | 0.85337 | 0.62841 | 0.36234 | 0.076307 | -0.60091 | -2.1858 | -3.4181 | -3.6098
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | System Transformation | Thermal headroom (MW) | 0.76915 | 0.84712 | 1.0439 | 1.0918 | 1.1019 | 1.0923 | 1.0142 | 0.88546 | 0.70617 | 0.48245 | 0.2292 | -0.48453 | -0.90022 | -1.3406 | -1.8005 | -2.2181 | -4.0272 | -4.5119 | -4.4676
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | WPD Best View | Thermal headroom (MW) | 0.73846 | 0.64997 | 0.62613 | 0.46863 | 0.25865 | 0.0016244 | -0.35336 | -0.72504 | -1.1147 | -1.8985 | -2.2845 | -2.6761 | -3.0026 | -3.2307 | -3.4677 | -3.6893 | -4.5932 | -4.8817 | -4.454
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Consumer Transformation | Thermal headroom (MW) | 4.9665 | 4.7745 | 4.5294 | 4.2857 | 3.6357 | 3.277 | 2.8392 | 2.3959 | 1.9484 | 1.4748 | 1.0234 | 0.13343 | -0.34574 | -0.7623 | -1.4423 | -1.7234 | -3.5162 | -4.6011 | -4.6394
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Leading the Way | Thermal headroom (MW) | 4.9425 | 4.7126 | 4.5254 | 3.9194 | 3.6371 | 3.281 | 2.8393 | 2.3945 | 1.9093 | 1.4124 | 0.89074 | 0.049893 | -0.35513 | -0.64544 | -1.1811 | -1.2917 | -2.8822 | -3.2352 | -2.5051
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Steady Progression | Thermal headroom (MW) | 5.0376 | 5.0271 | 5.0453 | 4.9562 | 4.9047 | 4.8308 | 4.7065 | 4.5887 | 4.4313 | 4.2565 | 4.0384 | 3.3935 | 3.081 | 2.7398 | 2.3542 | 1.9614 | -0.80468 | -3.0226 | -3.9775
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | System Transformation | Thermal headroom (MW) | 5.0033 | 4.9586 | 4.8942 | 4.8169 | 4.7045 | 4.5823 | 4.3849 | 4.1717 | 3.5449 | 3.2308 | 2.865 | 2.4354 | 1.9318 | 1.0566 | 0.46946 | -0.13734 | -3.3845 | -4.6919 | -5.0359
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | WPD Best View | Thermal headroom (MW) | 4.9909 | 4.8845 | 4.7399 | 4.602 | 4.0739 | 3.8435 | 3.5268 | 3.2018 | 2.8589 | 2.4816 | 2.0692 | 1.2623 | 0.79341 | 0.28169 | -0.59628 | -1.1004 | -3.6826 | -4.6801 | -4.6019
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Consumer Transformation | Thermal headroom (MW) | 10.9105 | 10.5521 | 10.224 | 9.8452 | 8.6902 | 7.59 | 6.2763 | 4.915 | 2.945 | 0.46294 | -1.4814 | -4.167 | -6.7581 | -9.0222 | -11.7353 | -14.0781 | -24.4024 | -27.3845 | -26.7192
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Leading the Way | Thermal headroom (MW) | 10.8322 | 10.3523 | 10.125 | 9.3607 | 8.4289 | 7.2201 | 5.916 | 4.5017 | 1.5436 | -0.41705 | -2.4497 | -4.8648 | -7.3058 | -9.3565 | -11.712 | -14.2641 | -20.6022 | -20.6599 | -18.2569
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Steady Progression | Thermal headroom (MW) | 11.0365 | 11.1381 | 11.4042 | 11.4083 | 11.1764 | 11.0376 | 11.0597 | 10.9154 | 10.5091 | 10.247 | 9.9442 | 9.1249 | 8.5164 | 7.8323 | 7.1158 | 5.5691 | -0.68103 | -7.4767 | -9.2523
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | System Transformation | Thermal headroom (MW) | 10.947 | 10.9644 | 11.0239 | 11.0302 | 10.6957 | 10.3976 | 10.1362 | 9.8632 | 8.7262 | 8.1832 | 7.5144 | 5.9545 | 4.8087 | 3.2925 | 2.0556 | 0.70568 | -8.7038 | -13.1556 | -13.6694
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | WPD Best View | Thermal headroom (MW) | 10.9663 | 10.999 | 11.1772 | 11.1276 | 10.8118 | 10.5269 | 10.3636 | 10.1217 | 9.1575 | 8.6993 | 8.1348 | 7.3914 | 6.4673 | 5.0792 | 3.9843 | 2.0108 | -6.3298 | -11.468 | -11.6888
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Consumer Transformation | Thermal headroom (MW) | 159.5679 | 156.2807 | 153.6236 | 150.2472 | 146.5992 | 142.5283 | 136.4577 | 130.8271 | 124.9951 | 116.197 | 110.7656 | 104.6797 | 98.9039 | 93.949 | 88.9976 | 84.2016 | 57.0615 | 45.4846 | 46.8051
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Leading the Way | Thermal headroom (MW) | 159.1823 | 155.3421 | 153.1617 | 149.4506 | 145.9283 | 141.8686 | 135.7391 | 130.4302 | 121.4706 | 115.7158 | 110.5979 | 106.0546 | 102.4253 | 98.8804 | 95.4289 | 89.0533 | 72.4542 | 71.1556 | 77.7253
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Steady Progression | Thermal headroom (MW) | 160.4139 | 160.2126 | 160.9988 | 160.2821 | 159.9473 | 159.773 | 159.2556 | 158.596 | 157.4939 | 156.3375 | 154.8257 | 152.4223 | 149.9201 | 147.0746 | 143.9525 | 137.5112 | 118.1581 | 101.3484 | 96.8371
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | System Transformation | Thermal headroom (MW) | 159.8721 | 159.0839 | 158.8897 | 157.8925 | 156.9627 | 156.008 | 154.4712 | 152.7074 | 150.3474 | 147.8146 | 144.8861 | 138.0461 | 133.9448 | 129.3467 | 124.6051 | 119.9863 | 98.9652 | 89.6131 | 88.5898
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | WPD Best View | Thermal headroom (MW) | 160.2233 | 159.7053 | 160.0338 | 159.0999 | 158.3941 | 158.0045 | 157.1026 | 155.9673 | 154.143 | 152.3967 | 150.3953 | 146.1938 | 143.2742 | 139.8757 | 136.4389 | 131.2813 | 111.4294 | 97.6762 | 94.0293
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Consumer Transformation | Thermal headroom (MW) | 7.0346 | 6.4946 | 6.0996 | 5.5341 | 4.7881 | 4.1213 | 3.0322 | 2.0182 | 1.0497 | 0.12076 | -0.6942 | -2.0425 | -2.9449 | -3.7104 | -4.6698 | -5.5602 | -12.5089 | -14.7634 | -15.0353
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Leading the Way | Thermal headroom (MW) | 6.9509 | 6.3353 | 5.994 | 5.0196 | 4.6774 | 4.0192 | 2.9046 | 1.9384 | 0.98956 | 0.095058 | -0.65447 | -1.5549 | -2.0141 | -2.2983 | -3.0961 | -3.9804 | -9.6785 | -10.9604 | -9.5662
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Steady Progression | Thermal headroom (MW) | 7.1433 | 7.0411 | 7.1115 | 6.9623 | 6.975 | 6.9249 | 6.8286 | 6.7452 | 6.6486 | 6.4759 | 6.274 | 5.616 | 5.3085 | 4.9469 | 4.5549 | 4.1446 | 0.96969 | -1.1582 | -1.9598
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | System Transformation | Thermal headroom (MW) | 7.0667 | 6.8765 | 6.8417 | 6.6209 | 6.601 | 6.481 | 6.3177 | 6.1236 | 5.5206 | 5.1954 | 4.8359 | 4.4084 | 3.9239 | 3.0393 | 2.5049 | 2.0212 | -1.9488 | -3.3875 | -3.4809
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | WPD Best View | Thermal headroom (MW) | 7.0864 | 6.9118 | 6.9229 | 6.7129 | 6.7102 | 6.6189 | 6.4949 | 6.3303 | 5.8016 | 5.5432 | 5.2537 | 4.8851 | 4.4696 | 3.6587 | 3.1861 | 2.7298 | -1.3499 | -3.1342 | -3.4627
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Consumer Transformation | Thermal headroom (MW) | 5.0568 | 4.1163 | 4.0649 | 3.8471 | 3.7316 | 3.2821 | 2.2939 | 1.6386 | 1.0441 | 0.11698 | -0.47887 | -1.1821 | -1.8332 | -2.395 | -2.8444 | -3.2583 | -6.4611 | -7.2628 | -6.6959
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Leading the Way | Thermal headroom (MW) | 4.9098 | 3.6547 | 3.6245 | 3.3809 | 3.2499 | 2.7912 | 1.8096 | 1.3103 | 0.42695 | -0.043738 | -0.49406 | -0.91024 | -1.2602 | -1.5341 | -1.6776 | -2.1884 | -4.0498 | -3.7299 | -2.8069
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Steady Progression | Thermal headroom (MW) | 5.1933 | 4.6369 | 4.7901 | 4.7446 | 4.7732 | 4.7481 | 4.6242 | 4.571 | 4.5001 | 4.4053 | 4.2808 | 4.1042 | 3.9291 | 3.6925 | 3.4212 | 2.7315 | 1.082 | 0.0025055 | 0.14741
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | System Transformation | Thermal headroom (MW) | 5.0746 | 4.2759 | 4.3607 | 4.2589 | 4.2835 | 4.2469 | 3.9883 | 3.8123 | 3.6322 | 3.4416 | 3.2171 | 2.5618 | 2.2405 | 1.8783 | 1.5107 | 1.1478 | -0.46417 | -0.73579 | -0.32466
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | WPD Best View | Thermal headroom (MW) | 5.0746 | 4.2759 | 4.3607 | 4.2589 | 4.2835 | 4.2469 | 3.9883 | 3.8123 | 3.6322 | 3.4416 | 3.2171 | 2.5618 | 2.2405 | 1.8783 | 1.5107 | 1.1478 | -0.46417 | -0.73579 | -0.32466
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Consumer Transformation | Thermal headroom (MW) | 5.6517 | 5.4051 | 5.0484 | 4.7508 | 4.4142 | 3.8555 | 2.8561 | 1.9947 | 1.119 | 0.22001 | -0.65801 | -1.6379 | -2.4928 | -3.1999 | -3.8739 | -4.5298 | -7.8739 | -9.4998 | -9.5636
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Leading the Way | Thermal headroom (MW) | 5.6448 | 5.1848 | 5.1003 | 4.8005 | 4.4833 | 3.9229 | 2.8907 | 2.0353 | 1.1102 | 0.17844 | -0.68406 | -1.348 | -1.8532 | -2.3354 | -2.6687 | -2.9304 | -5.4372 | -6.0122 | -4.7638
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Steady Progression | Thermal headroom (MW) | 5.728 | 5.8089 | 6.0346 | 5.8746 | 5.9098 | 5.9168 | 5.8617 | 5.8143 | 5.705 | 5.5042 | 5.2665 | 4.9118 | 4.5203 | 4.0711 | 3.5823 | 3.0665 | 0.39147 | -1.4489 | -1.9493
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | System Transformation | Thermal headroom (MW) | 5.6951 | 5.7406 | 5.6937 | 5.7133 | 5.6965 | 5.6204 | 5.4515 | 5.2624 | 4.941 | 4.5489 | 4.0883 | 3.5436 | 2.9069 | 2.2259 | 1.5316 | 0.87522 | -1.684 | -2.438 | -2.1412
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | WPD Best View | Thermal headroom (MW) | 5.6972 | 5.7205 | 5.6698 | 5.6472 | 5.5965 | 5.4755 | 5.269 | 5.0039 | 4.6878 | 4.3126 | 3.8991 | 3.4454 | 2.966 | 2.5095 | 2.0782 | 1.6711 | -0.63874 | -1.7898 | -1.7431
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Consumer Transformation | Thermal headroom (MW) | 10.6758 | 10.3596 | 10.0406 | 9.625 | 9.2283 | 8.6294 | 7.7978 | 7.0551 | 6.3019 | 5.1949 | 4.482 | 3.714 | 3.0237 | 2.4222 | 1.9189 | 1.4448 | -2.478 | -3.7754 | -3.5169
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Leading the Way | Thermal headroom (MW) | 10.6299 | 10.3139 | 10.0379 | 9.6292 | 9.2426 | 8.6648 | 7.8338 | 7.1169 | 6.0059 | 5.2396 | 4.5701 | 4.0649 | 3.7033 | 3.4121 | 3.1342 | 2.26 | 0.18642 | -0.037251 | 0.656
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Steady Progression | Thermal headroom (MW) | 10.7719 | 10.7913 | 10.8863 | 10.8536 | 10.8486 | 10.7881 | 10.7032 | 10.6105 | 10.4801 | 10.3019 | 10.1042 | 9.84 | 9.5307 | 9.19 | 8.7875 | 8.0131 | 5.7846 | 4.0385 | 3.6346
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | System Transformation | Thermal headroom (MW) | 10.7114 | 10.684 | 10.6994 | 10.6129 | 10.5417 | 10.3944 | 10.1914 | 9.9394 | 9.6735 | 9.3549 | 8.9892 | 8.1949 | 7.698 | 7.1659 | 6.5993 | 6.082 | 3.6445 | 2.7479 | 2.681
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | WPD Best View | Thermal headroom (MW) | 10.7719 | 10.7913 | 10.8863 | 10.8536 | 10.8486 | 10.7881 | 10.7032 | 10.6105 | 10.4801 | 10.3019 | 10.1042 | 9.84 | 9.5307 | 9.19 | 8.7875 | 8.0131 | 5.7846 | 4.0385 | 3.6346
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Consumer Transformation | Thermal headroom (MW) | 6.173 | 5.7984 | 5.538 | 5.1732 | 4.7782 | 4.3252 | 3.7744 | 3.2675 | 2.754 | 1.8758 | 1.3649 | 0.90837 | 0.52617 | 0.21832 | 0.0070633 | -0.62328 | -3.2238 | -3.9547 | -3.3626
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Leading the Way | Thermal headroom (MW) | 6.1307 | 5.7336 | 5.5538 | 5.2271 | 4.861 | 4.4292 | 3.8639 | 3.3914 | 2.5329 | 1.9851 | 1.4882 | 1.1517 | 0.91798 | 0.79666 | 0.15004 | -0.75117 | -1.959 | -1.5226 | -0.75663
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Steady Progression | Thermal headroom (MW) | 6.3129 | 6.3771 | 6.5987 | 6.6538 | 6.7233 | 6.7624 | 6.7765 | 6.774 | 6.7533 | 6.7085 | 6.6159 | 6.4109 | 6.2042 | 5.9684 | 5.7043 | 5.0621 | 3.4349 | 1.664 | 1.07
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | System Transformation | Thermal headroom (MW) | 6.225 | 6.2076 | 6.3206 | 6.3256 | 6.3238 | 6.2696 | 6.0743 | 5.9004 | 5.6629 | 5.4024 | 5.1157 | 4.3753 | 3.9688 | 3.5365 | 3.106 | 2.6965 | 1.1149 | 0.15284 | 0.01275
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | WPD Best View | Thermal headroom (MW) | 6.3129 | 6.3771 | 6.5987 | 6.6538 | 6.7233 | 6.7624 | 6.7765 | 6.774 | 6.7533 | 6.7085 | 6.6159 | 6.4109 | 6.2042 | 5.9684 | 5.7043 | 5.0621 | 3.4349 | 1.664 | 1.07
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Consumer Transformation | Thermal headroom (MW) | 4.7976 | 4.4087 | 4.1055 | 3.6501 | 3.1429 | 2.3969 | 1.2956 | 0.27263 | -0.83265 | -2.3355 | -3.4567 | -4.7749 | -6.3475 | -8.0386 | -9.8247 | -11.3476 | -16.9548 | -18.6637 | -18.1147
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Leading the Way | Thermal headroom (MW) | 4.7523 | 4.3285 | 4.1116 | 3.6624 | 3.1655 | 2.4032 | 1.3039 | 0.29845 | -1.2255 | -2.4072 | -3.4806 | -4.4082 | -5.8823 | -7.3731 | -8.8584 | -10.2684 | -13.2746 | -13.1635 | -11.4685
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Steady Progression | Thermal headroom (MW) | 4.9121 | 4.9881 | 5.214 | 5.1909 | 5.1887 | 5.1711 | 5.1369 | 5.0466 | 4.9145 | 4.7481 | 4.5368 | 4.1581 | 3.7377 | 3.2959 | 2.8188 | 1.9746 | -0.4968 | -3.372 | -4.4113
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | System Transformation | Thermal headroom (MW) | 4.8426 | 4.8452 | 4.9635 | 4.9103 | 4.8277 | 4.7307 | 4.5046 | 4.2437 | 3.9314 | 3.5636 | 3.0795 | 2.0681 | 1.4213 | 0.74906 | 0.08245 | -0.51442 | -3.563 | -6.2921 | -6.3847
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | WPD Best View | Thermal headroom (MW) | 4.9096 | 4.9698 | 5.1992 | 5.1745 | 5.1702 | 5.1472 | 5.1024 | 4.9882 | 4.8362 | 4.6531 | 4.3818 | 3.9232 | 3.4636 | 2.965 | 2.4363 | 1.5521 | -0.74051 | -3.7164 | -4.6273
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Consumer Transformation | Thermal headroom (MW) | 6.7802 | 6.4277 | 5.7147 | 4.5449 | 3.2202 | 2.8628 | 2.0542 | 1.1182 | 0.10391 | -1.1367 | -1.9374 | -2.8765 | -3.6895 | -4.4525 | -5.6629 | -6.8376 | -11.5263 | -13.7939 | -14.2441
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Leading the Way | Thermal headroom (MW) | 6.7498 | 6.3254 | 5.5902 | 4.1443 | 2.4933 | 2.1475 | 1.3227 | 0.4162 | -0.96457 | -1.8597 | -2.5633 | -3.0999 | -3.5404 | -4.3833 | -5.2393 | -6.3447 | -9.0332 | -10.1594 | -9.3914
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Steady Progression | Thermal headroom (MW) | 6.8546 | 6.8524 | 6.7017 | 6.0257 | 5.3191 | 5.291 | 5.1877 | 5.0033 | 4.8086 | 4.6234 | 4.3975 | 4.091 | 3.7521 | 3.3689 | 2.9501 | 2.1773 | 0.26038 | -1.9322 | -2.5216
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | System Transformation | Thermal headroom (MW) | 6.8112 | 6.759 | 6.3745 | 5.512 | 4.4773 | 4.453 | 4.2981 | 4.0167 | 3.6325 | 3.282 | 2.8904 | 2.0837 | 1.6317 | 1.1081 | 0.59266 | 0.088523 | -1.961 | -3.1209 | -3.3203
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | WPD Best View | Thermal headroom (MW) | 6.8195 | 6.7714 | 6.3948 | 5.5367 | 4.5085 | 4.4929 | 4.3508 | 4.0868 | 3.7202 | 3.4117 | 3.0734 | 2.3226 | 1.9232 | 1.4542 | 0.97716 | 0.5062 | -1.5873 | -3.0112 | -3.3635
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Consumer Transformation | Thermal headroom (MW) | 15.7508 | 15.7803 | 15.7754 | 15.8044 | 15.8311 | 15.8455 | 15.8584 | 15.8547 | 15.8141 | 15.4141 | 15.369 | 15.336 | 15.3141 | 15.3007 | 15.2828 | 15.2263 | 14.6095 | 14.2461 | 14.331
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Leading the Way | Thermal headroom (MW) | 15.7508 | 15.7804 | 15.7527 | 15.7812 | 15.8079 | 15.7974 | 15.8158 | 15.8208 | 15.4214 | 15.3779 | 15.3312 | 15.311 | 15.3062 | 15.2299 | 15.1704 | 14.7392 | 14.651 | 14.7672 | 14.6267
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Steady Progression | Thermal headroom (MW) | 15.7521 | 15.7831 | 15.7989 | 15.8313 | 15.8627 | 15.8897 | 15.9151 | 15.9395 | 15.9639 | 15.9864 | 15.9867 | 15.9782 | 15.9502 | 15.9177 | 15.8798 | 15.4802 | 15.2149 | 14.6655 | 14.6729
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | System Transformation | Thermal headroom (MW) | 15.7521 | 15.7826 | 15.7808 | 15.8126 | 15.8437 | 15.8728 | 15.8937 | 15.9143 | 15.9346 | 15.934 | 15.9097 | 15.5085 | 15.4536 | 15.3892 | 15.3317 | 15.2688 | 14.6817 | 14.3086 | 14.0417
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | WPD Best View | Thermal headroom (MW) | 15.7521 | 15.7826 | 15.7808 | 15.8126 | 15.8437 | 15.8728 | 15.8937 | 15.9143 | 15.9346 | 15.9228 | 15.9089 | 15.5085 | 15.4536 | 15.3892 | 15.3317 | 15.2688 | 14.6817 | 14.3086 | 14.0417
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Consumer Transformation | Thermal headroom (MW) | 7.4477 | 6.9516 | 6.3608 | 5.8565 | 5.3208 | 4.6565 | 3.7844 | 2.9213 | 2.0111 | 0.79188 | -0.032905 | -0.96039 | -1.8835 | -2.6916 | -3.3396 | -3.8618 | -6.6813 | -8.3821 | -8.4379
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Leading the Way | Thermal headroom (MW) | 7.4006 | 6.7752 | 6.3055 | 5.7986 | 5.2852 | 4.6325 | 3.748 | 2.9113 | 1.6492 | 0.74963 | -0.058438 | -0.87286 | -1.5775 | -2.0818 | -2.3784 | -2.9174 | -5.3893 | -5.616 | -4.7668
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Steady Progression | Thermal headroom (MW) | 7.5645 | 7.4484 | 7.3627 | 7.1487 | 7.0318 | 6.8929 | 6.6944 | 6.4514 | 6.1836 | 5.8804 | 5.5186 | 5.065 | 4.5601 | 3.9968 | 3.3998 | 2.409 | -1.3327 | -3.9962 | -4.8807
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | System Transformation | Thermal headroom (MW) | 7.4914 | 7.3018 | 7.033 | 6.8521 | 6.6756 | 6.445 | 6.1179 | 5.7404 | 5.2776 | 4.7752 | 4.2092 | 3.159 | 2.3795 | 1.5558 | 0.68958 | -0.22862 | -3.949 | -5.2608 | -5.5754
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | WPD Best View | Thermal headroom (MW) | 7.5475 | 7.382 | 7.2494 | 6.9755 | 6.7905 | 6.5683 | 6.2774 | 5.9481 | 5.5757 | 5.1758 | 4.7367 | 4.2242 | 3.7034 | 3.1606 | 2.5323 | 1.5329 | -1.6393 | -3.8173 | -4.4203
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Consumer Transformation | Thermal headroom (MW) | -1.3205 | -1.8755 | -1.809 | -1.8973 | -2.0249 | -2.3148 | -2.8649 | -3.2992 | -3.7211 | -4.827 | -5.2099 | -5.7342 | -6.5244 | -6.8892 | -7.4993 | -7.6727 | -9.9332 | -11.7904 | -11.8552
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Leading the Way | Thermal headroom (MW) | -1.3673 | -1.975 | -1.8906 | -1.9716 | -2.078 | -2.3741 | -2.8891 | -3.2769 | -4.3924 | -4.7447 | -5.1091 | -5.6888 | -5.8166 | -6.2425 | -6.1498 | -6.7358 | -7.3632 | -7.8628 | -7.2455
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Steady Progression | Thermal headroom (MW) | -1.2351 | -1.1798 | -0.85324 | -0.70142 | -0.55281 | -0.41865 | -0.3196 | -0.2379 | -0.52106 | -0.5007 | -0.48223 | -0.52841 | -0.56873 | -0.67093 | -0.78787 | -1.641 | -3.2022 | -4.4735 | -4.4647
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | System Transformation | Thermal headroom (MW) | -1.2905 | -1.3027 | -1.011 | -0.88781 | -0.76297 | -1.0382 | -1 | -0.99895 | -1.0066 | -1.0451 | -1.1364 | -1.9882 | -2.1747 | -2.3895 | -2.9705 | -3.5409 | -5.4605 | -6.6143 | -6.602
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | WPD Best View | Thermal headroom (MW) | -1.235 | -1.1818 | -0.85547 | -0.70698 | -0.56006 | -0.43081 | -0.34215 | -0.26812 | -0.56471 | -0.56968 | -0.55713 | -0.98643 | -1.0537 | -1.1879 | -1.3253 | -1.8418 | -3.6511 | -4.78 | -5.0768
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Consumer Transformation | Thermal headroom (MW) | 2.1497 | 1.8551 | 1.6073 | 1.3088 | 0.99987 | 0.61168 | 0.16389 | -0.26583 | -0.70013 | -1.1299 | -1.5442 | -1.9053 | -2.2764 | -2.6219 | -2.8883 | -3.1213 | -3.9496 | -4.4183 | -4.2716
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Leading the Way | Thermal headroom (MW) | 2.1177 | 1.8163 | 1.6073 | 1.3132 | 1.031 | 0.6506 | 0.1803 | -0.21664 | -0.66394 | -1.1195 | -1.515 | -1.8609 | -2.2088 | -2.4613 | -2.59 | -2.6793 | -3.5925 | -3.4033 | -2.7562
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Steady Progression | Thermal headroom (MW) | 2.2422 | 2.2144 | 2.2581 | 2.2162 | 2.1949 | 2.1439 | 2.0653 | 1.9747 | 1.8548 | 1.7225 | 1.5422 | 1.3011 | 1.0173 | 0.70942 | 0.38927 | 0.04468 | -2.0354 | -3.76 | -4.4576
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | System Transformation | Thermal headroom (MW) | 2.1825 | 2.1009 | 2.086 | 1.999 | 1.933 | 1.8173 | 1.6101 | 1.3879 | 1.1306 | 0.8269 | 0.52105 | 0.10636 | -0.3408 | -0.81141 | -1.2872 | -1.7495 | -3.6883 | -4.3455 | -4.2747
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | WPD Best View | Thermal headroom (MW) | 2.2051 | 2.1419 | 2.1619 | 2.094 | 2.0454 | 1.9633 | 1.8214 | 1.6544 | 1.4594 | 1.2342 | 0.98405 | 0.66147 | 0.30458 | -0.084885 | -0.47861 | -0.88139 | -2.8922 | -4.1224 | -4.3994
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Consumer Transformation | Thermal headroom (MW) | 29.7715 | 28.7876 | 28.6277 | 28.1594 | 27.6426 | 26.8807 | 25.7327 | 24.7041 | 23.8149 | 22.5505 | 21.5907 | 19.8587 | 16.7379 | 14.059 | 11.0048 | 8.1676 | -2.9468 | -6.9973 | -7.3946
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Leading the Way | Thermal headroom (MW) | 29.6761 | 28.5361 | 28.5902 | 28.1861 | 27.7449 | 26.9636 | 25.7896 | 24.8199 | 23.589 | 22.6637 | 21.6644 | 19.1579 | 16.5349 | 13.5461 | 10.9832 | 8.3582 | 1.9705 | 1.4383 | 5.6789
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Steady Progression | Thermal headroom (MW) | 29.9948 | 30.1213 | 30.8019 | 30.9747 | 31.2059 | 31.3919 | 31.5606 | 31.669 | 31.4381 | 31.4878 | 31.4976 | 31.2533 | 31.0176 | 30.7008 | 30.2662 | 29.359 | 23.8679 | 14.5979 | 11.6542
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | System Transformation | Thermal headroom (MW) | 29.8479 | 29.817 | 30.294 | 30.4392 | 30.5472 | 30.2895 | 30.216 | 30.115 | 30.0133 | 29.8249 | 29.5642 | 28.6323 | 28.0403 | 27.2839 | 26.1326 | 24.9409 | 14.2443 | 7.9788 | 8.1419
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | WPD Best View | Thermal headroom (MW) | 29.7715 | 28.7876 | 28.6277 | 28.1594 | 27.6426 | 26.8807 | 25.7327 | 24.7041 | 23.8149 | 22.5505 | 21.5907 | 19.8587 | 16.7379 | 14.059 | 11.0048 | 8.1676 | -2.9468 | -6.9973 | -7.3946
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Consumer Transformation | Thermal headroom (MW) | 53.0762 | 51.5186 | 50.3666 | 48.8236 | 47.0185 | 44.7603 | 41.4567 | 38.4811 | 35.5397 | 31.6054 | 28.5642 | 24.7163 | 21.331 | 17.7662 | 13.989 | 10.7819 | -7.1176 | -15.2115 | -15.9797
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Leading the Way | Thermal headroom (MW) | 52.8892 | 51.1217 | 50.021 | 48.2293 | 46.7382 | 44.5 | 41.2691 | 38.4636 | 34.562 | 31.5052 | 28.4589 | 25.7148 | 22.8164 | 20.0184 | 17.4556 | 14.2052 | 2.0549 | -0.79098 | 3.976
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Steady Progression | Thermal headroom (MW) | 53.4476 | 53.3178 | 53.7792 | 53.6428 | 53.5182 | 53.4335 | 53.3396 | 53.0923 | 52.6857 | 52.2007 | 51.4471 | 50.2002 | 49.0037 | 47.5762 | 46.0067 | 43.3954 | 32.6417 | 23.2388 | 20.2484
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | System Transformation | Thermal headroom (MW) | 53.2038 | 52.8059 | 52.8915 | 52.4886 | 52.2583 | 51.974 | 51.4319 | 50.7024 | 49.5304 | 48.3937 | 47.096 | 44.4346 | 42.3502 | 39.8303 | 37.4005 | 35.0076 | 22.1126 | 15.6635 | 15.1102
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | WPD Best View | Thermal headroom (MW) | 53.0762 | 51.5186 | 50.3666 | 48.8236 | 47.0185 | 44.7603 | 41.4567 | 38.4811 | 35.5397 | 31.6054 | 28.5642 | 24.7163 | 21.331 | 17.7662 | 13.989 | 10.7819 | -7.1176 | -15.2115 | -15.9797
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Consumer Transformation | Thermal headroom (MW) | 4.2852 | 3.7263 | 3.2984 | 2.7824 | 2.1769 | 1.8721 | 1.1597 | 0.49721 | -0.13665 | -0.79591 | -1.4424 | -2.646 | -3.5284 | -4.7703 | -6.452 | -7.7644 | -13.9704 | -16.8322 | -17.2954
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Leading the Way | Thermal headroom (MW) | 4.2617 | 3.5271 | 3.1453 | 2.212 | 2.0055 | 1.7279 | 1.0283 | 0.42369 | -0.19066 | -0.85362 | -1.496 | -2.3387 | -3.3184 | -4.3514 | -5.7285 | -6.6032 | -10.9053 | -12.4395 | -10.8365
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Steady Progression | Thermal headroom (MW) | 4.3585 | 4.2664 | 4.3909 | 4.2439 | 4.3588 | 4.4487 | 4.4971 | 4.5579 | 4.5831 | 4.6096 | 4.5879 | 4.1415 | 3.9806 | 3.7832 | 3.5548 | 3.3003 | 1.254 | -1.0009 | -2.1897
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | System Transformation | Thermal headroom (MW) | 4.3135 | 4.1071 | 4.0331 | 3.8699 | 3.9776 | 4.0287 | 4.0049 | 3.9329 | 3.4936 | 3.4074 | 3.2829 | 3.0399 | 2.7395 | 2.0217 | 1.6413 | 1.2917 | -1.5288 | -4.3842 | -4.7518
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | WPD Best View | Thermal headroom (MW) | 4.2852 | 3.7263 | 3.2984 | 2.7824 | 2.1769 | 1.8721 | 1.1597 | 0.49721 | -0.13665 | -0.79591 | -1.4424 | -2.646 | -3.5284 | -4.7703 | -6.452 | -7.7644 | -13.9704 | -16.8322 | -17.2954
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Consumer Transformation | Thermal headroom (MW) | 5.9409 | 5.5936 | 5.342 | 4.8614 | 4.3944 | 3.7337 | 2.799 | 1.8846 | 0.93582 | -0.37061 | -1.3261 | -2.3895 | -3.3333 | -4.3257 | -5.1928 | -5.9196 | -10.4657 | -12.8582 | -13.0617
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Leading the Way | Thermal headroom (MW) | 5.9131 | 5.5824 | 5.2966 | 4.9184 | 4.4851 | 3.8372 | 2.9079 | 2.0409 | 0.69104 | -0.29169 | -1.2616 | -1.991 | -2.7852 | -3.4514 | -3.8355 | -4.4697 | -7.8096 | -8.6557 | -7.4636
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Steady Progression | Thermal headroom (MW) | 6.0446 | 6.0912 | 6.2793 | 6.3113 | 6.2308 | 6.2102 | 6.1881 | 6.0977 | 5.9129 | 5.689 | 5.4036 | 5.0103 | 4.5469 | 4.0095 | 3.4364 | 2.467 | -0.9925 | -3.507 | -4.2727
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | System Transformation | Thermal headroom (MW) | 5.9946 | 5.9924 | 6.1283 | 6.0215 | 5.9479 | 5.8727 | 5.7096 | 5.4446 | 5.1078 | 4.6716 | 4.1575 | 3.1457 | 2.3923 | 1.5778 | 0.74367 | -0.052754 | -3.8004 | -5.1001 | -5.2364
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | WPD Best View | Thermal headroom (MW) | 5.9409 | 5.5936 | 5.342 | 4.8614 | 4.3944 | 3.7337 | 2.799 | 1.8846 | 0.93582 | -0.37061 | -1.3261 | -2.3895 | -3.3333 | -4.3257 | -5.1928 | -5.9196 | -10.4657 | -12.8582 | -13.0617
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Consumer Transformation | Thermal headroom (MW) | 9.5101 | 9.4048 | 9.4159 | 9.3073 | 9.062 | 8.6862 | 8.199 | 7.756 | 7.3565 | 6.9025 | 6.3702 | 5.7238 | 5.0601 | 4.4095 | 3.7436 | 3.0701 | 0.59179 | -0.1275 | -0.03425
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Leading the Way | Thermal headroom (MW) | 9.4828 | 9.3794 | 9.3717 | 9.2214 | 8.9515 | 8.5474 | 8.0718 | 7.6176 | 7.1748 | 6.6933 | 6.0981 | 5.4858 | 4.8716 | 4.1962 | 3.5527 | 2.9751 | 1.4769 | 1.6604 | 2.9881
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Steady Progression | Thermal headroom (MW) | 9.5493 | 9.5999 | 9.7651 | 9.8139 | 9.7567 | 9.773 | 9.7955 | 9.7551 | 9.719 | 9.7044 | 9.5915 | 9.4953 | 9.3522 | 9.1647 | 8.9563 | 8.6967 | 6.713 | 4.5952 | 4.1462
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | System Transformation | Thermal headroom (MW) | 9.5158 | 9.5405 | 9.6793 | 9.6412 | 9.5739 | 9.5563 | 9.4807 | 9.4031 | 9.301 | 9.143 | 8.9872 | 8.7443 | 8.4245 | 8.0665 | 7.6349 | 7.1212 | 4.5002 | 3.3007 | 3.5903
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | WPD Best View | Thermal headroom (MW) | 9.5101 | 9.4048 | 9.4159 | 9.3073 | 9.062 | 8.6862 | 8.199 | 7.756 | 7.3565 | 6.9025 | 6.3702 | 5.7238 | 5.0601 | 4.4095 | 3.7436 | 3.0701 | 0.59179 | -0.1275 | -0.03425
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Consumer Transformation | Thermal headroom (MW) | -0.6504 | -1.5249 | -2.2904 | -3.033 | -3.8384 | -5.0729 | -6.762 | -8.178 | -9.6016 | -11.7486 | -13.0878 | -14.6331 | -16.0086 | -17.2443 | -18.4602 | -19.4545 | -27.2864 | -30.973 | -31.4044
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Leading the Way | Thermal headroom (MW) | -0.78953 | -1.7841 | -2.4636 | -3.1888 | -3.9719 | -5.1805 | -6.8141 | -8.1103 | -10.2255 | -11.6108 | -12.8548 | -13.7888 | -14.7138 | -15.5225 | -16.0888 | -17.7706 | -22.9856 | -24.4169 | -23.2113
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Steady Progression | Thermal headroom (MW) | -0.43091 | -0.63036 | -0.61844 | -0.75784 | -0.84459 | -1.0304 | -1.1968 | -1.3983 | -1.6646 | -2.0157 | -2.4459 | -3.0021 | -3.6106 | -4.3248 | -5.1164 | -6.6527 | -11.3715 | -15.0993 | -16.2141
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | System Transformation | Thermal headroom (MW) | -0.58699 | -0.92177 | -1.097 | -1.272 | -1.4754 | -1.7628 | -2.1195 | -2.5472 | -3.072 | -3.6834 | -4.375 | -5.96 | -6.9615 | -7.9987 | -9.1044 | -10.1183 | -15.5461 | -17.7483 | -18.3549
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | WPD Best View | Thermal headroom (MW) | -0.6504 | -1.5249 | -2.2904 | -3.033 | -3.8384 | -5.0729 | -6.762 | -8.178 | -9.6016 | -11.7486 | -13.0878 | -14.6331 | -16.0086 | -17.2443 | -18.4602 | -19.4545 | -27.2864 | -30.973 | -31.4044
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Consumer Transformation | Thermal headroom (MW) | 84.8405 | 82.8798 | 82.445 | 81.128 | 79.345 | 76.8121 | 71.5791 | 66.9234 | 62.0264 | 56.8208 | 52.7349 | 47.1225 | 41.5869 | 35.7741 | 28.9473 | 21.4864 | -9.4726 | -21.8791 | -22.909
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Leading the Way | Thermal headroom (MW) | 84.4962 | 82.2833 | 82.2334 | 80.739 | 79.4094 | 76.9047 | 71.2969 | 66.2481 | 59.6777 | 55.374 | 50.6345 | 46.059 | 42.0557 | 37.474 | 30.8958 | 24.0097 | 3.0663 | -0.99223 | 7.227
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Steady Progression | Thermal headroom (MW) | 85.3779 | 85.4484 | 87.0501 | 87.4996 | 87.9502 | 88.1224 | 87.6291 | 87.1616 | 86.4419 | 86.1984 | 85.6413 | 84.0405 | 82.5992 | 80.6059 | 78.4416 | 74.999 | 61.1596 | 48.1878 | 44.2584
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | System Transformation | Thermal headroom (MW) | 84.9975 | 84.6782 | 85.9212 | 86.2702 | 86.4603 | 86.3092 | 84.9548 | 83.4331 | 81.4859 | 80.4432 | 78.8435 | 75.4711 | 72.8015 | 69.1946 | 65.9192 | 62.7779 | 43.9336 | 35.6905 | 35.3475
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | WPD Best View | Thermal headroom (MW) | 84.8499 | 82.9658 | 82.5965 | 81.3402 | 79.591 | 77.1543 | 71.9871 | 67.4108 | 62.5783 | 57.6985 | 53.8369 | 48.1721 | 42.5829 | 36.7801 | 30.0109 | 22.5964 | -8.6051 | -21.3468 | -22.4044
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Consumer Transformation | Thermal headroom (MW) | 19.2443 | 18.8399 | 18.632 | 18.2711 | 17.5453 | 17.0042 | 16.0106 | 15.1396 | 14.4292 | 13.6974 | 12.9649 | 11.6456 | 10.7895 | 10.0194 | 8.7537 | 7.3069 | 1.1173 | -1.5094 | -1.7644
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Leading the Way | Thermal headroom (MW) | 19.1802 | 18.6703 | 18.6313 | 17.951 | 17.6325 | 17.0834 | 16.1291 | 15.3219 | 14.6427 | 13.907 | 13.2166 | 12.356 | 11.9469 | 11.67 | 10.2372 | 9.2592 | 5.4597 | 3.9981 | 5.8283
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Steady Progression | Thermal headroom (MW) | 19.3704 | 19.4736 | 19.8815 | 19.921 | 20.0594 | 20.1793 | 20.2578 | 20.3377 | 20.4226 | 20.4857 | 20.5208 | 20.1022 | 20.0126 | 19.8327 | 19.6146 | 19.3609 | 17.4338 | 15.61 | 15.0974
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | System Transformation | Thermal headroom (MW) | 19.2788 | 19.3128 | 19.5504 | 19.6336 | 19.7089 | 19.7506 | 19.7365 | 19.6842 | 19.2933 | 19.236 | 19.1373 | 18.9324 | 18.6163 | 17.9015 | 17.5314 | 17.1757 | 14.8856 | 13.7102 | 13.5574
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | WPD Best View | Thermal headroom (MW) | 19.2443 | 18.8399 | 18.632 | 18.2711 | 17.5453 | 17.0042 | 16.0106 | 15.1396 | 14.4292 | 13.6974 | 12.9649 | 11.6456 | 10.7895 | 10.0194 | 8.7537 | 7.3069 | 1.1173 | -1.5094 | -1.7644
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Consumer Transformation | Thermal headroom (MW) | 14.0564 | 13.4692 | 13.1757 | 12.7396 | 12.2808 | 11.6219 | 10.322 | 9.0852 | 7.7959 | 6.1382 | 4.9064 | 3.389 | 2.0881 | 1.0013 | -0.37387 | -2.1296 | -9.0829 | -12.2183 | -12.6465
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Leading the Way | Thermal headroom (MW) | 13.8758 | 13.2577 | 13.0245 | 12.6368 | 12.2081 | 11.5946 | 10.3223 | 9.1528 | 7.49 | 6.1977 | 5.018 | 4.0632 | 3.3558 | 2.8092 | 1.4928 | -0.066402 | -4.1967 | -5.754 | -4.3135
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Steady Progression | Thermal headroom (MW) | 14.2684 | 14.2365 | 14.5093 | 14.5673 | 14.6178 | 14.6353 | 14.5731 | 14.5061 | 14.3933 | 14.2519 | 14.0498 | 13.6723 | 13.2792 | 12.8506 | 12.3894 | 11.5423 | 8.8656 | 6.8639 | 6.2718
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | System Transformation | Thermal headroom (MW) | 14.0948 | 13.9661 | 14.1422 | 14.1663 | 14.1754 | 14.1247 | 13.9578 | 13.729 | 13.4642 | 13.1058 | 12.6313 | 11.6568 | 11.0316 | 10.4038 | 9.7563 | 9.1568 | 6.7202 | 5.2737 | 5.2222
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | WPD Best View | Thermal headroom (MW) | 14.0564 | 13.4692 | 13.1757 | 12.7396 | 12.2808 | 11.6219 | 10.322 | 9.0852 | 7.7959 | 6.1382 | 4.9064 | 3.389 | 2.0881 | 1.0013 | -0.37387 | -2.1296 | -9.0829 | -12.2183 | -12.6465
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Consumer Transformation | Thermal headroom (MW) | 8.271 | 7.8322 | 7.7898 | 7.5982 | 7.3483 | 6.7787 | 5.5185 | 4.4549 | 3.3651 | 2.4051 | 1.7687 | 0.81065 | -0.48723 | -2.0115 | -3.5979 | -5.1939 | -12.3044 | -15.1334 | -15.5746
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Leading the Way | Thermal headroom (MW) | 8.2492 | 7.7343 | 7.7401 | 7.568 | 7.3184 | 6.7362 | 5.2289 | 3.9205 | 2.1972 | 1.5113 | 0.47041 | -0.55556 | -1.5338 | -2.9322 | -4.372 | -6.1042 | -11.6448 | -12.3487 | -10.9468
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Steady Progression | Thermal headroom (MW) | 8.3243 | 8.2136 | 8.4357 | 8.5115 | 8.5358 | 8.4433 | 8.097 | 7.7562 | 7.3519 | 7.2204 | 7.0647 | 6.8444 | 6.5824 | 6.1398 | 5.6666 | 4.7952 | 1.6593 | -2.2677 | -3.5854
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | System Transformation | Thermal headroom (MW) | 8.2907 | 8.0822 | 8.2844 | 8.3354 | 8.3142 | 8.1535 | 7.4756 | 6.8318 | 6.1525 | 5.9353 | 5.682 | 4.9391 | 4.4402 | 3.7191 | 2.9954 | 2.2848 | -3.5399 | -6.2917 | -6.7307
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | WPD Best View | Thermal headroom (MW) | 8.271 | 7.8322 | 7.7898 | 7.5982 | 7.3483 | 6.7787 | 5.5185 | 4.4549 | 3.2847 | 2.3643 | 1.7687 | 0.81065 | -0.48723 | -2.0115 | -3.5979 | -5.1939 | -12.3044 | -15.1334 | -15.5746
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Consumer Transformation | Thermal headroom (MW) | 32.9199 | 31.96 | 31.4441 | 30.3827 | 28.7803 | 26.9028 | 23.6422 | 20.2468 | 16.6595 | 11.3118 | 7.6594 | 3.124 | -1.5265 | -5.8985 | -10.6966 | -14.7517 | -34.3314 | -44.3988 | -45.2115
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Leading the Way | Thermal headroom (MW) | 32.8302 | 31.8814 | 31.5054 | 30.2258 | 29.0178 | 27.2207 | 24.0005 | 20.4863 | 14.8745 | 10.9039 | 7.015 | 3.3792 | -0.26839 | -3.8734 | -7.3677 | -11.7993 | -24.0805 | -27.0489 | -21.885
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Steady Progression | Thermal headroom (MW) | 33.2704 | 33.6778 | 34.6941 | 35.0989 | 35.4419 | 35.6676 | 35.8144 | 35.6259 | 35.1804 | 34.5805 | 33.7779 | 32.4019 | 31.0504 | 29.3771 | 27.5124 | 23.848 | 11.9268 | -0.85483 | -3.9125
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | System Transformation | Thermal headroom (MW) | 33.0924 | 33.2994 | 34.1347 | 34.367 | 34.5486 | 34.5475 | 34.3198 | 33.4235 | 31.9767 | 30.6564 | 28.9301 | 25.2987 | 22.8466 | 19.8026 | 16.8892 | 14.1242 | -1.476 | -9.2111 | -10.1303
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | WPD Best View | Thermal headroom (MW) | 32.9199 | 31.95 | 31.4463 | 30.3823 | 28.7795 | 26.8996 | 23.6386 | 20.2369 | 16.6458 | 11.2919 | 7.642 | 3.1191 | -1.5078 | -5.8891 | -10.6586 | -14.6811 | -34.3165 | -44.2924 | -45.0218
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Consumer Transformation | Thermal headroom (MW) | 10.279 | 10.2206 | 10.0764 | 10.0274 | 9.9783 | 9.8247 | 9.5073 | 8.8388 | 8.1301 | 7.5229 | 6.9142 | 6.4009 | 5.7935 | 5.2728 | 4.4818 | 3.9108 | 2.1727 | 1.6162 | 1.8535
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Leading the Way | Thermal headroom (MW) | 10.2699 | 10.2231 | 10.0332 | 10.0123 | 9.9425 | 9.8205 | 9.515 | 8.6675 | 7.7665 | 7.0096 | 6.1901 | 5.7686 | 5.2825 | 4.9181 | 4.2092 | 3.9359 | 3.124 | 3.1065 | 4.0183
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Steady Progression | Thermal headroom (MW) | 10.3122 | 10.3904 | 10.4569 | 10.5656 | 10.6536 | 10.7413 | 10.8105 | 10.635 | 10.4165 | 10.2599 | 10.072 | 10.016 | 9.9359 | 9.8494 | 9.6157 | 9.4992 | 8.834 | 7.716 | 7.5642
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | System Transformation | Thermal headroom (MW) | 10.2953 | 10.3574 | 10.3612 | 10.4569 | 10.5347 | 10.6254 | 10.6354 | 10.2541 | 9.7969 | 9.5142 | 9.1975 | 9.1139 | 8.9224 | 8.7364 | 8.2726 | 8.0308 | 7.0086 | 6.6142 | 6.9974
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | WPD Best View | Thermal headroom (MW) | 10.279 | 10.2206 | 10.0764 | 10.0274 | 9.9783 | 9.8247 | 9.5073 | 8.8388 | 8.1301 | 7.5229 | 6.9142 | 6.4009 | 5.7935 | 5.2728 | 4.4818 | 3.9108 | 2.1727 | 1.6162 | 1.8535
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Consumer Transformation | Thermal headroom (MW) | 4.634 | 4.4219 | 4.4 | 4.1804 | 3.9247 | 3.6001 | 2.8303 | 2.1258 | 1.3619 | 0.18237 | -0.72169 | -1.9634 | -3.261 | -4.4856 | -5.7722 | -7.048 | -12.215 | -14.5749 | -14.8574
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Leading the Way | Thermal headroom (MW) | 4.5922 | 4.4228 | 4.485 | 4.3044 | 4.0836 | 3.7793 | 3.0148 | 2.3082 | 1.148 | 0.2379 | -0.71766 | -1.7122 | -2.7181 | -3.7787 | -4.8198 | -6.0574 | -9.0579 | -9.9604 | -8.4815
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Steady Progression | Thermal headroom (MW) | 4.707 | 4.8829 | 5.2435 | 5.4382 | 5.6071 | 5.7354 | 5.851 | 5.9677 | 5.9902 | 6.0397 | 6.0649 | 5.9841 | 5.9056 | 5.7393 | 5.5437 | 4.9192 | 2.7419 | -0.19849 | -0.72259
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | System Transformation | Thermal headroom (MW) | 4.6407 | 4.779 | 5.1282 | 5.2628 | 5.4177 | 5.4984 | 5.5733 | 5.5278 | 5.5192 | 5.4283 | 5.2803 | 4.7249 | 4.4238 | 4.0242 | 3.5666 | 3.0789 | -0.42578 | -2.579 | -2.6447
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | WPD Best View | Thermal headroom (MW) | 4.634 | 4.4219 | 4.4 | 4.1804 | 3.9247 | 3.6001 | 2.8303 | 2.1258 | 1.3619 | 0.18237 | -0.72169 | -1.9634 | -3.261 | -4.4856 | -5.7722 | -7.048 | -12.215 | -14.5749 | -14.8574
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Consumer Transformation | Thermal headroom (MW) | 8.2896 | 7.9455 | 7.7263 | 7.4461 | 7.1158 | 6.6648 | 5.8959 | 5.1511 | 4.4051 | 2.9375 | 2.2079 | 1.3499 | 0.59291 | -0.092116 | -0.77682 | -1.379 | -6.362 | -9.0392 | -9.5008
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Leading the Way | Thermal headroom (MW) | 8.2437 | 7.8687 | 7.6919 | 7.4292 | 7.1391 | 6.6773 | 5.9371 | 5.2459 | 3.7912 | 3.0273 | 2.3163 | 1.7496 | 1.2818 | 0.77079 | 0.48202 | -0.928 | -3.8299 | -4.7823 | -4.2581
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Steady Progression | Thermal headroom (MW) | 8.3797 | 8.3614 | 8.4866 | 8.5063 | 8.5258 | 8.533 | 8.5223 | 8.497 | 8.3947 | 8.2179 | 8.0235 | 7.7443 | 7.427 | 7.0419 | 6.6519 | 5.4857 | 2.893 | 0.12154 | -0.48176
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | System Transformation | Thermal headroom (MW) | 8.3308 | 8.2438 | 8.3242 | 8.323 | 8.3143 | 8.2905 | 8.1927 | 8.0205 | 7.8037 | 7.4994 | 7.144 | 5.9826 | 5.4472 | 4.8764 | 4.291 | 3.7195 | 0.45657 | -1.244 | -1.8379
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | WPD Best View | Thermal headroom (MW) | 8.2896 | 7.9455 | 7.7263 | 7.4461 | 7.1158 | 6.6648 | 5.8959 | 5.1511 | 4.4051 | 2.9375 | 2.2079 | 1.3499 | 0.59291 | -0.092116 | -0.77682 | -1.379 | -6.362 | -9.0392 | -9.5008
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Consumer Transformation | Thermal headroom (MW) | 2.983 | 2.8746 | 2.8139 | 2.6378 | 2.3609 | 2.0197 | 1.5691 | 1.1093 | 0.61266 | 0.094097 | -0.39018 | -0.91189 | -1.4795 | -1.9571 | -2.3484 | -2.6558 | -3.6818 | -4.4611 | -4.4246
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Leading the Way | Thermal headroom (MW) | 2.9763 | 2.8842 | 2.8543 | 2.6703 | 2.3988 | 2.0621 | 1.6058 | 1.1522 | 0.60833 | 0.07042 | -0.42559 | -0.93787 | -1.3699 | -1.6747 | -1.8439 | -1.898 | -3.0442 | -3.0726 | -2.1064
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Steady Progression | Thermal headroom (MW) | 3.0324 | 3.0761 | 3.1944 | 3.2055 | 3.1969 | 3.1805 | 3.1353 | 3.0424 | 2.9073 | 2.7501 | 2.5419 | 2.2827 | 1.9863 | 1.6423 | 1.2527 | 0.84596 | -1.4837 | -2.734 | -3.1052
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | System Transformation | Thermal headroom (MW) | 3.0125 | 3.0417 | 3.1454 | 3.1223 | 3.0871 | 3.0208 | 2.8936 | 2.7125 | 2.4869 | 2.2033 | 1.8484 | 1.425 | 0.93542 | 0.40266 | -0.12935 | -0.71812 | -2.8688 | -3.2562 | -3.0935
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | WPD Best View | Thermal headroom (MW) | 2.983 | 2.8746 | 2.8139 | 2.6378 | 2.3609 | 2.0197 | 1.5691 | 1.1093 | 0.61266 | 0.094097 | -0.39018 | -0.91189 | -1.4795 | -1.9571 | -2.3484 | -2.6558 | -3.6818 | -4.4611 | -4.4246
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Consumer Transformation | Thermal headroom (MW) | 4.1172 | 3.9483 | 3.8936 | 3.7122 | 3.5312 | 3.2877 | 2.8154 | 2.3861 | 1.9404 | 1.1333 | 0.67476 | 0.086201 | -0.86026 | -1.8522 | -2.9031 | -3.9408 | -8.1043 | -9.9866 | -10.1944
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Leading the Way | Thermal headroom (MW) | 4.1136 | 3.9528 | 3.9329 | 3.768 | 3.6231 | 3.4044 | 2.9181 | 2.524 | 1.7119 | 1.2408 | 0.77576 | 0.33713 | -0.54347 | -1.4283 | -2.3058 | -3.4149 | -5.8259 | -6.4168 | -5.4306
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Steady Progression | Thermal headroom (MW) | 4.1698 | 4.2745 | 4.5079 | 4.6038 | 4.6977 | 4.7674 | 4.845 | 4.8949 | 4.9239 | 4.9441 | 4.9336 | 4.8854 | 4.8008 | 4.6452 | 4.4911 | 3.9419 | 2.7828 | 0.24566 | -0.45845
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | System Transformation | Thermal headroom (MW) | 4.143 | 4.2197 | 4.4245 | 4.4767 | 4.5388 | 4.5682 | 4.5774 | 4.5499 | 4.5104 | 4.4357 | 4.3456 | 3.8075 | 3.5742 | 3.3118 | 3.027 | 2.7559 | 0.25835 | -1.8083 | -2.0685
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | WPD Best View | Thermal headroom (MW) | 4.1172 | 3.9483 | 3.8936 | 3.7122 | 3.5312 | 3.2877 | 2.8154 | 2.3861 | 1.9404 | 1.1333 | 0.67476 | 0.086201 | -0.86026 | -1.8522 | -2.9031 | -3.9408 | -8.1043 | -9.9866 | -10.1944
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Consumer Transformation | Thermal headroom (MW) | 12.2769 | 12.1455 | 12.0902 | 11.939 | 11.7819 | 11.4674 | 10.9754 | 10.5694 | 10.1514 | 9.3633 | 8.9512 | 8.4712 | 7.9729 | 7.4813 | 7.1024 | 6.7824 | 4.389 | 2.913 | 2.7827
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Leading the Way | Thermal headroom (MW) | 12.2619 | 12.1154 | 12.0768 | 11.9116 | 11.7695 | 11.4555 | 10.9612 | 10.5703 | 9.7834 | 9.3302 | 8.9408 | 8.645 | 8.2991 | 7.844 | 7.6556 | 7.1898 | 5.4232 | 5.1184 | 5.5372
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Steady Progression | Thermal headroom (MW) | 12.3208 | 12.3372 | 12.4701 | 12.477 | 12.5006 | 12.4832 | 12.4665 | 12.4554 | 12.401 | 12.3058 | 12.1766 | 12.005 | 11.7482 | 11.4344 | 11.1625 | 10.5221 | 8.7929 | 7.1889 | 6.8581
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | System Transformation | Thermal headroom (MW) | 12.3012 | 12.2902 | 12.3911 | 12.3789 | 12.36 | 12.318 | 12.2574 | 12.179 | 12.0363 | 11.8594 | 11.6154 | 10.9767 | 10.5543 | 10.0427 | 9.6677 | 9.3019 | 7.2294 | 6.3287 | 6.1384
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | WPD Best View | Thermal headroom (MW) | 12.2769 | 12.1369 | 12.0921 | 11.9387 | 11.7811 | 11.4648 | 10.9724 | 10.5609 | 10.1396 | 9.3461 | 8.9362 | 8.4669 | 7.9891 | 7.4894 | 7.1352 | 6.8433 | 4.4019 | 3.0048 | 2.9464
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Consumer Transformation | Thermal headroom (MW) | 9.9858 | 9.8778 | 9.8747 | 9.723 | 9.1684 | 8.9343 | 8.4462 | 7.9913 | 7.4806 | 6.5892 | 5.942 | 4.742 | 3.8665 | 3.0012 | 1.7426 | 0.80215 | -3.8043 | -6.1292 | -6.4328
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Leading the Way | Thermal headroom (MW) | 9.9935 | 9.8777 | 9.8983 | 9.4348 | 9.2461 | 9.0394 | 8.5792 | 8.0744 | 7.2213 | 6.5534 | 5.8716 | 4.7985 | 4.038 | 3.2206 | 2.1179 | 1.0227 | -1.5814 | -2.6084 | -1.9002
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Steady Progression | Thermal headroom (MW) | 10.0471 | 10.1661 | 10.3768 | 10.482 | 10.5632 | 10.6324 | 10.6909 | 10.7349 | 10.7981 | 10.7633 | 10.7094 | 10.148 | 9.8838 | 9.581 | 9.253 | 8.5613 | 6.0768 | 3.1211 | 2.246
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | System Transformation | Thermal headroom (MW) | 10.0249 | 10.0998 | 10.3099 | 10.4011 | 10.4667 | 10.471 | 10.5113 | 10.4903 | 10.0956 | 9.9535 | 9.671 | 8.9484 | 8.5154 | 7.6878 | 7.208 | 6.7199 | 3.1439 | 1.0959 | 0.43462
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | WPD Best View | Thermal headroom (MW) | 9.9858 | 9.8778 | 9.8747 | 9.723 | 9.1684 | 8.9343 | 8.4462 | 7.9913 | 7.4806 | 6.5892 | 5.942 | 4.742 | 3.8665 | 3.0012 | 1.7426 | 0.80215 | -3.8043 | -6.1292 | -6.4328
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Consumer Transformation | Thermal headroom (MW) | 16.3847 | 14.246 | 13.3204 | 9.8023 | 7.1117 | 1.0843 | -3.757 | -8.7634 | -14.3318 | -20.6582 | -26.8317 | -34.0115 | -40.381 | -46.1414 | -52.6483 | -58.2114 | -81.1036 | -90.4543 | -89.399
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Leading the Way | Thermal headroom (MW) | 17.282 | 14.8192 | 14.182 | 9.6408 | 7.2476 | 0.35051 | -4.5965 | -9.5096 | -16.1574 | -22.0242 | -28.3035 | -33.9465 | -38.7653 | -43.5427 | -48.3389 | -52.972 | -68.7125 | -69.2996 | -58.7753
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Steady Progression | Thermal headroom (MW) | 17.1858 | 16.9921 | 18.1467 | 17.0518 | 16.9255 | 14.732 | 14.1038 | 13.2749 | 11.9517 | 10.4494 | 8.3415 | 5.3523 | 2.4587 | -0.82447 | -4.6088 | -9.0192 | -30.4718 | -46.1503 | -50.0663
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | System Transformation | Thermal headroom (MW) | 16.6839 | 16.0211 | 16.8298 | 15.0005 | 14.5687 | 11.2649 | 10.0999 | 8.4668 | 5.9529 | 3.1192 | -0.59326 | -5.476 | -10.0911 | -15.4242 | -20.9453 | -26.3376 | -48.4426 | -55.0848 | -53.5448
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | WPD Best View | Thermal headroom (MW) | 16.4452 | 14.6115 | 14.024 | 10.8454 | 8.806 | 3.3728 | -0.71752 | -5.0039 | -10.1597 | -15.8209 | -21.3221 | -27.565 | -33.4375 | -39.1832 | -45.2912 | -51.0048 | -73.4163 | -82.8204 | -81.7181
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Consumer Transformation | Thermal headroom (MW) | 6.8575 | 6.5903 | 6.4508 | 6.1658 | 5.8615 | 5.5128 | 4.7554 | 4.0279 | 3.2872 | 2.1818 | 1.1626 | -0.060081 | -0.92372 | -1.8365 | -3.517 | -4.9512 | -10.3394 | -13.0846 | -13.5011
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Leading the Way | Thermal headroom (MW) | 6.853 | 6.6312 | 6.5507 | 6.3142 | 6.0459 | 5.7222 | 4.9588 | 4.2734 | 3.1598 | 2.3906 | 1.2674 | 0.25966 | -0.29799 | -1.3334 | -2.916 | -4.2961 | -7.5372 | -8.7215 | -7.6141
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Steady Progression | Thermal headroom (MW) | 6.9374 | 7.045 | 7.2965 | 7.4055 | 7.4929 | 7.5464 | 7.5798 | 7.5944 | 7.5959 | 7.5325 | 7.248 | 6.8582 | 6.5753 | 6.2498 | 5.7218 | 4.9537 | 2.9525 | 0.60408 | -0.19706
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | System Transformation | Thermal headroom (MW) | 6.8973 | 6.9732 | 7.1978 | 7.25 | 7.3037 | 7.3054 | 7.2551 | 7.1824 | 7.0231 | 6.7845 | 6.2428 | 5.2308 | 4.7515 | 4.2457 | 3.4079 | 2.8428 | 0.44029 | -1.049 | -1.4246
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | WPD Best View | Thermal headroom (MW) | 6.8575 | 6.5903 | 6.4508 | 6.1658 | 5.8615 | 5.5128 | 4.7554 | 4.0279 | 3.2872 | 2.1818 | 1.1626 | -0.060081 | -0.92372 | -1.8365 | -3.517 | -4.9512 | -10.3394 | -13.0846 | -13.5011
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Consumer Transformation | Thermal headroom (MW) | 5.2946 | 5.0779 | 5.139 | 4.0031 | 3.4841 | 2.8488 | 2.4394 | 1.9266 | 1.3948 | 0.87139 | 0.36788 | -0.47848 | -0.87415 | -1.1759 | -1.7405 | -1.8633 | -4.3022 | -5.0638 | -4.6556
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Leading the Way | Thermal headroom (MW) | 5.2634 | 4.989 | 5.0372 | 3.1515 | 2.9911 | 2.24 | 1.7752 | 1.3206 | 0.69096 | 0.23109 | -0.21255 | -0.86907 | -1.0239 | -1.0511 | -1.2946 | -1.4778 | -2.8042 | -2.8054 | -1.5796
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Steady Progression | Thermal headroom (MW) | 5.3451 | 5.3047 | 5.5188 | 4.8383 | 4.8773 | 4.6228 | 4.5501 | 4.4621 | 4.3192 | 4.1798 | 3.9951 | 3.4249 | 3.194 | 2.9249 | 2.6493 | 2.3353 | 0.5285 | -1.037 | -1.3797
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | System Transformation | Thermal headroom (MW) | 5.3206 | 5.2059 | 5.3919 | 4.3783 | 4.3935 | 4.0179 | 3.9341 | 3.7314 | 3.1247 | 2.8463 | 2.5358 | 2.1972 | 1.8401 | 1.098 | 0.70887 | 0.35541 | -1.7381 | -2.5039 | -2.3266
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | WPD Best View | Thermal headroom (MW) | 5.3102 | 5.1879 | 5.3513 | 4.3129 | 4.2739 | 3.8573 | 3.7241 | 3.4711 | 2.8162 | 2.5068 | 2.1836 | 1.8662 | 1.5693 | 0.9324 | 0.6851 | 0.48233 | -1.3492 | -2.0931 | -1.9308
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Consumer Transformation | Thermal headroom (MW) | 7.9766 | 7.948 | 8.0533 | 8.0021 | 7.9638 | 7.875 | 7.6717 | 7.4767 | 7.1258 | 6.7223 | 6.3242 | 5.9162 | 5.514 | 5.0089 | 4.4614 | 3.9185 | 2.0504 | 1.5836 | 1.8844
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Leading the Way | Thermal headroom (MW) | 7.9613 | 7.9484 | 8.0865 | 8.056 | 8.0305 | 7.9449 | 7.7516 | 7.5158 | 7.1246 | 6.699 | 6.3026 | 5.9253 | 5.4134 | 4.8426 | 4.331 | 3.8673 | 2.7775 | 3.0592 | 4.2167
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Steady Progression | Thermal headroom (MW) | 8.0122 | 8.1304 | 8.3864 | 8.496 | 8.6117 | 8.7259 | 8.8101 | 8.9053 | 8.9545 | 9.0143 | 8.9814 | 8.7974 | 8.5794 | 8.3157 | 8.0312 | 7.7243 | 6.1227 | 5.3166 | 5.1735
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | System Transformation | Thermal headroom (MW) | 7.9993 | 8.1037 | 8.3365 | 8.4155 | 8.4954 | 8.5883 | 8.6586 | 8.6625 | 8.6725 | 8.587 | 8.331 | 7.9872 | 7.6105 | 7.1616 | 6.7273 | 6.3141 | 4.7716 | 4.6436 | 5.0205
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | WPD Best View | Thermal headroom (MW) | 7.9818 | 7.995 | 8.136 | 8.1182 | 8.0983 | 8.062 | 7.8947 | 7.7432 | 7.5099 | 7.2438 | 6.9266 | 6.4899 | 6.0585 | 5.5588 | 5.0428 | 4.5254 | 2.5246 | 1.8746 | 2.1603
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Consumer Transformation | Thermal headroom (MW) | 3.4951 | 3.1766 | 2.9775 | 2.6719 | 2.3066 | 0.84077 | 0.18241 | -0.50015 | -1.2552 | -2.1118 | -3.0022 | -3.9115 | -4.7495 | -5.4476 | -5.9962 | -6.4272 | -8.2367 | -9.0816 | -8.9942
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Leading the Way | Thermal headroom (MW) | 3.4858 | 3.1221 | 2.9255 | 2.586 | 2.2065 | 0.41024 | -0.27088 | -0.98011 | -1.7902 | -2.6929 | -3.6887 | -4.4373 | -5.0505 | -5.4992 | -5.7639 | -6.0999 | -7.858 | -7.6609 | -6.527
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Steady Progression | Thermal headroom (MW) | 3.5513 | 3.4123 | 3.3976 | 3.3013 | 3.177 | 2.3605 | 2.1517 | 1.9113 | 1.5783 | 1.1991 | 0.77512 | 0.30387 | -0.22345 | -0.81221 | -1.4487 | -2.0922 | -5.6026 | -7.5921 | -8.2233
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | System Transformation | Thermal headroom (MW) | 3.5353 | 3.3337 | 3.2938 | 3.1507 | 2.9822 | 1.8487 | 1.5534 | 1.2228 | 0.79388 | 0.21539 | -0.41507 | -1.1324 | -1.9231 | -2.7689 | -3.6775 | -4.5618 | -7.5222 | -8.1321 | -7.9905
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | WPD Best View | Thermal headroom (MW) | 3.5048 | 3.2364 | 3.091 | 2.8452 | 2.5404 | 1.1801 | 0.64259 | 0.082279 | -0.56775 | -1.3261 | -2.1043 | -2.9586 | -3.7804 | -4.5174 | -5.1468 | -5.674 | -7.2319 | -7.8471 | -7.7153
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Consumer Transformation | Thermal headroom (MW) | 6.9761 | 5.7508 | 4.9426 | 3.9985 | 2.9473 | 1.3616 | -0.4306 | -2.1905 | -3.8614 | -5.7664 | -7.287 | -9.0148 | -10.5647 | -11.8507 | -13.8132 | -15.9893 | -24.6154 | -27.7183 | -27.5022
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Leading the Way | Thermal headroom (MW) | 6.837 | 5.3667 | 4.5356 | 3.5056 | 2.3622 | 0.74293 | -1.068 | -2.702 | -4.7336 | -6.2449 | -7.5952 | -8.5633 | -9.2616 | -10.5075 | -12.1702 | -14.0265 | -18.6381 | -19.6973 | -17.4227
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Steady Progression | Thermal headroom (MW) | 7.1867 | 6.8163 | 6.882 | 6.6752 | 6.4135 | 6.0882 | 5.9612 | 5.745 | 5.5345 | 5.3093 | 4.9168 | 4.3832 | 3.7733 | 3.107 | 2.3704 | 1.2463 | -2.8758 | -6.0718 | -6.7301
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | System Transformation | Thermal headroom (MW) | 7.0377 | 6.4111 | 6.2402 | 5.9182 | 5.5079 | 4.9854 | 4.5771 | 4.1592 | 3.7375 | 3.1713 | 2.4474 | 1.2621 | 0.32528 | -0.6692 | -1.6695 | -2.6064 | -6.7199 | -8.1816 | -7.8644
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | WPD Best View | Thermal headroom (MW) | 6.9813 | 5.7598 | 4.9629 | 4.0285 | 2.9915 | 1.4208 | -0.35334 | -2.0604 | -3.7071 | -5.5966 | -7.1109 | -8.8493 | -10.433 | -11.7718 | -13.683 | -15.8486 | -24.5024 | -27.6311 | -27.3905
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Consumer Transformation | Thermal headroom (MW) | 9.6831 | 9.5539 | 9.5619 | 8.8657 | 8.8078 | 8.6979 | 8.4833 | 8.1926 | 7.8992 | 7.623 | 7.2151 | 6.6194 | 6.0066 | 5.4333 | 4.84 | 4.2684 | 2.1859 | 1.8325 | 2.2034
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Leading the Way | Thermal headroom (MW) | 10.617 | 10.3748 | 10.4942 | 9.474 | 9.4408 | 9.3471 | 9.1437 | 8.8955 | 8.5488 | 8.3048 | 8.075 | 7.7925 | 7.1582 | 6.5461 | 5.9882 | 5.468 | 4.2207 | 4.6281 | 5.9222
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Steady Progression | Thermal headroom (MW) | 9.9587 | 9.939 | 10.088 | 9.6257 | 9.6361 | 9.6183 | 9.533 | 9.4581 | 9.3847 | 9.2652 | 9.1203 | 8.9356 | 8.7715 | 8.5928 | 8.4199 | 8.23 | 6.6891 | 4.8285 | 4.7116
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | System Transformation | Thermal headroom (MW) | 9.7035 | 9.6373 | 9.7334 | 9.1171 | 9.1531 | 9.1496 | 9.1216 | 9.0011 | 8.865 | 8.7092 | 8.4609 | 8.2145 | 7.9424 | 7.6763 | 7.3866 | 6.9452 | 4.384 | 3.5921 | 4.1064
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | WPD Best View | Thermal headroom (MW) | 9.6983 | 9.6283 | 9.7131 | 9.0871 | 9.1089 | 9.0904 | 9.0443 | 8.8826 | 8.7108 | 8.5395 | 8.2848 | 8.049 | 7.8107 | 7.5974 | 7.2653 | 6.8045 | 4.2709 | 3.5049 | 3.9948
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Consumer Transformation | Thermal headroom (MW) | 23.6551 | 22.9907 | 22.6474 | 21.9217 | 20.8512 | 19.5625 | 17.4093 | 15.423 | 13.1497 | 9.635 | 6.8382 | 2.9002 | -0.89072 | -4.7349 | -9.3425 | -13.0866 | -29.9235 | -37.1395 | -37.6546
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Leading the Way | Thermal headroom (MW) | 23.5329 | 22.8409 | 22.6671 | 21.677 | 20.9382 | 19.6731 | 17.462 | 15.4439 | 12.0949 | 9.3618 | 6.2277 | 2.8547 | -0.45262 | -4.0211 | -8.3469 | -12.3234 | -22.8184 | -25.1088 | -21.1303
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Steady Progression | Thermal headroom (MW) | 23.9293 | 24.1902 | 24.9192 | 25.1793 | 25.4353 | 25.5899 | 25.7662 | 25.8674 | 25.9241 | 25.9242 | 25.7598 | 25.057 | 24.5529 | 23.7147 | 22.44 | 20.2713 | 12.3184 | 2.5126 | -0.10604
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | System Transformation | Thermal headroom (MW) | 23.7316 | 23.8906 | 24.4163 | 24.5433 | 24.821 | 24.8518 | 24.8177 | 24.7016 | 24.1467 | 23.6805 | 23.0102 | 21.1772 | 20.0568 | 18.1576 | 15.96 | 14.2079 | 1.2492 | -6.2114 | -6.9817
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | WPD Best View | Thermal headroom (MW) | 23.6394 | 22.9778 | 22.6093 | 21.8657 | 20.7862 | 19.4477 | 17.3088 | 15.3041 | 13.0197 | 9.4743 | 6.6181 | 2.5994 | -1.2677 | -5.1512 | -9.8015 | -13.5778 | -30.2274 | -37.161 | -37.4381
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Consumer Transformation | Thermal headroom (MW) | -2.9322 | -3.2899 | -3.454 | -3.8153 | -4.1126 | -4.7587 | -5.6571 | -6.4815 | -7.4371 | -8.8849 | -10.1058 | -11.6388 | -13.1659 | -14.5861 | -16.0852 | -17.5218 | -23.4214 | -25.7131 | -25.6883
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Leading the Way | Thermal headroom (MW) | -2.9815 | -3.3603 | -3.4517 | -3.7809 | -4.0333 | -4.6902 | -5.6038 | -6.4186 | -7.7029 | -8.8625 | -10.1712 | -11.3504 | -12.5758 | -13.7711 | -14.9464 | -16.3174 | -19.7259 | -20.4051 | -18.6354
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Steady Progression | Thermal headroom (MW) | -2.7883 | -2.7253 | -2.4069 | -2.2964 | -2.1844 | -2.1186 | -2.051 | -1.9926 | -1.9129 | -1.9105 | -2.0073 | -2.1361 | -2.3308 | -2.5606 | -2.926 | -3.7019 | -6.4566 | -9.8668 | -10.4862
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | System Transformation | Thermal headroom (MW) | -2.8825 | -2.8738 | -2.6297 | -2.5333 | -2.4427 | -2.474 | -2.5083 | -2.5246 | -2.6024 | -2.7591 | -3.0973 | -3.7648 | -4.1371 | -4.6456 | -5.2386 | -5.8922 | -10.23 | -12.5995 | -12.5507
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | WPD Best View | Thermal headroom (MW) | -2.9322 | -3.2899 | -3.454 | -3.8153 | -4.1126 | -4.7587 | -5.6571 | -6.4815 | -7.4371 | -8.8849 | -10.1058 | -11.6388 | -13.1659 | -14.5861 | -16.0852 | -17.5218 | -23.4214 | -25.7131 | -25.6883
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Consumer Transformation | Thermal headroom (MW) | 5.5312 | 5.3252 | 5.2116 | 4.9661 | 4.3143 | 3.7779 | 2.8689 | 2.0451 | 1.0688 | -0.34341 | -1.4844 | -3.3621 | -4.9035 | -6.7393 | -9.2907 | -10.8404 | -18.1639 | -21.2962 | -21.4188
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Leading the Way | Thermal headroom (MW) | 5.4699 | 5.2413 | 5.1525 | 4.5585 | 4.242 | 3.7236 | 2.7897 | 1.9302 | 0.56511 | -0.59015 | -1.8907 | -3.613 | -5.0154 | -6.8076 | -9.43 | -11.0596 | -15.4006 | -16.3395 | -14.6303
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Steady Progression | Thermal headroom (MW) | 5.6234 | 5.7257 | 5.9799 | 6.0402 | 6.121 | 6.14 | 6.1723 | 6.1968 | 6.1462 | 6.0933 | 6.013 | 5.4433 | 5.2486 | 4.7608 | 4.0304 | 3.1738 | -0.75094 | -5.3232 | -6.6893
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | System Transformation | Thermal headroom (MW) | 5.5375 | 5.6023 | 5.7879 | 5.7596 | 5.8468 | 5.8636 | 5.8588 | 5.8 | 5.2764 | 5.0407 | 4.7566 | 4.0232 | 3.5077 | 2.3212 | 0.96257 | 0.15007 | -6.1252 | -9.6783 | -10.1096
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | WPD Best View | Thermal headroom (MW) | 5.5133 | 5.3105 | 5.1682 | 4.9025 | 4.2404 | 3.6472 | 2.7544 | 1.9098 | 0.92083 | -0.52624 | -1.7349 | -3.7043 | -5.3325 | -7.213 | -9.8129 | -11.3993 | -18.5098 | -21.3206 | -21.1725
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Consumer Transformation | Thermal headroom (MW) | 8.1568 | 7.9723 | 7.87 | 7.6658 | 7.434 | 7.1466 | 6.5685 | 6.0218 | 5.4276 | 4.4212 | 3.6735 | 2.7058 | 1.6131 | 0.6255 | -0.42567 | -1.5277 | -6.5594 | -8.8606 | -9.2091
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Leading the Way | Thermal headroom (MW) | 8.13 | 7.9517 | 7.9273 | 7.7386 | 7.5104 | 7.2358 | 6.6371 | 6.0844 | 5.0832 | 4.3617 | 3.5045 | 2.6786 | 1.7036 | 0.77736 | -0.18334 | -1.457 | -4.9139 | -5.7126 | -4.7306
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Steady Progression | Thermal headroom (MW) | 8.2299 | 8.3328 | 8.5587 | 8.663 | 8.7484 | 8.8225 | 8.9036 | 8.9343 | 8.9701 | 9.0068 | 8.9873 | 8.8978 | 8.7401 | 8.5406 | 8.2383 | 7.5372 | 5.4768 | 2.7522 | 1.9567
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | System Transformation | Thermal headroom (MW) | 8.1855 | 8.264 | 8.4167 | 8.4842 | 8.5953 | 8.6269 | 8.6227 | 8.5796 | 8.548 | 8.4285 | 8.2839 | 7.7049 | 7.3784 | 6.9776 | 6.5061 | 6.0423 | 2.5094 | 0.3568 | 0.0072427
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | WPD Best View | Thermal headroom (MW) | 8.1568 | 7.9723 | 7.87 | 7.6658 | 7.434 | 7.1466 | 6.5685 | 6.0218 | 5.4276 | 4.4212 | 3.6735 | 2.7058 | 1.6131 | 0.6255 | -0.42567 | -1.5277 | -6.5594 | -8.8606 | -9.2091
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Consumer Transformation | Thermal headroom (MW) | 10.5064 | 9.6033 | 8.2603 | 6.8807 | 5.1215 | 3.4469 | 1.369 | -0.72833 | -2.8138 | -5.0894 | -7.5675 | -9.8789 | -12.609 | -14.9522 | -17.5475 | -20.0476 | -29.509 | -31.7395 | -30.6351
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Leading the Way | Thermal headroom (MW) | 10.2319 | 9.086 | 8.1596 | 6.6156 | 4.6384 | 3.0044 | 0.47222 | -1.3928 | -3.6054 | -6.3112 | -8.6228 | -11.1617 | -13.4767 | -16.021 | -18.5884 | -20.947 | -26.8275 | -25.5527 | -20.5736
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Steady Progression | Thermal headroom (MW) | 10.7927 | 11.095 | 11.1974 | 10.5006 | 10.1371 | 10.2555 | 10.2039 | 9.908 | 9.6179 | 9.1435 | 8.4725 | 7.3588 | 6.1365 | 4.4483 | 2.9342 | 1.2276 | -9.6318 | -17.8006 | -20.2054
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | System Transformation | Thermal headroom (MW) | 10.5981 | 10.5857 | 10.0596 | 9.4728 | 8.7202 | 8.7258 | 7.9794 | 7.207 | 6.3348 | 5.2538 | 3.4839 | 1.6412 | -0.74939 | -3.0389 | -5.6889 | -8.4253 | -19.7635 | -23.4457 | -22.7618
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | WPD Best View | Thermal headroom (MW) | 10.5721 | 10.3326 | 9.6217 | 8.8425 | 7.8709 | 7.4967 | 6.4301 | 5.4041 | 4.1153 | 2.5778 | 0.67947 | -1.0975 | -3.1563 | -5.0641 | -7.4673 | -9.7871 | -19.8708 | -24.095 | -23.4096
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Consumer Transformation | Thermal headroom (MW) | 2.6082 | 2.0546 | 0.67133 | 0.25798 | -0.21197 | -1.0363 | -2.2064 | -3.2696 | -4.0557 | -4.8754 | -6.1019 | -7.1768 | -8.5849 | -9.5594 | -10.9814 | -12.3985 | -16.7333 | -18.0401 | -18.063
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Leading the Way | Thermal headroom (MW) | 2.3099 | 1.3996 | 0.42931 | 0.015108 | -0.47918 | -1.3502 | -2.9618 | -3.725 | -4.5058 | -5.7202 | -6.6004 | -7.7585 | -8.6083 | -9.846 | -11.0394 | -11.777 | -14.2119 | -14.5029 | -12.6746
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Steady Progression | Thermal headroom (MW) | 2.7105 | 2.8076 | 2.3787 | 1.8186 | 1.8316 | 1.8099 | 1.6542 | 1.6247 | 1.6554 | 1.5652 | 1.5453 | 1.3528 | 1.1735 | 0.5824 | 0.32372 | -0.027116 | -3.3977 | -7.1714 | -8.03
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | System Transformation | Thermal headroom (MW) | 2.6173 | 2.4027 | 1.3846 | 1.368 | 1.2885 | 1.2103 | 0.71734 | 0.58066 | 0.38217 | 0.21429 | -0.42763 | -0.75418 | -1.5693 | -2.0255 | -2.9487 | -3.9305 | -8.6921 | -11.1379 | -11.28
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | WPD Best View | Thermal headroom (MW) | 2.6087 | 2.3176 | 1.2318 | 1.146 | 0.98666 | 0.82775 | 0.28208 | 0.081638 | -0.18647 | -0.43792 | -1.1462 | -1.5517 | -2.409 | -2.8709 | -3.8487 | -4.8788 | -9.4754 | -11.5887 | -11.6738
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Consumer Transformation | Thermal headroom (MW) | 3.8289 | 3.6206 | 3.458 | 2.9166 | 2.338 | 2.0459 | 1.7303 | 1.3687 | 0.92968 | 0.39204 | -0.12333 | -0.63977 | -1.2169 | -1.8098 | -2.4346 | -3.0535 | -5.042 | -5.4248 | -5.0374
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Leading the Way | Thermal headroom (MW) | 3.811 | 3.6158 | 3.4854 | 2.8473 | 2.1592 | 1.8952 | 1.5173 | 1.1484 | 0.64613 | 0.058027 | -0.51574 | -1.1138 | -1.7421 | -2.4419 | -3.1286 | -3.6829 | -4.7585 | -4.2548 | -3.1484
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Steady Progression | Thermal headroom (MW) | 3.9092 | 3.9638 | 4.0673 | 3.8834 | 3.6503 | 3.6651 | 3.6736 | 3.5935 | 3.5317 | 3.4479 | 3.2463 | 2.9297 | 2.5665 | 2.1701 | 1.7397 | 1.268 | -1.3503 | -3.107 | -3.7285
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | System Transformation | Thermal headroom (MW) | 3.8618 | 3.8966 | 3.9274 | 3.5878 | 3.2159 | 3.212 | 3.0719 | 2.8693 | 2.6871 | 2.4151 | 2.0023 | 1.4775 | 0.90689 | 0.27282 | -0.35366 | -1.0261 | -3.448 | -4.15 | -3.9119
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | WPD Best View | Thermal headroom (MW) | 3.8552 | 3.8201 | 3.7975 | 3.3843 | 2.9638 | 2.8736 | 2.673 | 2.409 | 2.0659 | 1.5992 | 1.1413 | 0.65051 | 0.19166 | -0.36309 | -0.89515 | -1.3867 | -3.6133 | -4.608 | -4.3527
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Consumer Transformation | Thermal headroom (MW) | 10.7083 | 10.6215 | 10.6278 | 10.5364 | 10.2377 | 9.8323 | 9.3541 | 8.8589 | 8.312 | 7.7707 | 7.2852 | 6.839 | 6.3501 | 5.9219 | 5.6076 | 5.3554 | 3.3238 | 2.8988 | 3.2422
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Leading the Way | Thermal headroom (MW) | 10.6984 | 10.6194 | 10.6574 | 10.5694 | 10.2638 | 9.8797 | 9.3977 | 8.9126 | 8.3494 | 7.7793 | 7.2941 | 6.8315 | 6.3983 | 6.1138 | 5.768 | 5.1368 | 3.508 | 3.9854 | 5.2424
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Steady Progression | Thermal headroom (MW) | 10.7602 | 10.8613 | 11.0555 | 11.0979 | 11.122 | 11.2057 | 11.2469 | 11.1445 | 10.9866 | 10.7886 | 10.5552 | 10.2379 | 9.8918 | 9.4768 | 9.0439 | 8.5729 | 5.7396 | 4.0569 | 3.5512
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | System Transformation | Thermal headroom (MW) | 10.7293 | 10.8003 | 10.9587 | 10.971 | 10.9365 | 10.9922 | 10.8988 | 10.6581 | 10.3507 | 9.9846 | 9.559 | 9.0403 | 8.452 | 7.8135 | 7.1649 | 6.5461 | 3.9075 | 3.4695 | 3.76
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | WPD Best View | Thermal headroom (MW) | 10.7233 | 10.7588 | 10.8866 | 10.8905 | 10.8005 | 10.728 | 10.5014 | 10.186 | 9.8149 | 9.408 | 8.9832 | 8.5162 | 8.058 | 7.6092 | 7.0563 | 6.5441 | 4.5077 | 3.8478 | 4.0829
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Consumer Transformation | Thermal headroom (MW) | 3.5176 | 1.795 | 0.34225 | -1.7104 | -4.5197 | -7.2066 | -11.0668 | -14.6084 | -18.655 | -24.8287 | -29.1058 | -34.6347 | -40.1926 | -45.0838 | -50.8224 | -55.496 | -78.1554 | -86.9032 | -86.3002
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Leading the Way | Thermal headroom (MW) | 3.3229 | 1.7792 | 0.44548 | -2.2073 | -4.6498 | -7.3364 | -11.3318 | -15.0376 | -21.1687 | -25.7674 | -30.3211 | -35.7004 | -40.2115 | -45.3995 | -49.8797 | -56.2003 | -68.8331 | -69.2044 | -62.3695
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Steady Progression | Thermal headroom (MW) | 3.9521 | 4.2525 | 4.5972 | 4.3958 | 4.1785 | 4.0491 | 3.6791 | 3.1537 | 2.0481 | 1.1392 | -0.10081 | -2.2904 | -4.3609 | -6.8686 | -9.4533 | -14.15 | -32.2304 | -48.9405 | -53.6536
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | System Transformation | Thermal headroom (MW) | 3.7642 | 3.7215 | 3.7517 | 3.1884 | 2.6348 | 1.7702 | 0.4942 | -0.69426 | -2.8032 | -4.6543 | -6.9171 | -11.7202 | -15.2552 | -19.7758 | -24.1812 | -28.6832 | -51.0537 | -61.4779 | -62.2699
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | WPD Best View | Thermal headroom (MW) | 3.5274 | 1.8256 | 0.41518 | -1.5958 | -4.3589 | -6.9924 | -10.7854 | -14.2577 | -18.231 | -24.3189 | -28.4928 | -33.99 | -39.6166 | -44.5474 | -50.1302 | -54.7257 | -77.2236 | -86.2026 | -85.7194
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Consumer Transformation | Thermal headroom (MW) | 6.6551 | 6.0296 | 5.0317 | 4.079 | 2.7703 | 2.0533 | 1.0163 | -0.058157 | -1.2378 | -2.41 | -3.5451 | -5.0289 | -6.2013 | -7.056 | -8.683 | -10.1984 | -16.7478 | -18.619 | -18.0638
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Leading the Way | Thermal headroom (MW) | 6.3505 | 5.9854 | 4.848 | 3.382 | 2.3358 | 1.6105 | 0.55928 | -0.54955 | -1.7513 | -2.9496 | -4.0274 | -5.2506 | -6.1248 | -7.4226 | -9.2163 | -10.4954 | -14.2017 | -14.2579 | -12.0478
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Steady Progression | Thermal headroom (MW) | 6.8108 | 6.8884 | 6.3635 | 6.0353 | 5.7679 | 5.6904 | 5.5276 | 5.2754 | 4.9756 | 4.6164 | 4.2117 | 3.2662 | 2.5374 | 1.8266 | 1.0591 | 0.25999 | -4.494 | -8.5037 | -9.836
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | System Transformation | Thermal headroom (MW) | 6.7276 | 6.4738 | 5.9325 | 5.3886 | 4.9314 | 4.7891 | 4.4168 | 3.93 | 2.9789 | 2.2957 | 1.565 | 0.68279 | -0.46227 | -1.9009 | -2.9874 | -4.0087 | -9.2627 | -11.0965 | -10.9099
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | WPD Best View | Thermal headroom (MW) | 6.6708 | 6.0807 | 5.1551 | 4.2722 | 3.0396 | 2.4083 | 1.4789 | 0.51184 | -0.55966 | -1.6618 | -2.722 | -4.1924 | -5.4085 | -6.3893 | -7.7774 | -9.2025 | -15.6998 | -17.7109 | -17.1576
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Consumer Transformation | Thermal headroom (MW) | 6.3175 | 6.2226 | 6.1194 | 5.9824 | 5.8014 | 5.5943 | 5.2624 | 4.9594 | 4.5875 | 3.7633 | 3.3188 | 2.7452 | 2.1098 | 1.5231 | 0.88246 | 0.27082 | -2.3144 | -3.4445 | -3.5454
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Leading the Way | Thermal headroom (MW) | 6.3304 | 6.2363 | 6.1895 | 6.047 | 5.8477 | 5.6672 | 5.3065 | 4.9945 | 4.2347 | 3.7159 | 3.1896 | 2.5989 | 2.0107 | 1.3731 | 0.79115 | -0.10367 | -1.481 | -1.5731 | -1.0702
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Steady Progression | Thermal headroom (MW) | 6.3681 | 6.3899 | 6.4632 | 6.4781 | 6.5008 | 6.4997 | 6.4904 | 6.4508 | 6.3804 | 6.3085 | 6.2047 | 6.0756 | 5.933 | 5.7262 | 5.5016 | 4.889 | 3.0292 | 0.74761 | 0.18403
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | System Transformation | Thermal headroom (MW) | 6.355 | 6.3721 | 6.4119 | 6.4238 | 6.4349 | 6.3856 | 6.285 | 6.1754 | 6.0465 | 5.8919 | 5.7197 | 5.1175 | 4.7934 | 4.4392 | 4.0197 | 3.5673 | 0.83841 | -0.75067 | -1.0763
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | WPD Best View | Thermal headroom (MW) | 6.3175 | 6.2226 | 6.1194 | 5.9824 | 5.8014 | 5.5943 | 5.2624 | 4.9594 | 4.5875 | 3.7633 | 3.3188 | 2.7452 | 2.1098 | 1.5231 | 0.88246 | 0.27082 | -2.3144 | -3.4445 | -3.5454
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Consumer Transformation | Thermal headroom (MW) | 8.0274 | 7.8534 | 7.6077 | 7.2451 | 6.8713 | 6.5152 | 6.0305 | 5.5618 | 5.0559 | 4.1742 | 3.6869 | 3.1183 | 2.5574 | 1.9489 | 1.5338 | 1.1806 | -1.3095 | -2.5807 | -2.6625
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Leading the Way | Thermal headroom (MW) | 8.0166 | 7.8618 | 7.6154 | 7.2079 | 6.8046 | 6.462 | 5.9647 | 5.4924 | 4.5889 | 4.0362 | 3.5321 | 3.0121 | 2.5645 | 2.0613 | 1.8371 | 0.94824 | -0.64962 | -0.74012 | -0.23733
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Steady Progression | Thermal headroom (MW) | 8.0705 | 8.0668 | 8.0314 | 7.901 | 7.7797 | 7.6999 | 7.5767 | 7.4368 | 7.2854 | 7.0911 | 6.8426 | 6.5755 | 6.2617 | 5.8332 | 5.4593 | 4.6755 | 2.3692 | 0.6714 | 0.16837
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | System Transformation | Thermal headroom (MW) | 8.0533 | 8.0302 | 7.9517 | 7.7544 | 7.5724 | 7.4403 | 7.2588 | 7.0415 | 6.7663 | 6.4591 | 6.104 | 5.3237 | 4.8491 | 4.2071 | 3.6517 | 3.0578 | 0.5106 | -0.38337 | -0.68687
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | WPD Best View | Thermal headroom (MW) | 8.0274 | 7.8534 | 7.6077 | 7.2451 | 6.8713 | 6.5152 | 6.0305 | 5.5618 | 5.0559 | 4.1742 | 3.6869 | 3.1183 | 2.5574 | 1.9489 | 1.5338 | 1.1806 | -1.3095 | -2.5807 | -2.6625
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Consumer Transformation | Thermal headroom (MW) | -11.0513 | -11.0471 | -10.8657 | -10.9381 | -11.0616 | -11.4622 | -11.8982 | -12.2785 | -12.8086 | -13.2512 | -13.6855 | -14.0987 | -14.4559 | -14.7003 | -14.8344 | -14.8768 | -15.2408 | -14.7629 | -13.6073
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Leading the Way | Thermal headroom (MW) | -11.0617 | -11.0464 | -10.8432 | -10.9099 | -11.0222 | -11.4637 | -11.9409 | -12.3339 | -12.9547 | -13.4501 | -13.8861 | -14.1931 | -14.4066 | -14.4159 | -14.2697 | -14.2256 | -13.5916 | -12.5941 | -11.0957
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Steady Progression | Thermal headroom (MW) | -10.9941 | -10.8302 | -10.4471 | -10.2776 | -10.1338 | -10.1319 | -10.1066 | -10.0942 | -10.1927 | -10.2618 | -10.3778 | -10.5501 | -10.7775 | -11.0434 | -11.3519 | -11.683 | -13.3216 | -13.6108 | -13.4957
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | System Transformation | Thermal headroom (MW) | -11.0213 | -10.8726 | -10.515 | -10.3751 | -10.2746 | -10.3594 | -10.4945 | -10.58 | -10.8528 | -11.0801 | -11.3579 | -11.7251 | -12.1461 | -12.6375 | -13.1211 | -13.5616 | -14.6076 | -14.3931 | -13.5746
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | WPD Best View | Thermal headroom (MW) | -11.0513 | -11.0471 | -10.8657 | -10.9381 | -11.0616 | -11.4622 | -11.8982 | -12.2785 | -12.8086 | -13.2512 | -13.6855 | -14.0987 | -14.4559 | -14.7003 | -14.8344 | -14.8768 | -15.2408 | -14.7629 | -13.7218
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Consumer Transformation | Thermal headroom (MW) | 12.8033 | 12.7962 | 12.8494 | 12.8275 | 12.7942 | 12.7357 | 12.6632 | 12.5993 | 12.5084 | 12.3236 | 12.1378 | 11.9807 | 11.8189 | 11.6574 | 11.4246 | 11.2219 | 10.4689 | 10.43 | 10.7491
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Leading the Way | Thermal headroom (MW) | 12.7959 | 12.799 | 12.874 | 12.8697 | 12.8567 | 12.7674 | 12.6842 | 12.6004 | 12.4897 | 12.3015 | 12.1145 | 11.9196 | 11.6625 | 11.4262 | 11.2021 | 10.9479 | 10.5388 | 10.951 | 11.6766
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Steady Progression | Thermal headroom (MW) | 12.8386 | 12.9201 | 13.0767 | 13.1637 | 13.2338 | 13.3169 | 13.3871 | 13.4742 | 13.5075 | 13.5637 | 13.5908 | 13.5234 | 13.4006 | 13.2617 | 13.1014 | 12.9228 | 11.9649 | 11.2342 | 11.0761
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | System Transformation | Thermal headroom (MW) | 12.8239 | 12.8976 | 13.0425 | 13.1207 | 13.1768 | 13.2474 | 13.2133 | 13.2014 | 13.2199 | 13.1922 | 13.1108 | 12.917 | 12.6767 | 12.4303 | 12.1728 | 11.9248 | 11.0707 | 10.8986 | 11.1746
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | WPD Best View | Thermal headroom (MW) | 12.8045 | 12.799 | 12.8554 | 12.8373 | 12.8088 | 12.7571 | 12.693 | 12.6397 | 12.5629 | 12.4232 | 12.2963 | 12.1621 | 11.958 | 11.8232 | 11.6156 | 11.4405 | 10.8127 | 10.6278 | 10.8854
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Consumer Transformation | Thermal headroom (MW) | 9.7845 | 9.4011 | 9.0615 | 8.6977 | 7.9043 | 7.2164 | 6.0975 | 5.2329 | 4.2094 | 3.2631 | 2.2427 | 0.5788 | -0.78724 | -2.0475 | -3.7223 | -4.9734 | -10.1349 | -11.9764 | -11.9307
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Leading the Way | Thermal headroom (MW) | 9.7677 | 9.3629 | 9.0366 | 8.3465 | 7.9107 | 7.21 | 6.063 | 5.103 | 4.0888 | 3.1068 | 2.021 | 0.5956 | -0.54991 | -1.681 | -3.1416 | -4.1201 | -7.1459 | -7.7552 | -6.0881
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Steady Progression | Thermal headroom (MW) | 9.859 | 9.8425 | 9.9122 | 9.9329 | 9.8839 | 9.8509 | 9.7166 | 9.5993 | 9.4995 | 9.3527 | 9.0778 | 8.3653 | 7.9598 | 7.5027 | 7.0207 | 6.4921 | 3.3131 | -0.51382 | -1.7405
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | System Transformation | Thermal headroom (MW) | 9.8232 | 9.7562 | 9.7143 | 9.6618 | 9.6041 | 9.5042 | 9.1066 | 8.9435 | 8.3013 | 7.9404 | 7.4887 | 6.9172 | 6.2772 | 5.2422 | 4.5688 | 3.9076 | -0.96191 | -3.715 | -3.8874
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | WPD Best View | Thermal headroom (MW) | 9.7845 | 9.4011 | 9.0615 | 8.6977 | 7.9043 | 7.2164 | 6.0975 | 5.2329 | 4.2094 | 3.2631 | 2.2427 | 0.5788 | -0.78724 | -2.0475 | -3.7223 | -4.9734 | -10.1349 | -11.9764 | -11.9307
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Consumer Transformation | Thermal headroom (MW) | 2.3433 | 1.8433 | 1.8141 | 1.7051 | 1.527 | 1.2306 | 0.84441 | 0.46316 | 0.077414 | -0.73417 | -1.2235 | -1.8635 | -2.8671 | -3.4968 | -4.5301 | -5.1686 | -8.5934 | -10.0015 | -10.2391
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Leading the Way | Thermal headroom (MW) | 2.3387 | 1.834 | 1.8485 | 1.7726 | 1.6025 | 1.2918 | 0.91548 | 0.51826 | -0.24985 | -0.7371 | -1.2842 | -2.1982 | -2.8014 | -3.7665 | -4.3012 | -5.1778 | -6.9896 | -7.3625 | -6.6381
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Steady Progression | Thermal headroom (MW) | 2.3751 | 2.4512 | 2.6172 | 2.6688 | 2.7233 | 2.7546 | 2.7902 | 2.7879 | 2.4064 | 2.3572 | 2.3423 | 2.2423 | 2.1095 | 1.9879 | 1.7941 | 1.2353 | -1.1785 | -3.5201 | -4.1944
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | System Transformation | Thermal headroom (MW) | 2.3533 | 2.3733 | 2.5099 | 2.5547 | 2.5756 | 2.2204 | 2.1692 | 2.1267 | 2.0262 | 1.9597 | 1.802 | 1.2216 | 0.96406 | 0.67384 | -0.051483 | -0.79966 | -4.0398 | -6.108 | -6.2297
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | WPD Best View | Thermal headroom (MW) | 2.3433 | 1.8433 | 1.8141 | 1.7051 | 1.527 | 1.2306 | 0.84441 | 0.46316 | 0.077414 | -0.73417 | -1.2235 | -1.8635 | -2.8671 | -3.4968 | -4.5301 | -5.1686 | -8.5934 | -10.0015 | -10.2391

## Generation headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | Limiting constraint | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Consumer Transformation | Headroom (MW) | N/A | 89.9078 | 89.9701 | 89.8353 | 89.6739 | 89.5128 | 89.3292 | 89.0657 | 88.7366 | 88.1402 | 87.3879 | 86.2984 | 85.228 | 84.1782 | 83.1305 | 82.0593 | 80.9091 | 74.2413 | 66.3746 | 59.0397
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Leading the Way | Headroom (MW) | N/A | 89.9659 | 90.0925 | 90.0677 | 89.8787 | 89.7517 | 89.5647 | 88.5149 | 88.3631 | 88.0473 | 87.8698 | 87.5139 | 86.8967 | 86.2208 | 85.4643 | 85.3356 | 85.204 | 82.7914 | 78.6587 | 72.5703
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | Steady Progression | Headroom (MW) | N/A | 89.864 | 89.8495 | 89.6311 | 89.4502 | 89.2864 | 89.0986 | 88.8827 | 88.7046 | 88.5085 | 88.3248 | 88.1338 | 87.9557 | 87.7682 | 87.5906 | 87.4107 | 87.2322 | 86.3002 | 85.3716 | 83.6186
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | System Transformation | Headroom (MW) | N/A | 89.9077 | 89.9697 | 89.8343 | 89.6723 | 89.5097 | 89.3239 | 89.149 | 88.9848 | 88.8073 | 88.6255 | 88.4268 | 88.1615 | 87.8997 | 87.6291 | 87.307 | 86.9831 | 85.4938 | 82.8963 | 78.8795
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | 52.42 | -1.5074 | WPD Best View | Headroom (MW) | N/A | 89.9089 | 89.9813 | 89.8623 | 89.7159 | 89.5704 | 89.3867 | 89.2239 | 88.8635 | 88.2832 | 87.5134 | 86.4345 | 85.3765 | 84.3396 | 83.291 | 82.2268 | 81.0623 | 74.3471 | 66.4361 | 59.0356
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Consumer Transformation | Headroom (MW) | N/A | 4.4575 | 4.4451 | 4.4179 | 4.4056 | 4.392 | 4.3785 | 4.3603 | 4.281 | 4.1941 | 4.1274 | 4.0491 | 3.9895 | 3.9192 | 3.8625 | 3.8003 | 3.7296 | 3.2783 | 2.6461 | 1.9726
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Leading the Way | Headroom (MW) | N/A | 4.4583 | 4.4461 | 4.4194 | 4.407 | 4.3939 | 4.3812 | 4.2231 | 4.2112 | 4.1925 | 4.1807 | 4.1589 | 4.1227 | 4.0834 | 4.0388 | 4.0326 | 4.0265 | 3.8914 | 3.4123 | 2.8399
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | Steady Progression | Headroom (MW) | N/A | 4.4569 | 4.4438 | 4.4159 | 4.4024 | 4.3879 | 4.3737 | 4.3592 | 4.3456 | 4.332 | 4.3182 | 4.3043 | 4.2909 | 4.2777 | 4.2648 | 4.2524 | 4.2405 | 4.1851 | 4.1292 | 4.0199
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | System Transformation | Headroom (MW) | N/A | 4.4575 | 4.445 | 4.4178 | 4.4055 | 4.3918 | 4.3782 | 4.3645 | 4.3514 | 4.3386 | 4.325 | 4.3119 | 4.299 | 4.2749 | 4.2543 | 4.2356 | 4.2207 | 4.1661 | 3.9528 | 3.5959
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | 52.4249 | -1.5052 | WPD Best View | Headroom (MW) | N/A | 4.4575 | 4.4451 | 4.4179 | 4.4056 | 4.392 | 4.3785 | 4.3603 | 4.281 | 4.1941 | 4.1274 | 4.0491 | 3.9895 | 3.9192 | 3.8625 | 3.8003 | 3.7296 | 3.2783 | 2.6461 | 1.9726
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Consumer Transformation | Headroom (MW) | N/A | 5.9894 | 5.9523 | 5.903 | 5.8394 | 5.7655 | 5.6693 | 5.5252 | 5.3766 | 5.2381 | 5.1021 | 4.9249 | 4.7737 | 4.6191 | 4.4635 | 4.3127 | 4.1595 | 3.3467 | 2.5377 | 1.7924
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Leading the Way | Headroom (MW) | N/A | 5.9425 | 5.9232 | 5.8903 | 5.8508 | 5.8045 | 5.781 | 5.7281 | 5.6598 | 5.5736 | 5.4954 | 5.3592 | 5.2727 | 5.1758 | 5.085 | 4.9872 | 4.8921 | 4.4488 | 4.0115 | 3.6079
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | Steady Progression | Headroom (MW) | N/A | 4.9762 | 4.9636 | 4.9501 | 4.9378 | 4.9254 | 4.9191 | 4.9071 | 4.8883 | 4.8716 | 4.8561 | 4.8311 | 4.8141 | 4.7903 | 4.7722 | 4.7474 | 4.7285 | 4.5996 | 4.4519 | 4.2894
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | System Transformation | Headroom (MW) | N/A | 5.7903 | 5.7744 | 5.7507 | 5.721 | 5.6875 | 5.6581 | 5.5923 | 5.5355 | 5.4744 | 5.4097 | 5.3359 | 5.2749 | 5.2054 | 5.1443 | 5.0749 | 5.0107 | 4.6723 | 4.3552 | 4.0563
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | 52.4098 | -1.502 | WPD Best View | Headroom (MW) | N/A | 5.6936 | 5.6582 | 5.6114 | 5.5509 | 5.4807 | 5.3892 | 5.2522 | 5.111 | 4.9793 | 4.8501 | 4.6816 | 4.5379 | 4.3909 | 4.243 | 4.0996 | 3.954 | 3.1814 | 2.4124 | 1.7039
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Consumer Transformation | Headroom (MW) | N/A | 15.2179 | 15.1856 | 15.1167 | 15.08 | 15.0438 | 15.005 | 14.9349 | 14.7941 | 14.6027 | 14.4063 | 14.2109 | 14.0386 | 13.8501 | 13.6651 | 13.4633 | 13.2396 | 11.9285 | 10.4939 | 9.3002
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Leading the Way | Headroom (MW) | N/A | 15.2204 | 15.1753 | 15.1081 | 15.0538 | 15.0188 | 14.9803 | 14.8314 | 14.7951 | 14.7272 | 14.6949 | 14.6266 | 14.5116 | 14.3884 | 14.2506 | 14.234 | 14.2168 | 13.8448 | 13.2449 | 12.1643
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | Steady Progression | Headroom (MW) | N/A | 15.2159 | 15.1823 | 15.112 | 15.0719 | 15.0344 | 14.9951 | 14.9431 | 14.9052 | 14.8631 | 14.8259 | 14.7848 | 14.7489 | 14.7116 | 14.6771 | 14.6437 | 14.6113 | 14.4424 | 14.2466 | 13.8924
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | System Transformation | Headroom (MW) | N/A | 15.2179 | 15.1855 | 15.1166 | 15.0798 | 15.0432 | 15.004 | 14.9612 | 14.9232 | 14.8835 | 14.8467 | 14.79 | 14.6668 | 14.5608 | 14.457 | 14.3727 | 14.2756 | 13.9031 | 13.4503 | 12.7455
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | 52.4305 | -1.4842 | WPD Best View | Headroom (MW) | N/A | 15.2179 | 15.1856 | 15.1167 | 15.08 | 15.0438 | 15.005 | 14.9673 | 14.7941 | 14.6027 | 14.4063 | 14.2109 | 14.0386 | 13.8501 | 13.6651 | 13.4633 | 13.2396 | 11.9285 | 10.4939 | 9.3002
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Consumer Transformation | Headroom (MW) | N/A | 6.8132 | 6.7976 | 6.7613 | 6.7414 | 6.7217 | 6.7024 | 6.6798 | 6.6615 | 6.597 | 6.531 | 6.4726 | 6.4166 | 6.3623 | 6.3059 | 6.2519 | 6.1884 | 5.7361 | 5.1355 | 4.5161
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Leading the Way | Headroom (MW) | N/A | 6.8132 | 6.7971 | 6.7608 | 6.739 | 6.7195 | 6.7003 | 6.5455 | 6.5272 | 6.5071 | 6.4909 | 6.4693 | 6.4384 | 6.4048 | 6.3666 | 6.3568 | 6.3469 | 6.213 | 5.8735 | 5.321
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | Steady Progression | Headroom (MW) | N/A | 6.8132 | 6.7965 | 6.76 | 6.7397 | 6.7198 | 6.7003 | 6.6797 | 6.6605 | 6.6422 | 6.6238 | 6.6053 | 6.5876 | 6.5699 | 6.5529 | 6.5363 | 6.5202 | 6.4457 | 6.3729 | 6.25
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | System Transformation | Headroom (MW) | N/A | 6.8132 | 6.7975 | 6.7612 | 6.7412 | 6.7214 | 6.7019 | 6.6822 | 6.6634 | 6.6462 | 6.6282 | 6.6105 | 6.5933 | 6.5764 | 6.5608 | 6.5462 | 6.5322 | 6.4627 | 6.265 | 5.9119
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | 52.4302 | -1.4843 | WPD Best View | Headroom (MW) | N/A | 6.8132 | 6.7976 | 6.7613 | 6.7414 | 6.7217 | 6.7024 | 6.6834 | 6.6651 | 6.597 | 6.531 | 6.4726 | 6.4166 | 6.3623 | 6.3059 | 6.2519 | 6.1884 | 5.7361 | 5.1355 | 4.5161
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Consumer Transformation | Headroom (MW) | N/A | 12.6687 | 12.6463 | 12.6038 | 12.5811 | 12.5577 | 12.5346 | 12.5096 | 12.4892 | 12.4653 | 12.4448 | 12.4215 | 12.4006 | 12.3807 | 12.3618 | 12.3463 | 12.3314 | 12.1533 | 11.728 | 11.2524
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Leading the Way | Headroom (MW) | N/A | 12.6687 | 12.6455 | 12.6034 | 12.58 | 12.5565 | 12.5335 | 12.5025 | 12.483 | 12.4584 | 12.4389 | 12.4149 | 12.3836 | 12.3505 | 12.3136 | 12.3005 | 12.2875 | 12.1468 | 11.9388 | 11.4578
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | Steady Progression | Headroom (MW) | N/A | 12.6685 | 12.646 | 12.6029 | 12.5795 | 12.5558 | 12.5323 | 12.5083 | 12.4866 | 12.4639 | 12.4419 | 12.4198 | 12.3985 | 12.3774 | 12.3569 | 12.3369 | 12.3174 | 12.2281 | 12.1435 | 12.0139
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | System Transformation | Headroom (MW) | N/A | 12.6687 | 12.6463 | 12.6036 | 12.5809 | 12.5572 | 12.5339 | 12.5105 | 12.4896 | 12.4674 | 12.4457 | 12.4245 | 12.4038 | 12.3836 | 12.3647 | 12.3465 | 12.3295 | 12.2561 | 12.1746 | 12.0371
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | 52.4375 | -1.5122 | WPD Best View | Headroom (MW) | N/A | 12.6687 | 12.6463 | 12.6038 | 12.5811 | 12.5577 | 12.5346 | 12.5119 | 12.4915 | 12.4703 | 12.4498 | 12.4302 | 12.4116 | 12.3941 | 12.378 | 12.3625 | 12.3476 | 12.1533 | 11.728 | 11.2524
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Consumer Transformation | Headroom (MW) | N/A | 17.8549 | 17.8648 | 17.8421 | 17.8321 | 17.826 | 17.7848 | 17.717 | 17.6841 | 17.6196 | 17.5842 | 17.4003 | 17.1217 | 16.8546 | 16.5848 | 16.3139 | 16.0244 | 14.3906 | 12.4552 | 10.656
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Leading the Way | Headroom (MW) | N/A | 17.8877 | 17.91 | 17.9215 | 17.9134 | 17.9318 | 17.8886 | 17.5964 | 17.5643 | 17.4837 | 17.4447 | 17.3431 | 17.1652 | 16.9736 | 16.7622 | 16.7325 | 16.7011 | 16.1454 | 15.5015 | 14.1045
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | Steady Progression | Headroom (MW) | N/A | 17.8304 | 17.8221 | 17.7724 | 17.7515 | 17.7372 | 17.6973 | 17.6491 | 17.6124 | 17.57 | 17.531 | 17.4881 | 17.4495 | 17.4053 | 17.3639 | 17.3201 | 17.2768 | 17.0582 | 16.8259 | 16.3599
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | System Transformation | Headroom (MW) | N/A | 17.8549 | 17.8647 | 17.8417 | 17.8314 | 17.8247 | 17.7827 | 17.7412 | 17.7062 | 17.6696 | 17.6296 | 17.5913 | 17.5525 | 17.5106 | 17.4692 | 17.43 | 17.3927 | 17.2398 | 16.664 | 15.6126
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | 52.4356 | -1.5071 | WPD Best View | Headroom (MW) | N/A | 17.856 | 17.876 | 17.8691 | 17.8741 | 17.8835 | 17.8423 | 17.8071 | 17.7753 | 17.7416 | 17.7048 | 17.5277 | 17.2593 | 17.0025 | 16.7292 | 16.4653 | 16.1615 | 14.4964 | 12.5166 | 10.6519
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Consumer Transformation | Headroom (MW) | N/A | 15.4704 | 15.4301 | 15.3574 | 15.3285 | 15.296 | 15.2594 | 15.1988 | 15.1648 | 15.0196 | 14.7101 | 14.3631 | 14.0483 | 13.7649 | 13.4754 | 13.179 | 12.8654 | 11.272 | 9.5582 | 8.0597
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Leading the Way | Headroom (MW) | N/A | 15.4716 | 15.4267 | 15.3568 | 15.3244 | 15.295 | 15.2604 | 15.0136 | 14.9833 | 14.9234 | 14.8989 | 14.8266 | 14.6707 | 14.4932 | 14.2923 | 14.2746 | 14.2557 | 13.6472 | 12.5248 | 11.2524
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | Steady Progression | Headroom (MW) | N/A | 15.4697 | 15.4292 | 15.3547 | 15.3208 | 15.2852 | 15.2468 | 15.2017 | 15.1656 | 15.1274 | 15.0929 | 15.0584 | 15.0256 | 14.9906 | 14.9575 | 14.9252 | 14.8942 | 14.737 | 14.5497 | 14.2121
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | System Transformation | Headroom (MW) | N/A | 15.4704 | 15.43 | 15.3573 | 15.3283 | 15.2955 | 15.2586 | 15.2171 | 15.1821 | 15.1456 | 15.1142 | 15.0866 | 15.057 | 15.0239 | 14.9763 | 14.8544 | 14.7358 | 14.2948 | 13.7336 | 12.8933
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | 52.4178 | -1.5118 | WPD Best View | Headroom (MW) | N/A | 15.4704 | 15.4301 | 15.3574 | 15.3285 | 15.296 | 15.2594 | 15.2208 | 15.1869 | 15.0196 | 14.7101 | 14.3631 | 14.0483 | 13.7649 | 13.4754 | 13.179 | 12.8654 | 11.272 | 9.5582 | 8.0597
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Consumer Transformation | Headroom (MW) | N/A | 62.118 | 61.9849 | 61.7126 | 61.5273 | 61.3425 | 61.2391 | 60.9413 | 60.7905 | 60.6297 | 60.4832 | 60.2227 | 60.0341 | 59.7759 | 59.5018 | 59.2925 | 59.0397 | 55.6843 | 52.3136 | 51.9124
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Leading the Way | Headroom (MW) | N/A | 62.1641 | 62.0376 | 61.7941 | 61.6586 | 61.502 | 61.5118 | 60.749 | 60.7882 | 60.6124 | 60.6043 | 60.1759 | 59.8683 | 59.5209 | 59.1382 | 59.0971 | 59.0505 | 66.776 | 64.3141 | 62.0294
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | Steady Progression | Headroom (MW) | N/A | 62.1118 | 61.9967 | 61.7607 | 61.6335 | 61.5131 | 61.4762 | 58.1589 | 55.0263 | 51.8928 | 48.7362 | 46.6298 | 44.5801 | 41.2948 | 39.0413 | 37.8065 | 37.72 | 37.2591 | 36.8011 | 35.8617
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | System Transformation | Headroom (MW) | N/A | 62.1336 | 62.0211 | 61.773 | 61.6304 | 61.4765 | 61.4385 | 61.2609 | 61.191 | 61.1064 | 61.0222 | 60.8806 | 60.7693 | 60.6828 | 60.5804 | 60.5104 | 60.4475 | 60.1259 | 59.4839 | 61.0818
Berkswell 132kV | Coventry South | Coventry South | Bulk Supply Point | 33 | 52.4057 | -1.539 | WPD Best View | Headroom (MW) | N/A | 62.118 | 61.9849 | 61.7126 | 61.5273 | 61.3425 | 61.2391 | 60.9747 | 60.8239 | 60.6983 | 60.5518 | 60.341 | 60.1836 | 60.0025 | 59.7837 | 59.4762 | 59.0991 | 55.6843 | 52.3136 | 51.9124
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Consumer Transformation | Headroom (MW) | N/A | 15.2341 | 15.1958 | 15.1208 | 15.0797 | 15.0394 | 14.9999 | 14.9411 | 14.9039 | 14.8474 | 14.8134 | 14.7531 | 14.7068 | 14.662 | 14.5868 | 14.4534 | 14.3053 | 13.369 | 12.2901 | 11.3493
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Leading the Way | Headroom (MW) | N/A | 15.2342 | 15.1884 | 15.1135 | 15.0634 | 15.0234 | 14.9843 | 14.894 | 14.8576 | 14.8078 | 14.7768 | 14.7302 | 14.6606 | 14.5857 | 14.5008 | 14.4877 | 14.4736 | 14.1944 | 13.8502 | 13.3487
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | Steady Progression | Headroom (MW) | N/A | 15.234 | 15.1956 | 15.1203 | 15.0777 | 15.0369 | 14.9967 | 14.9499 | 14.9109 | 14.87 | 14.8322 | 14.7925 | 14.7562 | 14.7195 | 14.685 | 14.6515 | 14.6193 | 14.4655 | 14.3032 | 14.016
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | System Transformation | Headroom (MW) | N/A | 15.2341 | 15.1957 | 15.1204 | 15.0791 | 15.0383 | 14.9981 | 14.9562 | 14.9173 | 14.8776 | 14.8402 | 14.8038 | 14.7686 | 14.7336 | 14.7027 | 14.6746 | 14.6488 | 14.5463 | 14.2627 | 13.6512
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | 52.4171 | -1.5434 | WPD Best View | Headroom (MW) | N/A | 15.2341 | 15.1958 | 15.1208 | 15.0797 | 15.0394 | 14.9999 | 14.9618 | 14.9246 | 14.8889 | 14.8549 | 14.8231 | 14.7942 | 14.7098 | 14.5868 | 14.4534 | 14.3053 | 13.369 | 12.2901 | 11.3493
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Consumer Transformation | Headroom (MW) | N/A | 14.892 | 14.8651 | 14.804 | 14.7743 | 14.7397 | 14.7126 | 14.6728 | 14.7471 | 14.8103 | 14.7946 | 14.7521 | 14.7253 | 14.606 | 14.4899 | 14.4785 | 14.4675 | 13.6859 | 12.6378 | 11.6333
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Leading the Way | Headroom (MW) | N/A | 14.9061 | 14.8767 | 14.8163 | 14.7833 | 14.7473 | 14.7212 | 14.4611 | 14.5768 | 14.6858 | 14.6872 | 14.5485 | 14.4695 | 14.3702 | 14.2481 | 14.2258 | 14.2012 | 13.8667 | 13.4795 | 13.0757
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | Steady Progression | Headroom (MW) | N/A | 14.8814 | 14.8539 | 14.7928 | 14.7623 | 14.7274 | 14.6964 | 14.6633 | 14.6946 | 14.7272 | 14.7074 | 14.6852 | 14.6658 | 14.6467 | 14.6287 | 14.609 | 14.5901 | 14.4557 | 14.3586 | 14.1182
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | System Transformation | Headroom (MW) | N/A | 14.892 | 14.865 | 14.8039 | 14.7742 | 14.7393 | 14.7121 | 14.6834 | 14.7571 | 14.8329 | 14.8157 | 14.7922 | 14.7761 | 14.7689 | 14.7626 | 14.7472 | 14.7329 | 14.616 | 14.4567 | 14.2162
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | 52.4088 | -1.5176 | WPD Best View | Headroom (MW) | N/A | 14.892 | 14.8651 | 14.804 | 14.7743 | 14.7397 | 14.7126 | 14.6856 | 14.7599 | 14.8374 | 14.8217 | 14.8004 | 14.7874 | 14.7847 | 14.7718 | 14.6622 | 14.5268 | 13.6859 | 12.6378 | 11.6333
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Consumer Transformation | Headroom (MW) | N/A | 15.4919 | 15.424 | 15.2878 | 15.1732 | 15.0634 | 15.0266 | 14.8274 | 14.6395 | 14.472 | 14.3752 | 14.2175 | 14.102 | 14.0079 | 13.9251 | 13.8607 | 13.767 | 12.1293 | 10.8857 | 12.4299
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Leading the Way | Headroom (MW) | N/A | 15.5238 | 15.4725 | 15.3643 | 15.3119 | 15.2314 | 15.3063 | 14.8939 | 14.8538 | 14.6188 | 14.6402 | 14.3973 | 14.2382 | 14.065 | 13.8894 | 13.8837 | 13.8757 | 22.215 | 20.4843 | 19.1049
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | Steady Progression | Headroom (MW) | Thermal | 15.4964 | 15.4472 | 15.3476 | 15.2936 | 15.2488 | 15.2831 | 12.0457 | 8.9209 | 5.7957 | 2.6966 | 0.65213 | -1.342 | -4.5715 | -6.7723 | -7.9541 | -7.9893 | -8.1621 | -8.3608 | -8.7724
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | System Transformation | Headroom (MW) | N/A | 15.5075 | 15.4604 | 15.3487 | 15.2772 | 15.1989 | 15.2284 | 15.1213 | 15.0166 | 14.8959 | 14.8663 | 14.7846 | 14.7246 | 14.6803 | 14.6151 | 14.5886 | 14.5658 | 14.4636 | 14.2646 | 16.7144
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | 52.3839 | -1.5646 | WPD Best View | Headroom (MW) | N/A | 15.4919 | 15.424 | 15.2878 | 15.1732 | 15.0634 | 15.0266 | 14.8274 | 14.6395 | 14.472 | 14.3752 | 14.2175 | 14.102 | 14.0079 | 13.9251 | 13.8607 | 13.767 | 12.1293 | 10.8857 | 12.4299
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Consumer Transformation | Headroom (MW) | N/A | 68.4506 | 68.3751 | 68.1823 | 68.2261 | 68.0773 | 67.8762 | 67.6758 | 67.5236 | 67.2079 | 66.7482 | 66.1819 | 63.0525 | 60.731 | 57.5673 | 55.3744 | 51.3109 | 31.6731 | 12.7308 | 4.9218
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Leading the Way | Headroom (MW) | Thermal | 68.4942 | 68.4669 | 68.3693 | 68.5158 | 68.4193 | 68.3428 | 68.2398 | 68.3157 | 68.0921 | 67.7894 | 67.3212 | 64.5869 | 62.118 | 59.613 | 56.7723 | 54.7454 | 31.2705 | 12.8145 | -9.7609
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | Steady Progression | Headroom (MW) | N/A | 68.439 | 68.3751 | 68.2214 | 68.2756 | 68.1954 | 68.1363 | 68.1164 | 68.139 | 68.1105 | 68.0764 | 68.0246 | 67.9934 | 67.944 | 67.8902 | 67.8635 | 67.8387 | 58.4606 | 48.1342 | 46.9547
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | System Transformation | Headroom (MW) | N/A | 68.4609 | 68.4048 | 68.2648 | 68.3413 | 68.2284 | 68.1189 | 68.0815 | 68.0799 | 68.0028 | 67.8779 | 67.7591 | 67.7056 | 67.653 | 67.6414 | 67.5982 | 67.5593 | 67.6627 | 62.7186 | 58.2954
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | 52.4017 | -1.605 | WPD Best View | Headroom (MW) | N/A | 68.4506 | 68.375 | 68.182 | 68.2263 | 68.0776 | 67.8768 | 67.7142 | 67.5543 | 67.2118 | 66.7552 | 66.1929 | 64.7809 | 64.4982 | 63.3771 | 63.2286 | 61.1853 | 56.5228 | 44.9018 | 35.557
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Consumer Transformation | Headroom (MW) | Thermal | 14.208 | 14.1815 | 14.136 | 14.1155 | 14.1014 | 14.0884 | 14.0477 | 14.0385 | 13.98 | 13.8682 | 13.7322 | 10.9848 | 8.9137 | 6.8649 | 4.8412 | 2.8184 | -13.4918 | -25.1027 | -27.1125
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Leading the Way | Headroom (MW) | Thermal | 14.2082 | 14.172 | 14.1293 | 14.0978 | 14.0882 | 14.0794 | 13.9482 | 13.9449 | 13.8955 | 13.9061 | 13.8276 | 11.4579 | 9.0537 | 6.6382 | 3.7324 | 1.71 | -14.2944 | -28.1656 | -42.0954
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | Steady Progression | Headroom (MW) | Thermal | 14.2077 | 14.1805 | 14.1319 | 14.1063 | 14.0866 | 14.0673 | 14.0364 | 14.0174 | 13.995 | 13.9792 | 13.9608 | 13.9469 | 13.9303 | 13.9086 | 13.8979 | 13.8901 | 4.4411 | -5.7752 | -6.1029
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | System Transformation | Headroom (MW) | N/A | 14.2077 | 14.1807 | 14.1342 | 14.1126 | 14.0966 | 14.0807 | 14.0606 | 14.0452 | 14.0191 | 14.0086 | 14.0012 | 13.9952 | 13.9865 | 13.9836 | 13.9856 | 13.9932 | 14.07 | 12.8802 | 10.837
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | 52.4016 | -1.6054 | WPD Best View | Headroom (MW) | N/A | 14.208 | 14.1815 | 14.136 | 14.1155 | 14.1014 | 14.0884 | 14.0762 | 14.0669 | 13.98 | 13.8682 | 13.7322 | 12.6981 | 12.6616 | 12.6513 | 12.6692 | 12.6687 | 11.3674 | 7.1179 | 3.6172
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Consumer Transformation | Headroom (MW) | N/A | 7.7306 | 7.726 | 7.7321 | 7.7318 | 7.7368 | 7.7429 | 7.7415 | 7.7046 | 7.629 | 7.5413 | 7.4165 | 7.3084 | 7.2701 | 7.2574 | 7.25 | 7.2494 | 6.1562 | 5.7087 | 3.928
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Leading the Way | Headroom (MW) | N/A | 7.7306 | 7.7249 | 7.7365 | 7.7351 | 7.7432 | 7.7528 | 7.7141 | 7.7263 | 7.613 | 7.4614 | 7.2885 | 7.1357 | 7.1592 | 7.2216 | 7.3061 | 7.3295 | 7.01 | 4.2379 | 3.5735
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | Steady Progression | Headroom (MW) | N/A | 7.7304 | 7.7256 | 7.7272 | 7.7249 | 7.7266 | 7.7294 | 7.7293 | 7.7323 | 7.7364 | 7.7427 | 7.7489 | 7.7603 | 7.7651 | 7.7714 | 7.7785 | 7.7867 | 7.9176 | 7.9115 | 7.7669
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | System Transformation | Headroom (MW) | N/A | 7.7305 | 7.7257 | 7.7313 | 7.7304 | 7.7346 | 7.7395 | 7.7443 | 7.751 | 7.7599 | 7.7712 | 7.7845 | 7.8048 | 7.8142 | 7.8254 | 7.8379 | 7.8524 | 8.0495 | 8.0532 | 6.9449
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | 52.4428 | -1.5606 | WPD Best View | Headroom (MW) | N/A | 7.7306 | 7.726 | 7.7321 | 7.7318 | 7.7368 | 7.7429 | 7.7505 | 7.7046 | 7.629 | 7.5413 | 7.4165 | 7.3084 | 7.2701 | 7.2574 | 7.25 | 7.2494 | 6.1562 | 5.7087 | 3.928
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Consumer Transformation | Headroom (MW) | Thermal | 12.2693 | 12.3121 | 12.3095 | 12.4816 | 12.448 | 12.4093 | 12.4597 | 12.5502 | 12.545 | 12.4552 | 12.3199 | 12.2027 | 12.159 | 11.2142 | 11.2191 | 9.3717 | 8.2899 | 2.6905 | -0.22102
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Leading the Way | Headroom (MW) | Thermal | 12.2931 | 12.3609 | 12.4021 | 12.6433 | 12.616 | 12.5878 | 12.7131 | 12.833 | 12.8204 | 12.6978 | 12.5395 | 12.3963 | 12.4157 | 12.3824 | 12.3901 | 12.3951 | 5.7861 | 4.8459 | -2.1267
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | Steady Progression | Headroom (MW) | N/A | 12.2535 | 12.2772 | 12.2832 | 12.4179 | 12.4162 | 12.42 | 12.4947 | 12.5935 | 12.6438 | 12.6789 | 12.7106 | 12.732 | 12.74 | 12.7488 | 12.7551 | 12.7622 | 12.8086 | 12.8425 | 12.5805
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | System Transformation | Headroom (MW) | N/A | 12.2693 | 12.3088 | 12.3318 | 12.5056 | 12.4848 | 12.4781 | 12.5814 | 12.715 | 12.7899 | 12.7924 | 12.8055 | 12.8466 | 12.8927 | 12.9597 | 12.9896 | 13.0094 | 13.1439 | 9.7996 | 9.1942
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | 52.438 | -1.5558 | WPD Best View | Headroom (MW) | Thermal | 12.2693 | 12.312 | 12.3093 | 12.4817 | 12.4483 | 12.4099 | 12.4607 | 12.5524 | 12.5489 | 12.4622 | 12.3308 | 12.2178 | 12.1783 | 11.2376 | 11.2453 | 9.3958 | 8.2804 | 2.6408 | -0.31559
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Consumer Transformation | Headroom (MW) | N/A | 15.3928 | 15.3055 | 15.1546 | 15.0473 | 14.9412 | 14.7856 | 14.5769 | 14.3803 | 14.2039 | 14.0335 | 13.8633 | 13.7066 | 13.5383 | 13.3807 | 13.2141 | 13.0214 | 11.8688 | 10.5844 | 9.4774
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Leading the Way | Headroom (MW) | N/A | 15.4124 | 15.3591 | 15.2514 | 15.1897 | 15.1219 | 15.0728 | 15.0144 | 14.9614 | 14.9132 | 14.8741 | 14.8156 | 14.747 | 14.6394 | 14.5208 | 14.4937 | 14.4608 | 13.9188 | 13.0463 | 12.0377
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | Steady Progression | Headroom (MW) | N/A | 15.3973 | 15.3418 | 15.229 | 15.1765 | 15.116 | 15.0697 | 15.006 | 14.9459 | 14.8853 | 14.8255 | 14.7543 | 14.7042 | 14.6585 | 14.6114 | 14.582 | 14.5497 | 14.4434 | 14.3054 | 13.8602
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | System Transformation | Headroom (MW) | N/A | 15.4034 | 15.3396 | 15.2174 | 15.1426 | 15.0624 | 14.9707 | 14.8452 | 14.7187 | 14.5839 | 14.4556 | 14.3178 | 14.209 | 14.1096 | 14.0226 | 13.9352 | 13.8543 | 13.5492 | 13.1356 | 12.4693
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | 52.3994 | -1.5716 | WPD Best View | Headroom (MW) | N/A | 15.3928 | 15.3055 | 15.1546 | 15.0473 | 14.9412 | 14.7856 | 14.5769 | 14.3803 | 14.2039 | 14.0335 | 13.8633 | 13.7066 | 13.5383 | 13.3807 | 13.2141 | 13.0214 | 11.8688 | 10.5844 | 9.4774
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Consumer Transformation | Headroom (MW) | Thermal | 48.5936 | 48.8795 | 49.0704 | 48.8378 | 48.8158 | 48.9304 | 48.8904 | 48.8495 | 48.8162 | 48.8041 | 47.7875 | 46.7933 | 46.7625 | 46.7107 | 10.9935 | 10.9462 | 4.454 | -5.866 | -17.8215
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Leading the Way | Headroom (MW) | Thermal | 48.6216 | 48.6487 | 48.9516 | 48.7801 | 48.8234 | 49.1098 | 49.1962 | 49.4541 | 49.6338 | 49.8159 | 15.9765 | 16.0183 | 15.9742 | 14.2091 | 11.835 | 8.4872 | -2.0237 | -14.4294 | -29.3896
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | Steady Progression | Headroom (MW) | N/A | 48.5883 | 48.805 | 48.9407 | 48.9117 | 48.9218 | 49.0587 | 49.1076 | 49.1665 | 49.2271 | 49.3134 | 49.4002 | 49.5133 | 49.6508 | 49.812 | 50.0089 | 50.1572 | 50.8768 | 50.111 | 49.2278
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | System Transformation | Headroom (MW) | N/A | 48.5971 | 48.9048 | 48.9092 | 48.8871 | 48.8749 | 49.0463 | 49.0875 | 49.1513 | 49.18 | 49.2802 | 49.3855 | 49.5457 | 49.7304 | 49.9704 | 16.311 | 16.5226 | 14.4511 | 9.2741 | 2.3184
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | 52.2278 | -1.4329 | WPD Best View | Headroom (MW) | N/A | 48.5919 | 48.8135 | 48.9556 | 48.9383 | 48.9606 | 49.1163 | 49.1961 | 49.2843 | 49.3877 | 49.5228 | 49.6718 | 49.8449 | 50.0632 | 50.3101 | 16.6398 | 16.7776 | 17.2274 | 16.2767 | 14.0976
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Consumer Transformation | Headroom (MW) | N/A | 14.6593 | 15.0044 | 15.2846 | 15.3093 | 15.3346 | 15.5507 | 15.6542 | 15.7099 | 15.7292 | 15.7326 | 14.7324 | 14.6548 | 14.5729 | 14.4583 | 13.496 | 13.4023 | 10.7067 | 7.9329 | 3.7511
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Leading the Way | Headroom (MW) | Thermal | 14.6646 | 15.133 | 15.4824 | 15.5135 | 15.5655 | 15.8596 | 15.9297 | 16.1233 | 16.234 | 16.2593 | 16.2051 | 16.1308 | 16.0393 | 15.0165 | 13.3267 | 13.2343 | 10.0695 | 4.2756 | -0.0063404
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | Steady Progression | Headroom (MW) | N/A | 14.6583 | 14.9074 | 15.129 | 15.1379 | 15.1622 | 15.3214 | 15.3847 | 15.4596 | 15.5424 | 15.6324 | 15.7226 | 15.81 | 15.9093 | 16.0152 | 16.1193 | 16.1679 | 16.2935 | 16.4489 | 16.1618
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | System Transformation | Headroom (MW) | N/A | 14.6594 | 15.0047 | 15.2837 | 15.3078 | 15.3321 | 15.5467 | 15.6796 | 15.812 | 15.941 | 16.0844 | 16.2213 | 16.3679 | 16.5155 | 16.6671 | 16.8182 | 16.8873 | 15.1784 | 14.9484 | 13.018
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | 52.2017 | -1.4852 | WPD Best View | Headroom (MW) | N/A | 14.6591 | 14.909 | 15.1292 | 15.1396 | 15.1641 | 15.3235 | 15.3961 | 15.4717 | 15.5584 | 15.6496 | 15.7447 | 15.8343 | 15.9383 | 16.0473 | 16.1547 | 16.2066 | 16.3748 | 16.6107 | 16.5577
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Consumer Transformation | Headroom (MW) | Thermal | 12.2183 | 12.1991 | 12.1528 | 11.9464 | 11.925 | 11.8998 | 11.8539 | 11.8258 | 11.8171 | 11.8258 | 11.835 | 10.928 | 10.9698 | 11.0149 | 11.0911 | 11.1324 | 7.7539 | 3.4184 | -3.2548
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Leading the Way | Headroom (MW) | Thermal | 12.2256 | 12.2275 | 12.1936 | 12.0137 | 12.0038 | 12.0143 | 12.0373 | 12.0716 | 12.114 | 12.1948 | 12.2812 | 12.2802 | 12.203 | 11.3427 | 10.5436 | 8.914 | 2.698 | -1.6877 | -8.9019
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | Steady Progression | Headroom (MW) | N/A | 12.217 | 12.2051 | 12.1641 | 12.143 | 12.1308 | 12.1213 | 12.1158 | 12.1111 | 12.0972 | 12.0997 | 12.1015 | 12.1143 | 12.1281 | 12.1525 | 12.1975 | 12.2428 | 12.4579 | 11.6099 | 11.3091
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | System Transformation | Headroom (MW) | N/A | 12.2187 | 12.2103 | 11.9706 | 11.9582 | 11.9377 | 11.922 | 11.8891 | 11.8628 | 11.8216 | 11.8114 | 11.8075 | 11.821 | 11.8477 | 11.8928 | 11.9656 | 12.0372 | 11.2216 | 7.6688 | 3.281
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | 52.227 | -1.4307 | WPD Best View | Headroom (MW) | N/A | 12.2192 | 12.2101 | 12.1752 | 12.1617 | 12.1584 | 12.1628 | 12.1735 | 12.1904 | 12.2057 | 12.2443 | 12.29 | 12.3526 | 12.4231 | 12.509 | 12.6096 | 12.6254 | 12.6 | 11.4314 | 9.5232
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Consumer Transformation | Headroom (MW) | N/A | 9.0819 | 9.0418 | 8.999 | 8.9481 | 8.922 | 8.8458 | 8.7481 | 8.6797 | 8.6358 | 8.6115 | 8.586 | 8.5764 | 8.5858 | 8.6034 | 7.72 | 7.7251 | 7.3069 | 4.0962 | 2.9957
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Leading the Way | Headroom (MW) | N/A | 9.0972 | 8.6541 | 8.6415 | 8.6188 | 8.62 | 8.6018 | 8.5951 | 8.6251 | 8.6517 | 8.7277 | 8.8037 | 8.9209 | 9.0453 | 9.1635 | 9.2782 | 7.6524 | 6.5223 | 4.2962 | 0.83213
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | Steady Progression | Headroom (MW) | N/A | 9.0788 | 9.0584 | 9.0134 | 8.9967 | 8.9947 | 8.9819 | 8.973 | 8.9617 | 8.9534 | 8.9472 | 8.942 | 8.9549 | 8.9793 | 9.0102 | 9.058 | 9.1124 | 9.4914 | 9.4181 | 9.1229
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | System Transformation | Headroom (MW) | N/A | 9.0849 | 9.0556 | 9.0208 | 8.987 | 8.971 | 8.9436 | 8.8846 | 8.8425 | 8.7833 | 8.7503 | 8.7225 | 8.7227 | 8.7331 | 8.7764 | 8.8408 | 8.9116 | 9.3647 | 7.9704 | 7.333
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | 52.2731 | -1.3905 | WPD Best View | Headroom (MW) | N/A | 9.0795 | 9.0603 | 9.0171 | 9.003 | 9.004 | 8.9958 | 8.9925 | 8.9882 | 8.9896 | 8.9948 | 9.003 | 9.0239 | 9.0677 | 9.1198 | 9.189 | 9.2591 | 9.5661 | 9.548 | 9.3302
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Consumer Transformation | Headroom (MW) | N/A | 39.0713 | 38.9725 | 38.6137 | 38.1674 | 37.7708 | 37.2924 | 36.6305 | 35.9293 | 35.2471 | 34.5625 | 33.9042 | 33.2865 | 32.6432 | 31.949 | 31.2972 | 30.6181 | 27.0926 | 22.24 | 16.9554
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Leading the Way | Headroom (MW) | N/A | 39.1227 | 39.1519 | 38.9114 | 38.5811 | 38.3215 | 38.1311 | 37.8655 | 37.5426 | 37.0825 | 36.886 | 36.3339 | 35.8099 | 35.3802 | 34.7691 | 34.628 | 33.6997 | 30.5255 | 27.946 | 24.1472
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | Steady Progression | Headroom (MW) | N/A | 39.1164 | 39.0725 | 38.8646 | 38.7464 | 38.6656 | 38.5826 | 38.4825 | 38.3459 | 38.2075 | 37.9731 | 37.6579 | 37.4534 | 37.243 | 36.862 | 36.6943 | 36.5279 | 35.68 | 34.9723 | 33.7658
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | System Transformation | Headroom (MW) | N/A | 39.1117 | 39.0849 | 38.8528 | 38.5687 | 38.3173 | 38.0713 | 37.679 | 37.2554 | 36.7829 | 36.3281 | 35.9073 | 35.529 | 35.1556 | 34.7657 | 34.4355 | 34.0883 | 32.8036 | 30.1396 | 27.023
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | 52.286 | -1.5621 | WPD Best View | Headroom (MW) | N/A | 39.0706 | 38.9708 | 38.6104 | 38.2588 | 37.9583 | 37.5773 | 37.0032 | 36.3938 | 35.8075 | 35.1251 | 34.4205 | 33.7993 | 33.1498 | 32.4517 | 31.7953 | 31.1177 | 27.6614 | 23.0826 | 17.8906
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Consumer Transformation | Headroom (MW) | N/A | 98.1504 | 97.8749 | 83.9522 | 83.618 | 83.3903 | 82.8989 | 81.9686 | 81.2896 | 80.2389 | 78.4197 | 75.474 | 74.3073 | 71.2855 | 70.2484 | 68.7005 | 66.1478 | 50.0145 | 24.8272 | 3.9754
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Leading the Way | Headroom (MW) | N/A | 98.2126 | 98.0105 | 84.2554 | 83.9646 | 83.9747 | 83.7815 | 82.6331 | 82.3867 | 81.5033 | 81.2386 | 80.2544 | 78.5216 | 76.7925 | 74.9544 | 73.2884 | 67.98 | 52.3872 | 26.3027 | 6.0449
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | Steady Progression | Headroom (MW) | N/A | 98.1333 | 97.9231 | 84.085 | 83.8855 | 83.8013 | 83.6398 | 83.2919 | 83.1303 | 82.9286 | 82.7709 | 82.5317 | 82.1295 | 81.7778 | 81.4811 | 81.3036 | 81.19 | 80.502 | 79.5703 | 75.6703
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | System Transformation | Headroom (MW) | N/A | 98.1613 | 97.9646 | 84.1203 | 83.8879 | 83.8168 | 83.4877 | 82.9195 | 82.4973 | 82.0612 | 81.679 | 81.2177 | 80.7379 | 80.2548 | 79.8566 | 79.6167 | 78.461 | 72.4855 | 61.8725 | 50.3971
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | 52.2861 | -1.5667 | WPD Best View | Headroom (MW) | N/A | 98.1556 | 97.9014 | 97.3196 | 97.0135 | 96.7492 | 96.3188 | 95.6948 | 95.0109 | 94.0926 | 93.2181 | 90.3782 | 89.436 | 88.4896 | 87.6855 | 86.0447 | 84.3741 | 73.4764 | 55.4953 | 41.5438
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Consumer Transformation | Headroom (MW) | Thermal | 6.3427 | 6.3032 | 6.2394 | 6.1383 | 6.1938 | 6.0543 | 5.8492 | 5.67 | 5.5093 | 5.3238 | 5.1716 | 5.0244 | 4.8883 | 4.8226 | 4.7205 | 4.6214 | 4.0151 | 0.83209 | -0.14399
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Leading the Way | Headroom (MW) | N/A | 6.3696 | 6.369 | 6.3241 | 6.2635 | 6.4095 | 6.3166 | 6.1897 | 6.0941 | 5.9896 | 5.9154 | 5.8622 | 5.8804 | 5.94 | 6.0652 | 6.1178 | 4.4246 | 4.364 | 2.2629 | 1.2237
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | Steady Progression | Headroom (MW) | N/A | 6.3358 | 6.3356 | 6.3098 | 6.2922 | 6.3674 | 6.3464 | 6.3249 | 6.3054 | 6.2936 | 6.2656 | 6.2386 | 6.2216 | 6.2163 | 6.239 | 6.2384 | 6.2559 | 6.5085 | 6.634 | 6.3141
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | System Transformation | Headroom (MW) | N/A | 6.3487 | 6.3545 | 6.3189 | 6.2898 | 6.4008 | 6.3392 | 6.2541 | 6.1784 | 6.1072 | 6.0409 | 5.9563 | 5.9081 | 5.8722 | 5.8946 | 5.8912 | 5.8871 | 6.0535 | 4.5525 | 3.9392
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | 52.2576 | -1.565 | WPD Best View | Headroom (MW) | N/A | 6.3443 | 6.317 | 6.2513 | 6.1699 | 6.185 | 6.0753 | 5.9115 | 5.7741 | 5.633 | 5.4618 | 5.3287 | 5.191 | 5.0767 | 5.0298 | 4.9465 | 4.8833 | 4.6222 | 1.9465 | 1.2503
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Consumer Transformation | Headroom (MW) | N/A | 13.1518 | 13.1152 | 13.0351 | 13.0426 | 12.9991 | 12.9558 | 12.8844 | 12.8492 | 12.7779 | 12.7438 | 12.6665 | 12.518 | 12.3526 | 12.1943 | 12.1747 | 12.1555 | 10.4473 | 8.0561 | 7.0878
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Leading the Way | Headroom (MW) | N/A | 13.1538 | 13.1056 | 13.0267 | 13.0362 | 12.9929 | 12.9497 | 12.6177 | 12.5811 | 12.4256 | 12.3912 | 12.2211 | 12.1218 | 12.0108 | 11.9009 | 11.8857 | 11.8649 | 11.4773 | 7.1648 | 6.1508
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | Steady Progression | Headroom (MW) | N/A | 13.1502 | 13.1118 | 13.0304 | 13.0209 | 12.9766 | 12.9324 | 12.8792 | 12.839 | 12.7951 | 12.755 | 12.7117 | 12.6733 | 12.6338 | 12.5975 | 12.5624 | 12.5288 | 12.3556 | 12.1635 | 11.8175
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | System Transformation | Headroom (MW) | N/A | 13.1517 | 13.115 | 13.0346 | 13.0417 | 12.9976 | 12.9533 | 12.9057 | 12.8684 | 12.8286 | 12.79 | 12.7525 | 12.7148 | 12.677 | 12.6446 | 12.6152 | 12.588 | 12.4679 | 11.1251 | 10.5085
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | 52.2964 | -1.516 | WPD Best View | Headroom (MW) | N/A | 13.1518 | 13.1152 | 13.035 | 13.0423 | 12.9986 | 12.955 | 12.9127 | 12.8769 | 12.8327 | 12.7974 | 12.7519 | 12.6366 | 12.5096 | 12.3785 | 12.2648 | 12.1332 | 10.3583 | 8.0995 | 7.1995
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Consumer Transformation | Headroom (MW) | Thermal | 10.0279 | 9.9875 | 9.9081 | 9.8651 | 9.8424 | 9.803 | 9.7102 | 9.6615 | 9.5957 | 8.6714 | 7.6881 | 7.6611 | 6.7164 | 6.7081 | 5.8617 | 4.9687 | -1.9312 | -11.7528 | -21.6892
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Leading the Way | Headroom (MW) | Thermal | 10.0371 | 10.0113 | 9.9686 | 9.9555 | 9.9506 | 9.9697 | 9.9939 | 10.0143 | 9.8374 | 9.8202 | 9.6158 | 8.5985 | 7.5743 | 7.4335 | 5.961 | 4.3621 | -3.8591 | -15.142 | -24.6049
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | Steady Progression | Headroom (MW) | N/A | 10.0313 | 10.0001 | 9.9252 | 9.8982 | 9.88 | 9.8672 | 9.8459 | 9.8353 | 9.814 | 9.812 | 9.7929 | 9.797 | 9.8277 | 9.8592 | 9.9184 | 9.9953 | 9.9342 | 9.637 | 8.0631
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | System Transformation | Headroom (MW) | Thermal | 10.031 | 9.9885 | 9.916 | 9.872 | 9.8333 | 9.7959 | 9.7338 | 9.6727 | 9.6282 | 9.5827 | 9.5402 | 9.5411 | 9.5499 | 9.6064 | 9.6968 | 8.8615 | 6.0067 | 2.1515 | -3.2596
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | 52.2769 | -1.6953 | WPD Best View | Headroom (MW) | Thermal | 10.0322 | 10.0025 | 9.9325 | 9.9012 | 9.8915 | 9.8816 | 9.8498 | 9.8464 | 9.83 | 9.8518 | 8.9054 | 8.9304 | 8.9598 | 9.0055 | 8.1705 | 8.2588 | 5.2523 | 0.57134 | -3.3151
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Consumer Transformation | Headroom (MW) | Fault level | 12.8192 | 12.7705 | 12.6872 | 12.581 | 12.3045 | 11.9429 | 11.4886 | 11.0424 | 10.5416 | 10.0576 | 8.4773 | 7.971 | 7.4434 | 6.9439 | 6.4968 | 5.0021 | 0.86402 | -4.6299 | -10.3105
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Leading the Way | Headroom (MW) | Fault level | 12.7233 | 12.7047 | 12.6523 | 12.4399 | 12.198 | 11.9042 | 11.5497 | 11.1669 | 10.7048 | 10.2825 | 9.8784 | 9.5302 | 9.2151 | 6.9181 | 6.6579 | 5.1338 | 0.77993 | -4.4757 | -8.8275
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | Steady Progression | Headroom (MW) | N/A | 10.0732 | 10.0606 | 10.045 | 10.0357 | 10.0182 | 9.9944 | 9.9728 | 9.9378 | 9.9026 | 9.8645 | 9.8147 | 9.6601 | 9.5085 | 9.3636 | 9.2113 | 9.0659 | 8.5939 | 7.6093 | 7.3091
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | System Transformation | Headroom (MW) | N/A | 12.2545 | 12.2327 | 12.1982 | 12.1514 | 12.0934 | 11.8799 | 11.6228 | 11.3719 | 11.0936 | 10.8128 | 10.525 | 10.2451 | 9.9499 | 9.6633 | 9.3904 | 9.1157 | 6.0598 | 3.8188 | 1.511
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | 52.3371 | -1.5846 | WPD Best View | Headroom (MW) | Fault level | 11.9939 | 11.9483 | 11.8703 | 11.771 | 11.5123 | 11.174 | 10.7489 | 10.3315 | 9.8629 | 9.4101 | 7.9315 | 7.4578 | 6.9642 | 6.4968 | 6.0785 | 4.683 | 0.83033 | -4.2766 | -9.5592
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Consumer Transformation | Headroom (MW) | N/A | 11.7057 | 11.6983 | 11.69 | 11.6783 | 11.6609 | 11.6422 | 11.6044 | 11.5752 | 11.5399 | 11.5024 | 11.4676 | 11.4272 | 11.3819 | 11.335 | 11.2907 | 11.2304 | 10.8957 | 10.5556 | 10.2427
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Leading the Way | Headroom (MW) | N/A | 11.6317 | 11.6288 | 11.6257 | 11.6195 | 11.6154 | 11.6105 | 11.5966 | 11.5881 | 11.5763 | 11.5517 | 11.5213 | 11.4832 | 11.4294 | 11.3828 | 11.3315 | 11.268 | 11.0442 | 10.7584 | 10.462
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | Steady Progression | Headroom (MW) | N/A | 9.6836 | 9.6819 | 9.6808 | 9.6798 | 9.6792 | 9.6786 | 9.6769 | 9.6746 | 9.6718 | 9.6683 | 9.662 | 9.6579 | 9.6475 | 9.6437 | 9.6401 | 9.6354 | 9.574 | 9.4746 | 9.3507
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | System Transformation | Headroom (MW) | N/A | 11.3039 | 11.3006 | 11.2971 | 11.2922 | 11.2872 | 11.2808 | 11.2602 | 11.2468 | 11.2303 | 11.207 | 11.1873 | 11.1708 | 11.1461 | 11.1282 | 11.1086 | 11.0768 | 10.9381 | 10.7856 | 10.6041
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | 52.272 | -1.5403 | WPD Best View | Headroom (MW) | N/A | 11.1274 | 11.1203 | 11.1125 | 11.1014 | 11.0848 | 11.067 | 11.0311 | 11.0034 | 10.9698 | 10.9341 | 10.9011 | 10.8627 | 10.8196 | 10.7751 | 10.7329 | 10.6756 | 10.3575 | 10.0341 | 9.7367
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Consumer Transformation | Headroom (MW) | N/A | 7.3887 | 7.3858 | 7.3639 | 7.3666 | 7.3804 | 7.3881 | 7.3984 | 7.4352 | 7.4144 | 7.4124 | 7.3844 | 7.3761 | 6.4633 | 6.4552 | 6.4757 | 6.4974 | 5.5236 | 4.3343 | 4.0153
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Leading the Way | Headroom (MW) | N/A | 7.3924 | 7.3935 | 7.3838 | 7.3869 | 7.4099 | 7.4411 | 7.4014 | 7.3946 | 7.3791 | 7.3811 | 7.3661 | 7.34 | 7.3172 | 7.2848 | 7.3144 | 7.3425 | 6.3266 | 6.2178 | 5.0016
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | Steady Progression | Headroom (MW) | N/A | 7.3871 | 7.3798 | 7.358 | 7.3512 | 7.3479 | 7.3481 | 7.3429 | 7.3498 | 7.3644 | 7.3812 | 7.3891 | 7.3792 | 7.3695 | 7.353 | 7.3469 | 7.3428 | 7.341 | 7.3476 | 7.2011
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | System Transformation | Headroom (MW) | N/A | 7.3874 | 7.3812 | 7.3586 | 7.3431 | 7.3389 | 7.3387 | 7.3396 | 7.3354 | 7.3517 | 7.3761 | 7.4006 | 7.3976 | 7.3926 | 7.3919 | 7.3952 | 7.4031 | 7.4745 | 7.4738 | 7.5193
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | 52.3302 | -1.4146 | WPD Best View | Headroom (MW) | N/A | 7.3881 | 7.3836 | 7.3664 | 7.3663 | 7.371 | 7.3809 | 7.3873 | 7.4123 | 7.4311 | 7.4237 | 7.4183 | 7.4158 | 7.4072 | 7.4014 | 7.4067 | 7.4137 | 7.4455 | 7.4568 | 7.4077
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Consumer Transformation | Headroom (MW) | N/A | 13.2208 | 13.2153 | 13.1931 | 13.175 | 13.1579 | 13.143 | 13.0079 | 12.9947 | 12.9773 | 12.9655 | 12.9507 | 12.8068 | 12.6509 | 12.501 | 12.498 | 12.4956 | 12.4462 | 12.2822 | 12.0481
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Leading the Way | Headroom (MW) | N/A | 13.2327 | 13.2285 | 13.2107 | 13.1895 | 13.1743 | 13.1576 | 12.8631 | 12.8486 | 12.6975 | 12.6858 | 12.5251 | 12.508 | 12.4916 | 12.4741 | 12.4747 | 12.4747 | 12.4093 | 12.2755 | 12.1172
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | Steady Progression | Headroom (MW) | N/A | 13.2117 | 13.2031 | 13.1769 | 13.16 | 13.1441 | 13.1295 | 13.0063 | 12.9919 | 12.9766 | 12.9627 | 12.9485 | 12.828 | 12.7181 | 12.6092 | 12.5953 | 12.5821 | 12.5358 | 12.4875 | 12.3794
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | System Transformation | Headroom (MW) | N/A | 13.2207 | 13.2151 | 13.1926 | 13.1742 | 13.1567 | 13.1409 | 13.03 | 13.0151 | 12.9995 | 12.9844 | 12.9714 | 12.8634 | 12.7559 | 12.6486 | 12.6385 | 12.6304 | 12.6173 | 12.5637 | 12.4714
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | 52.2651 | -1.6112 | WPD Best View | Headroom (MW) | N/A | 13.2208 | 13.2153 | 13.1931 | 13.175 | 13.1579 | 13.143 | 13.1293 | 13.1161 | 13.1032 | 13.0915 | 13.0827 | 13.0759 | 13.071 | 13.0666 | 13.0635 | 13.0611 | 13.044 | 12.9819 | 12.912
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Consumer Transformation | Headroom (MW) | N/A | 17.2121 | 17.1213 | 16.9482 | 16.8059 | 16.6681 | 16.4823 | 16.2145 | 15.9508 | 15.7097 | 15.4599 | 15.1963 | 14.9461 | 14.6877 | 14.4502 | 14.2044 | 13.9476 | 12.5206 | 10.9915 | 9.6463
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Leading the Way | Headroom (MW) | N/A | 17.2141 | 17.1466 | 17.0421 | 16.9619 | 16.8715 | 16.7908 | 16.6881 | 16.5766 | 16.4599 | 16.3371 | 16.2024 | 16.0588 | 15.9093 | 15.7941 | 15.6693 | 15.5353 | 14.7871 | 13.7552 | 12.5952
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | Steady Progression | Headroom (MW) | N/A | 17.2107 | 17.1538 | 17.0384 | 16.9744 | 16.9018 | 16.8364 | 16.7653 | 16.6966 | 16.6143 | 16.5438 | 16.4607 | 16.3888 | 16.3111 | 16.2491 | 16.196 | 16.153 | 15.9728 | 15.7519 | 15.2192
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | System Transformation | Headroom (MW) | N/A | 17.2121 | 17.1558 | 17.0246 | 16.9291 | 16.8268 | 16.725 | 16.5594 | 16.4058 | 16.234 | 16.0735 | 15.911 | 15.7636 | 15.6246 | 15.5007 | 15.3864 | 15.2725 | 14.8287 | 14.2869 | 13.5005
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | 52.2833 | -1.5329 | WPD Best View | Headroom (MW) | N/A | 17.2121 | 17.1213 | 16.9482 | 16.8059 | 16.6681 | 16.4823 | 16.2145 | 15.9508 | 15.7097 | 15.4599 | 15.1963 | 14.9461 | 14.6877 | 14.4502 | 14.2044 | 13.9476 | 12.5206 | 10.9915 | 9.6463
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Consumer Transformation | Headroom (MW) | Thermal | 1.7412 | 1.5222 | 1.17 | 0.81321 | 0.44268 | -0.08676 | -0.91797 | -1.6524 | -3.4415 | -5.2021 | -9.0418 | -11.9949 | -13.9862 | -16.9048 | -18.6772 | -23.3243 | -45.3845 | -82.0449 | -114.8935
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Leading the Way | Headroom (MW) | Thermal | 1.8023 | 1.6627 | 1.4359 | 1.2628 | 1.0435 | 0.82979 | 0.38598 | 0.0050681 | -0.53858 | -1.0071 | -2.5506 | -3.9933 | -5.434 | -13.5082 | -19.8882 | -28.8575 | -56.6804 | -89.0932 | -120.4346
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | Steady Progression | Headroom (MW) | Thermal | 1.7959 | 1.6759 | 1.4613 | 1.3469 | 1.2442 | 1.1294 | 1.0092 | 0.8827 | 0.74646 | 0.60339 | 0.42656 | 0.26785 | 0.14058 | 0.025528 | -0.070089 | -0.19742 | -0.58292 | -5.5683 | -7.9376
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | System Transformation | Headroom (MW) | Thermal | 1.789 | 1.6325 | 1.3823 | 1.1922 | 0.96974 | 0.74342 | 0.34737 | -0.0029094 | -0.42973 | -0.82269 | -1.2575 | -1.621 | -2.92 | -3.2329 | -3.5278 | -4.7736 | -16.0236 | -33.9264 | -49.4865
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | 52.9243 | -0.5889 | WPD Best View | Headroom (MW) | Thermal | 34.5523 | 34.3409 | 33.9906 | 33.6488 | 33.2864 | 32.7675 | 31.9967 | 31.2733 | 29.5277 | 27.7756 | 24.9001 | 22.9 | 20.9375 | 18.0517 | 16.2753 | 13.496 | -3.4684 | -32.7626 | -59.4224
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Consumer Transformation | Headroom (MW) | Thermal | 6.4387 | 6.4107 | 6.3425 | 6.2873 | 6.237 | 6.1717 | 6.0337 | 5.9424 | 5.8187 | 4.8107 | 4.6761 | 3.6199 | 2.5797 | 2.4628 | 2.421 | 0.49911 | -7.0182 | -20.5766 | -32.0165
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Leading the Way | Headroom (MW) | Thermal | 6.4542 | 6.4283 | 6.3957 | 6.3757 | 6.3498 | 6.3548 | 6.3191 | 6.3165 | 6.295 | 6.3177 | 6.2949 | 5.3767 | 5.3953 | 1.9149 | -1.4389 | -5.6604 | -17.7677 | -30.302 | -43.0098
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | Steady Progression | Headroom (MW) | N/A | 6.4536 | 6.4244 | 6.387 | 6.3672 | 6.3496 | 6.3341 | 6.3113 | 6.2888 | 6.2703 | 6.2587 | 6.2356 | 6.2238 | 6.2247 | 6.2296 | 6.2426 | 6.2608 | 6.4163 | 3.975 | 2.4788
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | System Transformation | Headroom (MW) | Thermal | 6.4515 | 6.4191 | 6.3755 | 6.3381 | 6.2916 | 6.2617 | 6.1836 | 6.135 | 6.0619 | 6.0102 | 5.9344 | 5.9052 | 5.8705 | 5.8582 | 5.856 | 4.9406 | 0.26401 | -7.5874 | -15.2806
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | 52.8948 | -0.365 | WPD Best View | Headroom (MW) | Thermal | 6.4403 | 6.4127 | 6.3544 | 6.3028 | 6.2622 | 6.2009 | 6.0992 | 6.0132 | 5.9196 | 4.9167 | 4.8158 | 4.7024 | 3.6834 | 3.5885 | 3.5476 | 2.5743 | -1.1298 | -9.7899 | -17.3662
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Consumer Transformation | Headroom (MW) | Thermal | 6.9755 | 6.9552 | 6.9105 | 6.8872 | 6.8618 | 6.8367 | 6.7973 | 6.7738 | 6.7361 | 6.7145 | 5.7611 | 5.6965 | 5.646 | 5.5953 | 4.6481 | 4.6213 | 2.0279 | -4.2051 | -9.2071
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Leading the Way | Headroom (MW) | Thermal | 6.977 | 6.9555 | 6.9119 | 6.8856 | 6.86 | 6.835 | 6.7759 | 6.7524 | 6.7128 | 6.6919 | 6.6452 | 6.5888 | 6.5327 | 4.6355 | 4.6418 | 2.0945 | -1.6592 | -8.1256 | -13.0627
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | Steady Progression | Headroom (MW) | N/A | 6.9743 | 6.9528 | 6.9071 | 6.8824 | 6.8565 | 6.831 | 6.8035 | 6.7789 | 6.7534 | 6.7292 | 6.7046 | 6.6724 | 6.6492 | 6.6269 | 6.6054 | 6.5846 | 6.4713 | 5.4485 | 5.2682
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | System Transformation | Headroom (MW) | Thermal | 6.9755 | 6.955 | 6.9102 | 6.8868 | 6.8611 | 6.8355 | 6.8097 | 6.7851 | 6.7605 | 6.7368 | 6.7135 | 6.6822 | 6.6603 | 6.64 | 6.621 | 6.6034 | 4.5214 | 0.54679 | -2.2585
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | 52.8279 | -0.6075 | WPD Best View | Headroom (MW) | Thermal | 6.9755 | 6.9552 | 6.9105 | 6.8872 | 6.8618 | 6.8367 | 6.8036 | 6.7801 | 6.7485 | 6.7269 | 5.7611 | 5.6965 | 5.646 | 5.5953 | 4.6481 | 4.6213 | 2.0279 | -4.2051 | -9.2071
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Consumer Transformation | Headroom (MW) | Thermal | 15.101 | 14.9526 | 14.7285 | 14.4813 | 14.202 | 13.7926 | 13.204 | 12.6231 | 11.0524 | 10.3617 | 9.5486 | 7.7911 | 6.9518 | 5.1832 | 4.4043 | 2.6352 | -5.9056 | -16.8249 | -26.2442
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Leading the Way | Headroom (MW) | Thermal | 15.141 | 15.0569 | 14.9124 | 14.7973 | 14.6241 | 14.4243 | 14.0886 | 13.7311 | 13.2432 | 12.742 | 11.264 | 10.7792 | 10.2878 | 8.5074 | 7.1179 | 4.9027 | -3.5975 | -12.2581 | -20.0891
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | Steady Progression | Headroom (MW) | N/A | 15.1397 | 15.0737 | 14.9575 | 14.8881 | 14.8305 | 14.7653 | 14.694 | 14.6123 | 14.5163 | 14.4121 | 14.2902 | 14.1725 | 14.055 | 13.9343 | 13.8165 | 13.6711 | 13.0672 | 11.416 | 10.8698
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | System Transformation | Headroom (MW) | Thermal | 15.1344 | 15.0428 | 14.8906 | 14.7747 | 14.6316 | 14.476 | 14.2145 | 13.962 | 13.6493 | 13.3535 | 13.0242 | 12.7352 | 11.4946 | 11.1892 | 10.889 | 10.554 | 7.7578 | 3.0562 | -0.42067
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | 52.9133 | -0.6291 | WPD Best View | Headroom (MW) | Thermal | 15.1003 | 14.951 | 14.7251 | 14.4758 | 14.1938 | 13.7806 | 13.1872 | 12.6003 | 11.0217 | 10.3219 | 9.4982 | 7.7276 | 6.8741 | 5.0909 | 4.298 | 2.5209 | -5.9938 | -16.7807 | -26.1318
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Consumer Transformation | Headroom (MW) | Thermal | 5.8547 | 5.8324 | 5.8173 | 5.7861 | 5.7706 | 5.741 | 5.6758 | 5.6371 | 5.58 | 5.5397 | 3.6011 | 3.5264 | 3.465 | 2.4827 | 2.4781 | 1.5488 | -1.8599 | -7.8096 | -14.797
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Leading the Way | Headroom (MW) | Thermal | 5.8588 | 5.8507 | 5.8446 | 5.8329 | 5.8384 | 5.8443 | 5.8311 | 5.8337 | 5.8392 | 5.87 | 5.874 | 5.8908 | 4.979 | 4.0627 | 2.4198 | 2.4344 | -1.0274 | -5.7788 | -11.6443
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | Steady Progression | Headroom (MW) | N/A | 5.8569 | 5.8537 | 5.8385 | 5.8379 | 5.8363 | 5.8277 | 5.829 | 5.8315 | 5.8351 | 5.8322 | 5.8249 | 5.8279 | 5.8405 | 5.8634 | 5.8941 | 5.9147 | 6.0909 | 6.2209 | 6.0743
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | System Transformation | Headroom (MW) | N/A | 5.8562 | 5.8442 | 5.8348 | 5.8213 | 5.8142 | 5.799 | 5.7682 | 5.7437 | 5.7273 | 5.7056 | 5.6991 | 5.6851 | 5.6832 | 5.7083 | 5.7349 | 5.7572 | 4.062 | 2.6867 | 1.1021
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | 52.812 | -0.6766 | WPD Best View | Headroom (MW) | Thermal | 5.8554 | 5.8412 | 5.8198 | 5.802 | 5.7878 | 5.7683 | 5.7257 | 5.6988 | 5.657 | 5.6292 | 4.644 | 4.5926 | 4.553 | 3.5961 | 3.6006 | 3.5987 | 1.4464 | -2.1679 | -6.8982
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Consumer Transformation | Headroom (MW) | Thermal | 26.408 | 25.7645 | 23.7188 | 22.5526 | 12.0446 | 10.4446 | 8.2735 | 5.2954 | -0.36423 | -5.2085 | -9.5408 | -13.8256 | -18.9578 | -26.8646 | -31.5907 | -35.534 | -72.9488 | -122.7138 | -166.1811
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Leading the Way | Headroom (MW) | Thermal | 26.5292 | 26.0906 | 24.3494 | 23.6059 | 13.5432 | 12.7419 | 11.3953 | 10.4318 | 6.3524 | 5.4208 | 2.4291 | -1.3228 | -3.2659 | -9.0747 | -12.478 | -25.9732 | -60.4663 | -97.8302 | -134.5639
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | Steady Progression | Headroom (MW) | Thermal | 26.5329 | 26.1367 | 25.4155 | 25.0003 | 4.0686 | 3.57 | 3.0777 | 2.5667 | 2.0208 | 1.3656 | 0.70138 | 0.037577 | -0.59346 | -1.1608 | -1.6805 | -2.2167 | -16.3215 | -22.2087 | -25.0259
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | System Transformation | Headroom (MW) | Thermal | 26.497 | 26.0313 | 25.1899 | 24.3884 | 23.4997 | 22.6081 | 21.3304 | 19.2055 | 17.8464 | 7.2359 | 5.8482 | 3.707 | 1.5864 | -2.1196 | -4.988 | -6.9662 | -18.3053 | -36.344 | -54.0902
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 53.1409 | 0.2613 | WPD Best View | Headroom (MW) | Thermal | 26.508 | 26.0374 | 25.2111 | 24.5113 | 3.2367 | 2.4781 | 1.3534 | -0.64445 | -1.83 | -12.3863 | -13.6209 | -15.7163 | -16.8475 | -20.4991 | -23.3194 | -25.2394 | -36.055 | -52.9182 | -70.5027
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Consumer Transformation | Headroom (MW) | Thermal | 4.7908 | 4.7305 | 4.6367 | 4.5474 | 4.4518 | 4.3164 | 4.1214 | 3.9366 | 3.7487 | 3.5643 | 2.407 | 2.1974 | 1.9889 | 0.84128 | 0.66481 | 0.47983 | -2.6847 | -8.1482 | -12.6851
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Leading the Way | Headroom (MW) | Thermal | 4.7986 | 4.7697 | 4.7075 | 4.6651 | 4.6227 | 4.5822 | 4.4971 | 4.4406 | 4.3505 | 4.2911 | 4.213 | 4.1555 | 3.1634 | 3.094 | 3.0476 | 1.2827 | -2.396 | -5.3179 | -9.2101
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | Steady Progression | Headroom (MW) | N/A | 4.8026 | 4.7681 | 4.7145 | 4.6847 | 4.652 | 4.621 | 4.592 | 4.5649 | 4.5264 | 4.4969 | 4.4398 | 4.4122 | 4.3768 | 4.3531 | 4.3329 | 4.305 | 4.2577 | 4.1987 | 3.9593
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | System Transformation | Headroom (MW) | Thermal | 4.7942 | 4.7566 | 4.6943 | 4.6423 | 4.5784 | 4.5213 | 4.4158 | 4.3204 | 4.209 | 4.0959 | 3.9741 | 3.8852 | 3.7973 | 3.7069 | 3.6403 | 3.5593 | 2.3009 | 0.64214 | -1.0516
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 53.2546 | 0.1883 | WPD Best View | Headroom (MW) | Thermal | 4.7942 | 4.7566 | 4.6943 | 4.6423 | 4.5784 | 4.5213 | 4.4158 | 4.3204 | 4.209 | 4.0959 | 3.9741 | 3.8852 | 3.7973 | 3.7069 | 3.6403 | 3.5593 | 2.3009 | 0.64214 | -1.0516
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Consumer Transformation | Headroom (MW) | Thermal | 7.6949 | 7.6482 | 7.5587 | 7.4787 | 7.4057 | 7.3057 | 7.1666 | 7.042 | 6.9028 | 5.8463 | 5.6729 | 5.5047 | 4.4191 | 4.2499 | 3.2069 | 3.0727 | -2.0014 | -8.4543 | -14.9171
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Leading the Way | Headroom (MW) | Thermal | 7.6982 | 7.6664 | 7.6015 | 7.5539 | 7.5009 | 7.4585 | 7.3896 | 7.3422 | 7.2723 | 7.2312 | 7.1534 | 6.1765 | 6.1035 | 4.7711 | 4.7325 | 2.0574 | -3.1978 | -10.4703 | -15.5864
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | Steady Progression | Headroom (MW) | N/A | 7.7 | 7.6689 | 7.6132 | 7.5749 | 7.5449 | 7.5064 | 7.4828 | 7.4475 | 7.4102 | 7.3754 | 7.3201 | 7.289 | 7.2577 | 7.2314 | 7.2105 | 7.1849 | 7.1099 | 5.7613 | 5.5208
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | System Transformation | Headroom (MW) | Thermal | 7.6969 | 7.6623 | 7.5921 | 7.5445 | 7.4854 | 7.4411 | 7.3545 | 7.2878 | 7.1926 | 7.1114 | 7.0295 | 6.9576 | 6.8812 | 6.824 | 5.8462 | 5.7879 | 4.2673 | 1.4064 | -2.4208
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 53.2251 | 0.3159 | WPD Best View | Headroom (MW) | Thermal | 7.6969 | 7.6623 | 7.5921 | 7.5445 | 7.4854 | 7.4411 | 7.3545 | 7.2878 | 7.1926 | 7.1114 | 7.0295 | 6.9576 | 6.8812 | 6.824 | 5.8462 | 5.7879 | 4.2673 | 1.4064 | -2.4208
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Consumer Transformation | Headroom (MW) | Thermal | 11.1468 | 11.0446 | 10.8465 | 10.6949 | 10.5302 | 10.3224 | 10.0382 | 9.7582 | 9.4803 | 9.2079 | 8.937 | 7.7232 | 7.439 | 7.1695 | 6.9269 | 6.6599 | 4.2219 | -0.54156 | -4.9638
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Leading the Way | Headroom (MW) | Thermal | 11.1694 | 11.0989 | 10.9441 | 10.8482 | 10.7503 | 10.6502 | 10.5065 | 10.3765 | 10.2373 | 10.1282 | 10.0536 | 9.9817 | 9.9093 | 9.8189 | 9.7407 | 7.0084 | 5.1223 | 2.82 | -0.30222
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | Steady Progression | Headroom (MW) | N/A | 11.1616 | 11.0972 | 10.9639 | 10.8882 | 10.8094 | 10.7401 | 10.6644 | 10.5807 | 10.5053 | 10.417 | 10.3416 | 10.2605 | 10.1865 | 10.1057 | 10.0454 | 9.9782 | 9.796 | 9.6283 | 9.2104
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | System Transformation | Headroom (MW) | N/A | 11.162 | 11.0854 | 10.9388 | 10.8343 | 10.7238 | 10.6086 | 10.4389 | 10.2779 | 10.09 | 9.9135 | 9.7692 | 9.6139 | 9.4668 | 9.3312 | 9.2065 | 9.0748 | 8.5724 | 5.7988 | 3.6579
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | 53.2181 | -0.1122 | WPD Best View | Headroom (MW) | N/A | 11.162 | 11.0854 | 10.9388 | 10.8343 | 10.7238 | 10.6086 | 10.4389 | 10.2779 | 10.09 | 9.9135 | 9.7692 | 9.6139 | 9.4668 | 9.3312 | 9.2065 | 9.0748 | 8.5724 | 5.7988 | 3.6579
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Consumer Transformation | Headroom (MW) | N/A | 14.4308 | 14.3821 | 14.2861 | 14.2337 | 14.182 | 14.1309 | 14.0655 | 14.0156 | 13.9519 | 13.9035 | 13.8279 | 13.7523 | 13.6864 | 12.7296 | 12.6875 | 12.6462 | 11.8515 | 8.6257 | 8.4311
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Leading the Way | Headroom (MW) | N/A | 14.4313 | 14.3765 | 14.2808 | 14.2204 | 14.1691 | 14.1185 | 13.8814 | 13.8321 | 13.7569 | 13.7095 | 13.6334 | 13.5337 | 13.4323 | 13.3267 | 13.2867 | 12.8411 | 11.515 | 11.331 | 8.4334
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | Steady Progression | Headroom (MW) | N/A | 14.4305 | 14.3816 | 14.2853 | 14.2314 | 14.1792 | 14.1278 | 14.0706 | 14.0202 | 13.968 | 13.9186 | 13.8677 | 13.8195 | 13.771 | 13.7243 | 13.6782 | 13.633 | 13.399 | 13.1628 | 12.8743
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | System Transformation | Headroom (MW) | N/A | 14.4308 | 14.3821 | 14.286 | 14.2336 | 14.1817 | 14.1305 | 14.0778 | 14.0275 | 13.9765 | 13.9271 | 13.8696 | 13.8218 | 13.7741 | 13.7284 | 13.684 | 13.6408 | 13.4304 | 12.2186 | 13.471
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 53.1802 | 0.3314 | WPD Best View | Headroom (MW) | N/A | 14.4308 | 14.3821 | 14.286 | 14.2336 | 14.1817 | 14.1305 | 14.0799 | 14.0296 | 13.9796 | 13.9302 | 13.8727 | 13.8249 | 13.7781 | 13.7325 | 13.688 | 13.6449 | 13.4363 | 12.2186 | 13.471
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Consumer Transformation | Headroom (MW) | Thermal | 4.1435 | 4.093 | 4.0009 | 3.9145 | 3.8199 | 3.7025 | 3.5122 | 3.3431 | 3.1865 | 2.0848 | 1.8605 | 1.6449 | 0.51476 | 0.31558 | -0.75824 | -0.90772 | -7.4131 | -14.0289 | -21.9446
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Leading the Way | Headroom (MW) | Thermal | 4.1617 | 4.1239 | 4.059 | 4.0201 | 3.9659 | 3.9195 | 3.8406 | 3.7694 | 3.7118 | 3.6381 | 3.5353 | 2.547 | 2.4933 | 1.1557 | -0.57235 | -3.2239 | -9.5448 | -18.1308 | -24.5883
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | Steady Progression | Headroom (MW) | N/A | 4.1601 | 4.1321 | 4.07 | 4.041 | 4.0034 | 3.9756 | 3.9413 | 3.9044 | 3.8801 | 3.8453 | 3.7947 | 3.7643 | 3.7261 | 3.7027 | 3.6844 | 3.6658 | 3.642 | 2.3338 | 2.1028
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | System Transformation | Headroom (MW) | Thermal | 4.1581 | 4.1169 | 4.0461 | 3.996 | 3.9339 | 3.8732 | 3.7719 | 3.6862 | 3.607 | 3.5083 | 3.4024 | 3.3149 | 3.2389 | 3.1703 | 2.1786 | 2.1313 | -0.66665 | -3.5507 | -8.6778
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 53.1686 | 0.1046 | WPD Best View | Headroom (MW) | Thermal | 4.1581 | 4.1169 | 4.0461 | 3.996 | 3.9339 | 3.8732 | 3.7719 | 3.6862 | 3.607 | 3.5083 | 3.4024 | 3.3149 | 3.2389 | 3.1703 | 2.1786 | 2.1313 | -0.66665 | -3.5507 | -8.6778
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Consumer Transformation | Headroom (MW) | Thermal | 8.1582 | 8.074 | 7.0071 | 6.879 | 6.7387 | 6.5377 | 6.2525 | 5.9829 | 5.7226 | 5.447 | 5.1332 | 4.8529 | 4.5739 | 3.3737 | 3.1135 | 2.822 | 0.23259 | -2.4538 | -4.1699
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Leading the Way | Headroom (MW) | N/A | 8.1779 | 8.1213 | 7.106 | 7.0414 | 6.9833 | 6.918 | 6.799 | 6.706 | 6.5961 | 6.5076 | 6.4044 | 6.3364 | 6.2701 | 6.199 | 6.119 | 6.0192 | 4.5047 | 2.7849 | 1.9449
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | Steady Progression | Headroom (MW) | N/A | 8.1743 | 8.1283 | 8.0524 | 8.0048 | 7.9587 | 7.9135 | 7.8784 | 7.8356 | 7.787 | 7.7321 | 7.6585 | 7.6013 | 7.5506 | 7.5166 | 7.4787 | 7.4339 | 6.2408 | 6.1569 | 5.8336
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | System Transformation | Headroom (MW) | N/A | 8.1736 | 8.1131 | 8.017 | 7.9353 | 7.8475 | 7.7596 | 7.6135 | 6.5385 | 6.3745 | 6.2115 | 6.0245 | 5.8816 | 5.7549 | 5.6326 | 5.5128 | 5.3871 | 4.8831 | 4.3328 | 2.8531
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 53.3259 | 0.2642 | WPD Best View | Headroom (MW) | N/A | 8.1736 | 8.1131 | 8.017 | 7.9353 | 7.8475 | 7.7596 | 7.6135 | 6.5385 | 6.3745 | 6.2115 | 6.0245 | 5.8816 | 5.7549 | 5.6326 | 5.5128 | 5.3871 | 4.8831 | 4.3328 | 2.8531
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Consumer Transformation | Headroom (MW) | Thermal | 17.6783 | 17.5075 | 17.2233 | 16.9559 | 16.675 | 16.2731 | 15.7002 | 14.2276 | 13.6589 | 13.1026 | 11.512 | 10.842 | 9.2768 | 7.7128 | 6.2379 | 5.6466 | -3.8707 | -15.6915 | -26.0846
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Leading the Way | Headroom (MW) | Thermal | 17.7158 | 17.6021 | 17.4171 | 17.2724 | 17.1251 | 16.9678 | 16.7231 | 16.4991 | 16.2327 | 16.0165 | 14.8189 | 14.6009 | 14.3604 | 11.9191 | 11.7242 | 8.8746 | 0.82813 | -8.025 | -15.9762
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | Steady Progression | Headroom (MW) | N/A | 17.7198 | 17.6285 | 17.4634 | 17.366 | 17.2687 | 17.1729 | 17.076 | 16.9818 | 16.8494 | 16.7225 | 16.5838 | 16.443 | 16.3249 | 16.2162 | 16.1144 | 16.0056 | 15.6545 | 14.0492 | 13.4057
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | System Transformation | Headroom (MW) | N/A | 17.7087 | 17.5911 | 17.3982 | 17.2367 | 17.056 | 16.8768 | 16.594 | 16.3032 | 15.9736 | 15.6492 | 15.3071 | 14.0773 | 13.7749 | 13.4981 | 13.2425 | 12.9668 | 9.6056 | 4.9846 | 1.7845
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 53.1429 | 0.307 | WPD Best View | Headroom (MW) | N/A | 17.7087 | 17.5911 | 17.3982 | 17.2367 | 17.056 | 16.8768 | 16.594 | 16.3032 | 15.9736 | 15.6492 | 15.3071 | 14.0773 | 13.7749 | 13.4981 | 13.2425 | 12.9668 | 9.6056 | 4.9846 | 1.7845
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Consumer Transformation | Headroom (MW) | Thermal | 4.725 | 4.6449 | 4.5198 | 4.2087 | 3.8797 | 3.4944 | 3.0554 | 2.6277 | 1.2205 | -0.12873 | -0.65497 | -2.1067 | -2.6203 | -5.0207 | -5.4337 | -7.7173 | -15.0487 | -23.785 | -31.6108
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Leading the Way | Headroom (MW) | Thermal | 4.7366 | 4.6922 | 4.5937 | 4.3445 | 4.0644 | 3.7656 | 3.4444 | 3.1524 | 2.8084 | 2.5123 | 1.2308 | -0.040906 | -0.38456 | -0.74542 | -1.9427 | -2.2189 | -8.6842 | -14.2084 | -20.6654
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | Steady Progression | Headroom (MW) | N/A | 4.7443 | 4.6923 | 4.613 | 4.5696 | 4.5187 | 4.3789 | 4.2385 | 4.0979 | 3.9608 | 3.7241 | 3.5614 | 3.3141 | 3.0792 | 2.8555 | 2.6413 | 2.4431 | 1.9496 | 1.8157 | 1.4631
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | System Transformation | Headroom (MW) | Thermal | 4.733 | 4.684 | 4.5776 | 4.3261 | 4.0531 | 3.7573 | 3.4243 | 3.1242 | 2.7835 | 2.4574 | 2.1102 | 1.7931 | 0.5367 | 0.22514 | -0.062629 | -1.278 | -2.4619 | -3.9404 | -5.4703
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 53.041 | 0.1201 | WPD Best View | Headroom (MW) | Thermal | 4.744 | 4.6901 | 4.5988 | 4.4489 | 4.2961 | 4.1332 | 3.9513 | 3.7782 | 3.61 | 3.3381 | 3.144 | 2.8727 | 2.6047 | 2.3475 | 2.1079 | 0.95068 | 0.28841 | -0.0086644 | -1.3769
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Consumer Transformation | Headroom (MW) | Thermal | 13.1864 | 12.8091 | 12.1585 | 11.2103 | -9.3536 | -10.6559 | -63.1828 | -64.8484 | -66.5349 | -69.1075 | -70.9191 | -73.6502 | -78.3186 | -80.9725 | -83.513 | -85.2405 | -106.9682 | -132.3177 | -155.849
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Leading the Way | Headroom (MW) | Thermal | 13.291 | 12.9432 | 12.5098 | -7.6741 | -25.3834 | -60.1122 | -61.1654 | -62.2102 | -63.3228 | -64.2583 | -65.378 | -67.2251 | -68.2693 | -73.9612 | -80.0649 | -86.8698 | -109.6113 | -136.3281 | -160.492
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | Steady Progression | Headroom (MW) | Thermal | 13.2747 | 13.0486 | 12.6444 | 12.1658 | 11.6524 | 11.1472 | -8.8521 | -9.4323 | -27.0161 | -61.5749 | -62.228 | -62.7704 | -63.3487 | -63.8808 | -64.3767 | -64.8179 | -65.9594 | -69.7021 | -72.8128
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | System Transformation | Headroom (MW) | Thermal | 13.2626 | 12.9891 | 12.513 | 11.7996 | -8.5032 | -9.3299 | -61.2664 | -62.2568 | -63.3376 | -64.3717 | -65.4381 | -66.3835 | -67.2907 | -68.1129 | -69.828 | -70.5957 | -79.7603 | -92.1283 | -106.6574
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | 52.9917 | -0.4053 | WPD Best View | Headroom (MW) | Thermal | 13.2623 | 13.028 | 12.5846 | 12.0599 | -8.0323 | -8.6126 | -9.2495 | -9.9584 | -27.6982 | -62.3706 | -63.1707 | -63.9016 | -65.5963 | -66.2937 | -66.9478 | -67.5539 | -70.4906 | -77.3084 | -82.1053
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Consumer Transformation | Headroom (MW) | Thermal | 3.8956 | 3.8861 | 3.8674 | 3.8573 | 3.8477 | 3.8386 | 3.8253 | 3.8176 | 3.8065 | 3.8013 | 3.7826 | 3.6946 | 3.591 | 2.6143 | 2.5441 | 2.4856 | 2.3933 | 0.40629 | -0.96682
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Leading the Way | Headroom (MW) | Thermal | 3.8956 | 3.8839 | 3.8652 | 3.8525 | 3.8429 | 3.8339 | 3.809 | 3.8019 | 3.7822 | 3.779 | 3.6823 | 3.5894 | 3.4873 | 3.3949 | 3.3213 | 3.3294 | 2.3371 | 1.2234 | -1.1328
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | Steady Progression | Headroom (MW) | N/A | 3.8955 | 3.8858 | 3.8668 | 3.8561 | 3.8459 | 3.8358 | 3.8239 | 3.8143 | 3.8043 | 3.7953 | 3.7859 | 3.7776 | 3.7696 | 3.7624 | 3.7558 | 3.7502 | 3.726 | 3.7138 | 3.6121
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | System Transformation | Headroom (MW) | N/A | 3.8956 | 3.8859 | 3.8669 | 3.8565 | 3.8464 | 3.8365 | 3.8261 | 3.8168 | 3.8075 | 3.799 | 3.7912 | 3.7753 | 3.7692 | 3.7648 | 3.7622 | 3.7618 | 3.7789 | 3.7492 | 3.6908
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | 53.0368 | -0.4983 | WPD Best View | Headroom (MW) | N/A | 3.8956 | 3.8859 | 3.867 | 3.8567 | 3.8467 | 3.837 | 3.8276 | 3.8186 | 3.8102 | 3.8024 | 3.7953 | 3.7151 | 3.6272 | 3.548 | 3.4701 | 3.4039 | 3.3736 | 2.4606 | 2.408
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Consumer Transformation | Headroom (MW) | Thermal | 3.0565 | 3.0231 | 2.973 | 2.8155 | 2.6571 | 2.4832 | 2.2823 | 2.0026 | 1.7212 | 1.4593 | 1.2778 | 1.0259 | 0.79664 | 0.55719 | 0.32857 | 0.097549 | -2.1066 | -4.4714 | -6.8763
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Leading the Way | Headroom (MW) | Thermal | 3.0639 | 3.0504 | 3.0156 | 2.8834 | 2.767 | 2.6403 | 2.4348 | 2.227 | 2.0201 | 1.8439 | 1.6719 | 1.517 | 1.3794 | 1.2093 | -0.63886 | -0.79472 | -4.1095 | -6.2033 | -8.4231
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | Steady Progression | Headroom (MW) | Thermal | 3.0619 | 3.0468 | 3.0179 | 2.8942 | 2.7788 | 2.6649 | 2.5529 | 2.4499 | 2.3352 | 2.2301 | 2.1217 | 2.0115 | 1.9168 | 1.8194 | 1.726 | 1.6584 | 1.3784 | 1.3981 | -0.043436
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | System Transformation | Headroom (MW) | Thermal | 3.0604 | 3.0432 | 3 | 2.8643 | 2.7242 | 2.5822 | 2.4351 | 2.2838 | 2.1264 | 1.9741 | 1.82 | 1.6757 | 1.5462 | 1.4116 | 1.2971 | 1.1913 | -0.46962 | -2.057 | -3.7219
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | 52.9686 | -0.2947 | WPD Best View | Headroom (MW) | Thermal | 3.0619 | 3.0468 | 3.0179 | 2.8942 | 2.7788 | 2.6649 | 2.5529 | 2.4499 | 2.3352 | 2.2301 | 2.1217 | 2.0115 | 1.9168 | 1.8194 | 1.726 | 1.6584 | 1.3784 | 1.3981 | -0.043436
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Consumer Transformation | Headroom (MW) | Thermal | 6.3167 | 6.2695 | 6.1865 | 6.1168 | 6.0451 | 5.9543 | 5.8346 | 5.7282 | 5.6103 | 4.5996 | 4.4395 | 4.3343 | 2.3662 | 2.2488 | 1.2944 | 1.2277 | -4.6778 | -12.3011 | -17.8487
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Leading the Way | Headroom (MW) | Thermal | 6.3325 | 6.2197 | 6.164 | 6.1214 | 6.0991 | 6.0795 | 6.045 | 6.0211 | 6.0166 | 6.0322 | 6.0407 | 5.1219 | 5.17 | 3.9126 | 3.0499 | 1.3825 | -4.3867 | -11.9487 | -19.1328
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | Steady Progression | Headroom (MW) | N/A | 6.3312 | 6.2997 | 6.2311 | 6.2 | 6.1719 | 6.1367 | 6.1118 | 6.0796 | 6.0609 | 6.0276 | 6.0027 | 5.9866 | 5.9809 | 5.9674 | 5.9778 | 6.0005 | 6.1882 | 5.033 | 4.7315
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | System Transformation | Headroom (MW) | Thermal | 6.3289 | 6.2862 | 6.2202 | 6.1634 | 6.1223 | 6.0645 | 5.9844 | 5.9124 | 5.8457 | 5.779 | 5.7191 | 5.6599 | 5.6455 | 5.639 | 4.7182 | 4.7368 | 3.581 | 0.77893 | -2.8766
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | 53.0461 | -0.577 | WPD Best View | Headroom (MW) | Thermal | 6.3198 | 6.2845 | 6.2065 | 6.1543 | 6.0974 | 6.029 | 5.9606 | 5.8904 | 5.8221 | 5.7606 | 5.6714 | 5.6307 | 4.6597 | 4.6145 | 4.5995 | 4.5775 | 3.3071 | 0.46924 | -1.3287
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Consumer Transformation | Headroom (MW) | Thermal | 13.2602 | 13.1961 | 13.0897 | 12.9952 | 12.8988 | 12.7727 | 12.5901 | 12.4303 | 12.2567 | 12.0922 | 11.8717 | 10.7336 | 10.495 | 10.2852 | 10.1235 | 9.9379 | 5.7611 | 1.2027 | -3.0437
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Leading the Way | Headroom (MW) | Thermal | 13.2699 | 13.2226 | 13.1491 | 13.097 | 13.0454 | 12.9931 | 12.9147 | 12.8452 | 12.7587 | 12.6987 | 12.5879 | 12.4914 | 12.3448 | 10.0293 | 9.9754 | 7.3603 | 3.4177 | -2.8694 | -6.9911
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | Steady Progression | Headroom (MW) | N/A | 13.2707 | 13.2315 | 13.1528 | 13.1128 | 13.0743 | 13.0375 | 12.99 | 12.9533 | 12.9062 | 12.8689 | 12.806 | 12.7687 | 12.7154 | 12.6729 | 12.644 | 12.6059 | 12.5251 | 11.1815 | 10.9252
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | System Transformation | Headroom (MW) | N/A | 13.2678 | 13.2162 | 13.1376 | 13.0756 | 13.0101 | 12.9497 | 12.8502 | 12.7573 | 12.6391 | 12.534 | 12.4192 | 12.3237 | 12.231 | 12.1375 | 12.0661 | 11.9796 | 10.403 | 6.5917 | 3.9839
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | 53.0445 | -0.4003 | WPD Best View | Headroom (MW) | N/A | 13.2707 | 13.2315 | 13.1528 | 13.1128 | 13.0743 | 13.0375 | 12.99 | 12.9533 | 12.9062 | 12.8689 | 12.806 | 12.7687 | 12.7154 | 12.6729 | 12.644 | 12.6059 | 12.5251 | 11.1815 | 10.9252
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Consumer Transformation | Headroom (MW) | Thermal | 13.1768 | 13.054 | 12.8597 | 12.7191 | 12.5007 | 12.1689 | 11.7059 | 11.2353 | 10.7572 | 10.2253 | 9.6198 | 9.0736 | 7.5416 | 6.9902 | 6.4003 | 5.7627 | -0.62539 | -6.4812 | -13.4164
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Leading the Way | Headroom (MW) | Thermal | 13.2095 | 13.1185 | 12.9985 | 12.9769 | 12.8593 | 12.6981 | 12.4383 | 12.1638 | 11.836 | 11.4787 | 11.1029 | 10.8663 | 10.5397 | 9.011 | 6.0432 | 3.979 | -2.7425 | -9.8781 | -15.6533
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Steady Progression | Headroom (MW) | N/A | 13.2066 | 13.1504 | 13.0533 | 13.0375 | 12.982 | 12.9287 | 12.8745 | 12.8121 | 12.7356 | 12.6483 | 12.5484 | 12.4978 | 12.4116 | 12.347 | 12.2616 | 12.1604 | 11.8821 | 10.5207 | 10.1334
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | System Transformation | Headroom (MW) | Thermal | 13.2029 | 13.1294 | 13.0043 | 12.9565 | 12.8419 | 12.7111 | 12.5043 | 12.3014 | 12.0554 | 11.8209 | 11.5618 | 11.3857 | 11.1518 | 10.9758 | 10.7448 | 10.5017 | 6.9727 | 3.6643 | -1.7589
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | 52.9778 | -0.033 | WPD Best View | Headroom (MW) | N/A | 13.2066 | 13.1504 | 13.0533 | 13.0375 | 12.982 | 12.9287 | 12.8745 | 12.8121 | 12.7356 | 12.6483 | 12.5484 | 12.4978 | 12.4116 | 12.347 | 12.2616 | 12.1604 | 11.8821 | 10.5207 | 10.1334
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Consumer Transformation | Headroom (MW) | Thermal | 10.3012 | 10.2322 | 10.0921 | 9.7729 | 9.4397 | 9.0583 | 8.6463 | 8.2126 | 7.7842 | 7.3743 | 6.94 | 6.5071 | 6.0638 | 5.6535 | 5.2586 | 4.863 | 2.843 | 1.0088 | -0.87276
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Leading the Way | Headroom (MW) | N/A | 10.3243 | 10.2732 | 10.1775 | 9.9009 | 9.6091 | 9.3252 | 9.0199 | 8.698 | 8.3608 | 8.0904 | 7.8049 | 7.5113 | 7.1787 | 6.9005 | 6.6521 | 6.4105 | 5.006 | 3.4318 | 2.0263
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | Steady Progression | Headroom (MW) | N/A | 10.3162 | 10.2649 | 10.1814 | 10.037 | 9.8925 | 9.7473 | 9.6135 | 9.3826 | 9.1483 | 8.9154 | 8.6726 | 8.4469 | 8.2114 | 7.9927 | 7.7828 | 7.5943 | 7.0569 | 7.0128 | 6.6056
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | System Transformation | Headroom (MW) | N/A | 10.3161 | 10.2618 | 10.1606 | 9.893 | 9.6196 | 9.3283 | 9.0082 | 8.7021 | 8.3818 | 8.0592 | 7.7446 | 7.4299 | 7.1235 | 6.8328 | 6.5589 | 6.2946 | 5.3365 | 4.7614 | 4.0488
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | 53.0866 | -0.224 | WPD Best View | Headroom (MW) | N/A | 10.3168 | 10.2631 | 10.1643 | 10.0115 | 9.8492 | 9.681 | 9.4819 | 9.2042 | 8.9136 | 8.63 | 8.3493 | 8.0748 | 7.8002 | 7.5481 | 7.3011 | 7.0765 | 6.3519 | 6.0561 | 5.5267
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Consumer Transformation | Headroom (MW) | Thermal | 2.9669 | 2.9355 | 2.8777 | 2.7208 | 2.5646 | 2.3755 | 2.1616 | 1.9539 | 1.7578 | 1.5692 | 1.3782 | 1.2095 | 1.056 | 0.90714 | 0.7663 | 0.61377 | -0.32696 | -1.4531 | -2.5955
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Leading the Way | Headroom (MW) | Thermal | 2.9828 | 2.9623 | 2.9275 | 2.801 | 2.675 | 2.5464 | 2.4015 | 2.2616 | 2.1315 | 2.0476 | 1.9602 | 1.9065 | 1.8597 | 1.8101 | 1.761 | 1.6919 | 1.0955 | 0.145 | -0.95633
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | Steady Progression | Headroom (MW) | N/A | 2.98 | 2.957 | 2.9285 | 2.8157 | 2.6945 | 2.5836 | 2.4886 | 2.3833 | 2.2747 | 2.1682 | 2.0635 | 1.9694 | 1.8745 | 1.7863 | 1.704 | 1.6412 | 1.5127 | 1.6667 | 1.4516
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | System Transformation | Headroom (MW) | N/A | 2.9784 | 2.9539 | 2.9109 | 2.7778 | 2.6397 | 2.5051 | 2.3541 | 2.1981 | 2.0354 | 1.8908 | 1.7348 | 1.595 | 1.471 | 1.3544 | 1.2535 | 1.1674 | 0.86607 | 0.61209 | 0.20532
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | 53.1421 | -0.2404 | WPD Best View | Headroom (MW) | N/A | 2.9784 | 2.9533 | 2.9102 | 2.7802 | 2.6466 | 2.5166 | 2.3704 | 2.2205 | 2.0603 | 1.9178 | 1.7659 | 1.6287 | 1.5016 | 1.3852 | 1.2788 | 1.1922 | 0.92 | 0.83422 | 0.50237
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Consumer Transformation | Headroom (MW) | Thermal | 24.6522 | 24.3083 | 23.6744 | 23.2003 | 22.7172 | 22.0879 | 21.0397 | 20.0346 | 19.0656 | 18.1037 | 16.1108 | 15.2154 | 13.4215 | 10.7295 | 9.0601 | 8.2218 | -3.977 | -23.6616 | -43.9687
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Leading the Way | Headroom (MW) | Thermal | 24.7134 | 24.1479 | 23.6761 | 23.3648 | 23.1038 | 22.8547 | 22.2919 | 21.9676 | 21.5659 | 21.3551 | 21.051 | 20.666 | 19.4644 | 18.4343 | 13.8202 | 8.7073 | -5.7876 | 2.9505 | -14.8362
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | Steady Progression | Headroom (MW) | Thermal | 24.6931 | 24.4606 | 23.9972 | 22.7295 | -1.0967 | -1.3168 | -10.799 | -23.3726 | -32.8292 | -42.2908 | -50.8817 | -58.3864 | -67.7973 | -74.0655 | -78.7527 | -81.8697 | -96.5559 | -112.8754 | -123.0118
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | System Transformation | Headroom (MW) | Thermal | 24.6915 | 24.4199 | 23.9121 | 23.5782 | 23.2265 | 22.8629 | 22.3302 | 21.8241 | 21.2712 | 20.6671 | 20.0371 | 19.5825 | 19.1922 | 18.8763 | 18.6114 | 18.3889 | 14.5369 | 5.1886 | -5.0091
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | 53.1088 | -1.385 | WPD Best View | Headroom (MW) | Thermal | 24.6522 | 24.3083 | 23.6744 | 23.2003 | 22.7172 | 22.0879 | 21.0397 | 20.0346 | 19.0656 | 18.1037 | 16.1108 | 15.2228 | 13.4432 | 10.7768 | 9.1075 | 8.2691 | -3.977 | -23.6616 | -43.9687
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Consumer Transformation | Headroom (MW) | N/A | 12.0893 | 12.0534 | 11.9965 | 11.9552 | 11.908 | 11.8456 | 11.7706 | 11.6966 | 11.6307 | 11.5697 | 11.4913 | 11.4418 | 11.3988 | 11.3665 | 11.3271 | 11.284 | 9.9406 | 8.3513 | 6.9441
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Leading the Way | Headroom (MW) | N/A | 12.094 | 12.0751 | 12.0292 | 12.013 | 11.9914 | 11.974 | 11.9438 | 11.9371 | 11.9282 | 11.9328 | 11.9482 | 11.9634 | 12.0067 | 12.01 | 12.012 | 10.3796 | 9.2828 | 7.7212 | 5.8185
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | Steady Progression | Headroom (MW) | N/A | 12.0928 | 12.0714 | 12.0297 | 12.0079 | 11.9791 | 11.9609 | 11.9433 | 11.9179 | 11.9052 | 11.8821 | 11.869 | 11.8544 | 11.8443 | 11.8474 | 11.8477 | 11.855 | 11.9704 | 12.1579 | 12.128
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | System Transformation | Headroom (MW) | N/A | 12.0916 | 12.0682 | 12.0141 | 11.9867 | 11.9502 | 11.9143 | 11.8592 | 11.8187 | 11.7677 | 11.7194 | 11.676 | 11.6471 | 11.6269 | 11.6174 | 11.6178 | 11.6189 | 11.6959 | 10.6138 | 10.5111
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | 53.0628 | -1.4824 | WPD Best View | Headroom (MW) | N/A | 12.0893 | 12.0534 | 11.9965 | 11.9552 | 11.908 | 11.8456 | 11.7706 | 11.6966 | 11.6307 | 11.5697 | 11.4913 | 11.4418 | 11.3988 | 11.3665 | 11.3271 | 11.284 | 9.9406 | 8.3513 | 6.9441
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Consumer Transformation | Headroom (MW) | N/A | 15.6342 | 15.5861 | 15.4921 | 15.4423 | 15.3922 | 15.3425 | 15.1375 | 14.8724 | 14.6263 | 14.3686 | 14.0786 | 13.8917 | 13.6889 | 12.5637 | 12.3495 | 12.143 | 10.6024 | 6.6393 | 2.6164
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Leading the Way | Headroom (MW) | N/A | 15.6355 | 15.5691 | 15.4754 | 15.4029 | 15.3533 | 15.3039 | 15.1088 | 15.0633 | 14.9651 | 14.9266 | 14.8366 | 14.7451 | 14.6355 | 14.5165 | 14.514 | 13.7225 | 10.9286 | 8.4793 | 4.9436
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | Steady Progression | Headroom (MW) | Thermal | 15.6331 | 15.5849 | 15.4904 | 15.4366 | 0.0060202 | -0.04497 | -4.2143 | -11.4407 | -15.5965 | -19.7455 | -24.2996 | -28.4292 | -32.5554 | -36.6761 | -39.2902 | -42.3759 | -53.722 | -65.1901 | -72.7627
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | System Transformation | Headroom (MW) | N/A | 15.6341 | 15.5859 | 15.4915 | 15.4413 | 15.3905 | 15.3398 | 15.284 | 15.2347 | 15.1707 | 14.9988 | 14.8149 | 14.7266 | 14.6321 | 14.555 | 14.4691 | 14.4166 | 14.1049 | 12.3418 | 10.2638
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | 53.1155 | -1.3441 | WPD Best View | Headroom (MW) | N/A | 15.6342 | 15.5861 | 15.4921 | 15.4423 | 15.3922 | 15.3425 | 15.1375 | 14.8724 | 14.6263 | 14.3686 | 14.0786 | 13.8917 | 13.6889 | 12.5637 | 12.3495 | 12.143 | 10.6024 | 6.6393 | 2.6164
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Consumer Transformation | Headroom (MW) | N/A | 15.6182 | 15.5136 | 15.3235 | 15.1719 | 15.0067 | 14.7772 | 14.4606 | 14.1632 | 13.8723 | 13.5685 | 13.2631 | 12.9685 | 12.6811 | 12.4504 | 12.2255 | 11.9762 | 10.3398 | 8.3915 | 6.8159
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Leading the Way | Headroom (MW) | N/A | 15.6425 | 15.2642 | 15.1383 | 15.0437 | 14.946 | 14.8623 | 14.7326 | 14.6083 | 14.4793 | 14.3683 | 14.2715 | 14.1958 | 14.1393 | 14.1358 | 14.146 | 14.118 | 13.4699 | 11.4224 | 10.1528
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | Steady Progression | Headroom (MW) | N/A | 15.6369 | 15.5773 | 15.4585 | 14.3705 | 14.2997 | 14.2444 | 14.1793 | 14.1004 | 14.0328 | 13.9631 | 13.5361 | 13.4685 | 13.4057 | 13.3767 | 13.3643 | 13.3578 | 13.3656 | 13.3053 | 12.877
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | System Transformation | Headroom (MW) | N/A | 15.6374 | 15.559 | 15.4249 | 15.3328 | 15.2132 | 15.1054 | 14.9375 | 14.765 | 14.5845 | 14.4111 | 14.2341 | 14.0737 | 13.934 | 13.8542 | 13.7875 | 13.7335 | 13.4063 | 12.8231 | 12.3702
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | 53.1021 | -1.3758 | WPD Best View | Headroom (MW) | N/A | 15.6182 | 15.5136 | 15.3235 | 15.1719 | 15.0067 | 14.7772 | 14.4606 | 14.1632 | 13.8723 | 13.5685 | 13.2631 | 12.9685 | 12.6811 | 12.4504 | 12.2255 | 11.9762 | 10.3398 | 8.3915 | 6.8159
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Consumer Transformation | Headroom (MW) | Thermal | 9.0935 | 9.0632 | 9.0098 | 8.9868 | 8.9566 | 8.9343 | 8.8851 | 8.8672 | 8.8334 | 8.8324 | 7.8734 | 7.8476 | 6.8906 | 6.837 | 5.9462 | 5.9478 | 0.40329 | -5.6751 | -11.8914
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Leading the Way | Headroom (MW) | Thermal | 9.0972 | 9.078 | 9.0277 | 9.0066 | 8.999 | 8.9876 | 8.9239 | 8.9042 | 8.8682 | 8.8551 | 8.8075 | 8.7401 | 7.7919 | 7.0448 | 5.425 | 2.8539 | -3.0482 | -10.6788 | -16.3162
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | Steady Progression | Headroom (MW) | N/A | 9.0921 | 9.0682 | 9.0194 | 8.9959 | 8.9658 | 8.9464 | 8.9299 | 8.9071 | 8.8962 | 8.8893 | 8.8686 | 8.8386 | 8.8178 | 8.7986 | 8.7806 | 8.7642 | 8.6851 | 8.0322 | 6.5589
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | System Transformation | Headroom (MW) | Thermal | 9.0929 | 9.0682 | 9.0098 | 8.9758 | 8.9516 | 8.9304 | 8.8982 | 8.8652 | 8.8473 | 8.8339 | 8.8286 | 8.8174 | 8.8339 | 8.8196 | 8.8082 | 8.8002 | 5.7974 | 3.1625 | -0.69156
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | 53.0007 | -1.5997 | WPD Best View | Headroom (MW) | Thermal | 9.0935 | 9.0632 | 9.0098 | 8.9868 | 8.9566 | 8.9343 | 8.8851 | 8.8672 | 8.8334 | 8.8324 | 7.8734 | 7.855 | 6.9122 | 6.8844 | 5.9935 | 5.9951 | 0.40329 | -5.6751 | -11.8914
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Consumer Transformation | Headroom (MW) | Fault level | -30.3358 | -30.3827 | -30.454 | -30.5509 | -30.6542 | -30.7922 | -31.0064 | -31.2123 | -31.4249 | -31.6531 | -31.8938 | -32.1374 | -32.3863 | -32.6337 | -32.8821 | -33.1568 | -34.5051 | -35.7653 | -36.907
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Leading the Way | Headroom (MW) | Fault level | -30.1232 | -30.1502 | -30.1812 | -30.225 | -30.2749 | -30.3207 | -30.4078 | -30.491 | -30.5956 | -30.6904 | -30.7894 | -30.8961 | -30.9859 | -31.1023 | -31.2041 | -31.3284 | -31.8406 | -18.0364 | -18.5612
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | Steady Progression | Headroom (MW) | Fault level | -25.075 | -25.0872 | -25.0992 | -25.1116 | -25.1243 | -25.1349 | -27.5423 | -29.9574 | -32.3746 | -34.7995 | -36.668 | -38.3809 | -40.8071 | -43.2332 | -44.3177 | -44.3465 | -48.2808 | -53.263 | -53.4761
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | System Transformation | Headroom (MW) | Fault level | -29.2739 | -29.2996 | -29.3291 | -29.37 | -29.4151 | -29.4666 | -29.5598 | -29.653 | -29.7698 | -29.8794 | -29.9947 | -30.1107 | -30.2188 | -30.3352 | -30.4447 | -30.5711 | -31.119 | -31.5694 | -31.9476
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | 53.085 | -1.3729 | WPD Best View | Headroom (MW) | Fault level | -28.8371 | -28.8817 | -28.9495 | -29.0416 | -29.1398 | -29.271 | -29.4746 | -29.6704 | -29.8724 | -30.0893 | -30.3182 | -30.5497 | -30.7864 | -31.0215 | -31.2577 | -31.5187 | -32.8004 | -33.9984 | -35.0837
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Consumer Transformation | Headroom (MW) | Thermal | 4.0489 | 4.0203 | 3.9596 | 3.9073 | 3.8617 | 3.7954 | 3.6771 | 3.594 | 3.528 | 3.4527 | 3.374 | 3.3096 | 3.2775 | 2.2926 | 2.2533 | 2.2017 | 1.5903 | -2.9008 | -8.4393
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Leading the Way | Headroom (MW) | Thermal | 4.0589 | 4.0456 | 4.0196 | 4.0048 | 3.9945 | 3.9961 | 3.9845 | 3.9766 | 3.9823 | 4.0234 | 4.0397 | 3.9697 | 3.9082 | 3.8389 | 0.91356 | 0.93841 | -2.485 | -5.8099 | -10.3114
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | Steady Progression | Headroom (MW) | Thermal | 4.0526 | 4.0395 | 3.9993 | 3.9845 | -4.2262 | -4.236 | -7.3307 | -10.4241 | -13.5064 | -16.5945 | -18.5188 | -20.2618 | -23.3334 | -23.3141 | -24.3941 | -24.3564 | -24.32 | -24.3627 | -24.5621
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | System Transformation | Headroom (MW) | Thermal | 4.0524 | 4.0288 | 3.9965 | 3.9639 | 3.9296 | 3.8951 | 3.8349 | 3.7788 | 3.7167 | 3.6744 | 3.6179 | 3.6089 | 3.5986 | 3.6062 | 3.6289 | 3.6515 | 3.8839 | 1.1813 | -1.8573
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | 53.1179 | -1.4324 | WPD Best View | Headroom (MW) | Thermal | 4.0489 | 4.0203 | 3.9596 | 3.9073 | 3.8617 | 3.7954 | 3.6771 | 3.594 | 3.528 | 3.4527 | 3.374 | 3.3096 | 3.2775 | 2.2926 | 2.2533 | 2.2017 | 1.5903 | -2.9008 | -8.4393
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Consumer Transformation | Headroom (MW) | Thermal | 27.5695 | 27.2695 | 26.7663 | 26.2794 | 25.7597 | 25.0403 | 24.0182 | 23.0995 | 22.2254 | 21.3395 | 20.3135 | 17.5209 | 16.692 | 15.8139 | 14.1167 | 13.2469 | 2.2255 | -13.5095 | -29.4168
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Leading the Way | Headroom (MW) | Thermal | 27.6538 | 27.4851 | 27.1829 | 26.9382 | 26.6954 | 26.4165 | 25.9809 | 25.6202 | 25.2914 | 25.0708 | 24.8493 | 24.7251 | 24.797 | 23.4394 | 19.8847 | 16.3429 | 6.1398 | -7.1236 | -21.6473
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Steady Progression | Headroom (MW) | N/A | 27.6563 | 27.4883 | 27.1923 | 27.0253 | 18.6549 | 18.5024 | 17.2977 | 15.0784 | 12.8818 | 10.6658 | 9.3425 | 8.15 | 8.0268 | 7.928 | 7.51 | 7.4452 | 7.9089 | 7.0857 | 5.8484
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | System Transformation | Headroom (MW) | N/A | 27.6292 | 27.4173 | 27.058 | 26.7573 | 26.4733 | 26.1309 | 25.6303 | 25.1686 | 24.633 | 24.1593 | 23.6386 | 23.1948 | 22.8726 | 22.5567 | 22.3112 | 22.0527 | 20.2304 | 11.9516 | 2.6021
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | WPD Best View | Headroom (MW) | Thermal | 27.57 | 27.2699 | 26.7665 | 26.2799 | 25.7604 | 25.0415 | 24.0202 | 23.1028 | 22.2302 | 21.3471 | 20.325 | 17.5365 | 16.7119 | 15.8378 | 14.1434 | 13.2712 | 2.2187 | -13.5295 | -29.5124
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Consumer Transformation | Headroom (MW) | Thermal | 6.3434 | 6.2946 | 6.1946 | 6.106 | 6.0245 | 5.9029 | 5.7268 | 5.5733 | 5.4125 | 5.2577 | 5.0831 | 4.0137 | 3.8929 | 3.7536 | 2.7345 | 2.623 | 0.7153 | -4.7358 | -9.7062
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Leading the Way | Headroom (MW) | Thermal | 6.3636 | 6.3283 | 6.2776 | 6.2354 | 6.2152 | 6.1854 | 6.1406 | 6.1063 | 6.0455 | 6.031 | 6.0194 | 6.0498 | 6.1087 | 6.155 | 3.6159 | 3.6433 | -1.0862 | -3.3533 | -9.0223
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | Steady Progression | Headroom (MW) | N/A | 6.3625 | 6.331 | 6.2673 | 6.2379 | 6.2097 | 6.1904 | 6.1568 | 6.127 | 6.1023 | 6.0627 | 6.0328 | 6.0167 | 5.998 | 5.9988 | 6.0111 | 6.0329 | 6.2681 | 6.4768 | 6.1358
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | System Transformation | Headroom (MW) | Thermal | 6.3589 | 6.3144 | 6.249 | 6.1874 | 6.1442 | 6.0757 | 5.981 | 5.8887 | 5.7735 | 5.6868 | 5.591 | 5.5295 | 5.4726 | 5.4515 | 5.4511 | 5.4416 | 5.5488 | 3.1006 | -0.070763
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | 53.0884 | -1.1444 | WPD Best View | Headroom (MW) | Thermal | 6.3434 | 6.2946 | 6.1946 | 6.106 | 6.0245 | 5.9029 | 5.7268 | 5.5733 | 5.4125 | 5.2577 | 5.0831 | 4.0137 | 3.8929 | 3.7536 | 2.7345 | 2.623 | 0.7153 | -4.7358 | -9.7062
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Consumer Transformation | Headroom (MW) | Thermal | 10.7409 | 10.706 | 10.6509 | 10.5983 | 10.5388 | 10.4663 | 10.35 | 10.2543 | 10.1657 | 10.0724 | 9.9642 | 8.9379 | 8.8472 | 8.7675 | 8.7009 | 8.6209 | 5.8117 | 0.66906 | -3.5703
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Leading the Way | Headroom (MW) | Thermal | 10.7545 | 10.7281 | 10.6864 | 10.6628 | 10.6391 | 10.6154 | 10.5778 | 10.5521 | 10.5249 | 10.51 | 10.4905 | 10.4852 | 10.4954 | 9.2275 | 8.3149 | 6.622 | 3.8447 | -1.3658 | -5.4035
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | Steady Progression | Headroom (MW) | N/A | 10.7545 | 10.7258 | 10.6891 | 10.6693 | 10.6429 | 10.6266 | 10.6104 | 10.5854 | 10.5644 | 10.5496 | 10.525 | 10.5084 | 10.4866 | 10.4784 | 10.4752 | 10.472 | 10.5405 | 9.2972 | 9.147
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | System Transformation | Headroom (MW) | N/A | 10.7529 | 10.7218 | 10.6719 | 10.6366 | 10.601 | 10.5646 | 10.51 | 10.4541 | 10.3802 | 10.3207 | 10.2657 | 10.2202 | 10.1889 | 10.1597 | 10.1384 | 10.1261 | 8.8273 | 5.1923 | 2.3562
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | 53.1047 | -1.0233 | WPD Best View | Headroom (MW) | Thermal | 10.7409 | 10.706 | 10.6509 | 10.5983 | 10.5388 | 10.4663 | 10.35 | 10.2543 | 10.1657 | 10.0724 | 9.9642 | 8.9379 | 8.8472 | 8.7675 | 8.7009 | 8.6209 | 5.8117 | 0.66906 | -3.5703
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Consumer Transformation | Headroom (MW) | Fault level | 14.8871 | 14.7444 | 14.5467 | 14.2839 | 13.9754 | 13.5332 | 12.9048 | 12.2702 | 11.6696 | 11.0195 | 10.3006 | 9.5958 | 8.8883 | 8.1697 | 7.484 | 6.7503 | 1.2339 | -3.0839 | -7.0466
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Leading the Way | Headroom (MW) | N/A | 14.8279 | 14.7571 | 14.6577 | 14.5184 | 14.3371 | 14.1287 | 13.8102 | 13.4595 | 13.1442 | 12.8233 | 12.5218 | 12.2484 | 12.0051 | 11.6994 | 11.4289 | 9.6832 | 8.3513 | 3.8187 | 0.43955
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | Steady Progression | Headroom (MW) | N/A | 12.3586 | 12.3231 | 12.2865 | 12.2484 | 12.2065 | 12.1591 | 12.1124 | 12.0511 | 11.9824 | 11.8995 | 11.7985 | 11.7101 | 11.6158 | 11.5263 | 11.4368 | 11.3257 | 10.8971 | 10.4277 | 9.8892
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | System Transformation | Headroom (MW) | N/A | 14.4098 | 14.3452 | 14.2579 | 14.14 | 14.0008 | 13.8352 | 13.565 | 13.2851 | 12.9734 | 12.659 | 12.3247 | 12.0119 | 11.7005 | 11.3886 | 11.0816 | 10.7424 | 9.2644 | 7.1303 | 5.1754
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | 53.0415 | -1.1987 | WPD Best View | Headroom (MW) | Fault level | 14.1514 | 14.0158 | 13.8278 | 13.578 | 13.2848 | 12.8646 | 12.2676 | 11.6644 | 11.0933 | 10.4752 | 9.7916 | 9.1217 | 8.4492 | 7.766 | 7.1141 | 6.4139 | 1.1636 | -2.9497 | -6.7235
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Consumer Transformation | Headroom (MW) | N/A | 14.9335 | 14.898 | 14.8287 | 14.7906 | 14.7532 | 14.7164 | 14.6804 | 14.6453 | 14.6023 | 14.5694 | 14.529 | 14.4903 | 14.4533 | 14.4178 | 14.3923 | 14.3678 | 13.3018 | 13.0998 | 11.1379
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Leading the Way | Headroom (MW) | N/A | 14.9335 | 14.898 | 14.8287 | 14.7907 | 14.7532 | 14.7165 | 14.6807 | 14.6458 | 14.6034 | 14.5715 | 14.5415 | 14.5047 | 14.4787 | 14.4456 | 14.4221 | 14.3991 | 12.8154 | 12.4135 | 11.9304
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | Steady Progression | Headroom (MW) | Thermal | 14.9334 | 14.8978 | 14.8283 | 14.79 | 6.5498 | 6.5125 | 5.4503 | 3.3634 | 1.2769 | -0.80898 | -1.9725 | -3.0382 | -3.0717 | -3.1046 | -3.4919 | -3.5231 | -3.672 | -3.7955 | -3.9561
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | System Transformation | Headroom (MW) | N/A | 14.9334 | 14.8979 | 14.8284 | 14.7901 | 14.7523 | 14.7151 | 14.6783 | 14.6421 | 14.6066 | 14.5716 | 14.5374 | 14.504 | 14.4717 | 14.4316 | 14.4017 | 14.3737 | 14.2516 | 14.1247 | 13.3334
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | 53.0707 | -1.2611 | WPD Best View | Headroom (MW) | N/A | 14.9335 | 14.898 | 14.8287 | 14.7906 | 14.7532 | 14.7164 | 14.6804 | 14.6453 | 14.6023 | 14.5694 | 14.529 | 14.4903 | 14.4533 | 14.4178 | 14.3923 | 14.3678 | 13.3053 | 13.1305 | 11.1379
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Consumer Transformation | Headroom (MW) | Thermal | 15.2365 | 14.8616 | 14.1829 | 13.5534 | 12.831 | 11.8195 | 10.2817 | 6.1918 | 4.7246 | 3.1989 | 1.5653 | -0.96217 | -4.3416 | -5.885 | -7.3201 | -8.9186 | -21.8459 | -37.8744 | -52.3534
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Leading the Way | Headroom (MW) | Thermal | 15.2939 | 14.9674 | 14.4095 | 14.0048 | 13.6923 | 10.7769 | 9.5727 | 9.1665 | 8.5276 | 8.1435 | 7.5528 | 6.9211 | 8.3978 | 2.2991 | -0.15049 | -5.0396 | -15.7887 | -16.2817 | -27.7081
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | Steady Progression | Headroom (MW) | Thermal | 15.2816 | 14.9996 | 14.4762 | 14.1695 | 7.7472 | 7.4591 | 4.9782 | -0.44351 | -5.8681 | -10.7953 | -14.059 | -17.1496 | -18.5604 | -19.9413 | -20.5914 | -20.8276 | -23.1489 | -26.1478 | -29.695
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | System Transformation | Headroom (MW) | Thermal | 15.2785 | 14.973 | 14.4059 | 14.0263 | 13.6723 | 13.1861 | 12.3994 | 9.1169 | 8.2697 | 7.336 | 6.4395 | 5.6107 | 4.843 | 4.1212 | 3.4886 | 2.8149 | 2.2914 | -6.9353 | -13.2699
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | 53.0885 | -1.2458 | WPD Best View | Headroom (MW) | Thermal | 15.2365 | 14.8616 | 14.1829 | 13.5534 | 12.831 | 11.8195 | 10.2817 | 6.1918 | 4.7246 | 3.1989 | 1.5653 | -0.96217 | -4.3416 | -5.885 | -7.3201 | -8.9186 | -21.8459 | -37.8744 | -52.3534
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Consumer Transformation | Headroom (MW) | Fault level | -22.256 | -22.3563 | -22.5067 | -22.6853 | -22.8959 | -23.2125 | -23.6816 | -24.1353 | -24.6143 | -25.1035 | -25.6657 | -27.2162 | -27.7822 | -28.3659 | -28.898 | -29.4951 | -37.0076 | -41.9039 | -47.6226
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Leading the Way | Headroom (MW) | Fault level | -22.0784 | -22.1228 | -22.1795 | -22.2482 | -22.3485 | -22.4578 | -22.6495 | -22.8244 | -23.0533 | -23.2877 | -23.5385 | -23.7955 | -24.0354 | -24.2962 | -26.912 | -27.1627 | -32.9928 | -28.6264 | -31.8785
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | Steady Progression | Headroom (MW) | Fault level | -18.3684 | -18.394 | -18.419 | -18.4435 | -18.4694 | -18.4951 | -18.5247 | -22.1626 | -25.8057 | -25.8681 | -27.9233 | -29.7978 | -29.8729 | -29.9392 | -30.0044 | -30.0818 | -30.4429 | -30.8434 | -32.5697
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | System Transformation | Headroom (MW) | Fault level | -21.4561 | -21.5026 | -21.5644 | -21.6415 | -21.7445 | -21.8572 | -22.0612 | -22.2571 | -22.5074 | -22.7621 | -23.0221 | -23.2648 | -23.5129 | -23.7627 | -24.0032 | -24.2716 | -25.4883 | -29.8902 | -32.7575
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | 53.0886 | -1.2451 | WPD Best View | Headroom (MW) | Fault level | -21.1565 | -21.2519 | -21.3948 | -21.5646 | -21.7648 | -22.0658 | -22.5116 | -22.9429 | -23.3983 | -23.8633 | -24.3978 | -25.8716 | -26.4097 | -26.9645 | -27.4704 | -28.038 | -35.1793 | -39.8338 | -45.2699
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Consumer Transformation | Headroom (MW) | Thermal | 1.7533 | 1.7027 | 1.5926 | 1.4901 | 1.3987 | 1.268 | 1.0811 | -1.6723 | -1.8392 | -1.993 | -2.1884 | -2.36 | -4.3785 | -4.5352 | -4.6469 | -4.7784 | -5.5666 | -11.2019 | -15.6229
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Leading the Way | Headroom (MW) | Thermal | 1.7748 | 1.7431 | 1.663 | 1.612 | 1.5611 | -1.0533 | -1.1525 | -1.2302 | -1.274 | -1.2998 | -1.3249 | -1.3248 | 0.75421 | 0.76295 | 0.81354 | -3.5074 | -6.0917 | -11.3179 | -15.8089
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | Steady Progression | Headroom (MW) | Thermal | 1.7677 | 1.7349 | 1.6778 | 1.6475 | 1.6068 | 1.5775 | 1.5476 | 1.5165 | 1.4858 | -1.1154 | -1.1659 | -1.1914 | -1.2086 | -1.2305 | -1.2356 | -1.2319 | -1.0781 | -1.008 | -1.2945
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | System Transformation | Headroom (MW) | Thermal | 1.7676 | 1.7336 | 1.6607 | 1.608 | 1.5493 | 1.4882 | 1.3841 | -1.2666 | -1.3677 | -1.4609 | -1.5538 | -1.6289 | -1.686 | -1.7334 | -1.7486 | -1.7714 | 0.26299 | -2.5609 | -6.2067
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | 53.0473 | -1.1029 | WPD Best View | Headroom (MW) | Thermal | 1.7533 | 1.7027 | 1.5926 | 1.4901 | 1.3987 | 1.268 | 1.0811 | -1.6723 | -1.8392 | -1.993 | -2.1884 | -2.36 | -4.3785 | -4.5352 | -4.6469 | -4.7784 | -5.5666 | -11.2019 | -15.6229
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Consumer Transformation | Headroom (MW) | Thermal | 8.3296 | 8.1745 | 7.9495 | 7.715 | 7.4621 | 7.1136 | 6.6068 | 6.1423 | 5.6813 | 5.1695 | 4.63 | 4.1133 | 3.6099 | 3.1033 | 2.5922 | 2.0382 | -0.8228 | -3.6999 | -4.2575
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Leading the Way | Headroom (MW) | N/A | 8.3606 | 8.2712 | 8.1327 | 8.023 | 7.8896 | 7.7711 | 7.5667 | 7.4123 | 7.2076 | 7.0019 | 6.8138 | 6.6258 | 6.4866 | 6.3032 | 6.139 | 5.9356 | 4.9199 | 6.6408 | 5.2294
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | Steady Progression | Headroom (MW) | N/A | 8.3641 | 8.2873 | 8.1681 | 8.0918 | 8.0206 | 7.9477 | 7.8738 | 7.7899 | 7.7042 | 7.6031 | 7.4978 | 7.3908 | 7.2945 | 7.2143 | 7.1362 | 7.0488 | 6.8318 | 6.6582 | 6.0952
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | System Transformation | Headroom (MW) | N/A | 8.3575 | 8.2552 | 8.105 | 7.9716 | 7.8236 | 7.6729 | 7.417 | 7.1904 | 6.9115 | 6.6322 | 6.3452 | 6.0833 | 5.8403 | 5.6068 | 5.3871 | 5.1527 | 4.2427 | 3.3615 | 5.4657
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | 53.1271 | -1.2911 | WPD Best View | Headroom (MW) | Thermal | 8.3296 | 8.1745 | 7.9495 | 7.715 | 7.4621 | 7.1136 | 6.6068 | 6.1423 | 5.6813 | 5.1695 | 4.63 | 4.1133 | 3.6099 | 3.1033 | 2.5922 | 2.0382 | -0.8228 | -3.6999 | -4.2575
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Consumer Transformation | Headroom (MW) | N/A | 24.4342 | 24.334 | 24.1268 | 24.0081 | 23.9335 | 23.8196 | 23.5594 | 23.2403 | 22.9435 | 22.6383 | 22.3509 | 22.0412 | 21.7499 | 21.4479 | 21.1556 | 20.8345 | 19.0783 | 17.1982 | 14.4565
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Leading the Way | Headroom (MW) | N/A | 24.4381 | 24.3285 | 24.1246 | 23.9896 | 23.9314 | 23.8171 | 23.4737 | 23.3656 | 23.2284 | 23.13 | 23.047 | 22.8602 | 22.6762 | 17.056 | 16.9106 | 16.7314 | 15.7894 | 17.6278 | 16.3155
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | Steady Progression | Headroom (MW) | Thermal | 24.4311 | 24.3281 | 24.1184 | 23.9981 | 17.7608 | 17.6469 | 15.4732 | 13.3136 | 11.1509 | 8.9939 | 7.655 | 6.4074 | 5.279 | 4.154 | 3.6471 | 3.5526 | 1.6028 | -0.92382 | -1.5423
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | System Transformation | Headroom (MW) | N/A | 24.4341 | 24.3339 | 24.1266 | 24.0077 | 23.9328 | 23.8184 | 23.705 | 23.5937 | 23.4559 | 23.2401 | 23.0552 | 22.8514 | 22.6595 | 22.4776 | 22.3057 | 22.1249 | 21.3474 | 20.4994 | 19.5165
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | 53.1236 | -1.2316 | WPD Best View | Headroom (MW) | N/A | 24.4342 | 24.334 | 24.1268 | 24.0081 | 23.9335 | 23.8196 | 23.5594 | 23.2403 | 22.9435 | 22.6383 | 22.3509 | 22.0412 | 21.7499 | 21.4479 | 21.1556 | 20.8345 | 19.0783 | 17.1982 | 14.4565
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Consumer Transformation | Headroom (MW) | Thermal | 36.7502 | 36.3867 | 35.7129 | 35.0413 | 34.3184 | 33.3344 | 31.9424 | 30.5508 | 29.1511 | 27.6958 | 16.0763 | 14.5587 | 13.0451 | 11.6159 | 7.4334 | 5.8581 | -7.425 | -21.7051 | -35.4988
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Leading the Way | Headroom (MW) | Thermal | 36.8643 | 36.7434 | 36.3426 | 35.9938 | 35.5941 | 35.2207 | 24.6023 | 23.9369 | 23.2167 | 19.1604 | 18.4735 | 17.876 | 13.2269 | 12.8099 | 9.0046 | 5.0391 | -9.1995 | -16.0283 | -33.8044
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | Steady Progression | Headroom (MW) | N/A | 36.8264 | 36.6352 | 36.2309 | 30.8336 | 30.6115 | 30.3952 | 30.157 | 23.7338 | 19.3492 | 14.9647 | 11.5066 | 8.3819 | 8.133 | 7.8808 | 7.6724 | 7.4279 | 7.6349 | 7.3557 | 2.5151
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | System Transformation | Headroom (MW) | N/A | 36.8155 | 36.6305 | 36.1597 | 35.7747 | 35.3407 | 34.9186 | 34.265 | 33.5441 | 32.78 | 32.0298 | 21.2156 | 20.4976 | 19.856 | 19.2678 | 18.7255 | 18.1334 | 14.1101 | 8.926 | 1.957
Chesterfield 132kV | Chesterfield 33 | Chesterfield 33 | Bulk Supply Point | 33 | 53.2252 | -1.387 | WPD Best View | Headroom (MW) | Thermal | 36.7495 | 36.3851 | 35.7095 | 35.0358 | 34.3101 | 33.3224 | 31.9256 | 29.5028 | 27.0698 | 24.5802 | 12.4503 | 10.4629 | 8.9352 | 7.4913 | 3.2949 | 1.7115 | -11.5455 | -25.7024 | -39.428
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Consumer Transformation | Headroom (MW) | Thermal | 3.9774 | 3.9795 | 3.9274 | 3.8818 | 3.8274 | 3.782 | 3.6831 | 3.5818 | 3.4796 | 3.367 | 3.2314 | 3.1137 | 2.9767 | 2.8551 | 1.8202 | 1.6953 | 1.0306 | -0.59301 | -2.1963
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Leading the Way | Headroom (MW) | Thermal | 3.9835 | 4.0162 | 3.9761 | 3.9559 | 3.9155 | 3.93 | 3.8911 | 3.8408 | 3.775 | 3.7125 | 3.6392 | 3.5753 | 3.5253 | 3.4759 | 3.4479 | 3.4155 | 2.187 | 0.52898 | -0.85438
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | Steady Progression | Headroom (MW) | N/A | 3.9823 | 3.9921 | 3.9626 | 3.9468 | 3.9349 | 3.947 | 3.9337 | 3.9191 | 3.9004 | 3.8866 | 3.86 | 3.841 | 3.8336 | 3.8145 | 3.8055 | 3.7875 | 3.7692 | 3.7745 | 3.5988
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | System Transformation | Headroom (MW) | N/A | 3.9814 | 3.9992 | 3.9566 | 3.9346 | 3.9026 | 3.9156 | 3.8719 | 3.8223 | 3.776 | 3.7263 | 3.6707 | 3.6159 | 3.5768 | 3.5317 | 3.4938 | 3.4461 | 3.3038 | 3.1177 | 2.8568
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | 53.1739 | -1.4055 | WPD Best View | Headroom (MW) | Thermal | 3.9774 | 3.9795 | 3.9274 | 3.8818 | 3.8274 | 3.782 | 3.6831 | 3.5818 | 3.4796 | 3.367 | 3.2314 | 3.1137 | 2.9767 | 2.8551 | 1.8202 | 1.6953 | 1.0306 | -0.59301 | -2.1963
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Consumer Transformation | Headroom (MW) | Thermal | 7.8784 | 7.7936 | 7.6531 | 7.5185 | 7.3577 | 7.1421 | 6.8609 | 6.5594 | 6.2564 | 5.9457 | 5.6004 | 5.271 | 4.9479 | 4.6642 | 4.3991 | 4.095 | 1.6484 | -2.6297 | -2.6269
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Leading the Way | Headroom (MW) | Thermal | 7.9136 | 7.8703 | 7.7867 | 7.706 | 7.6017 | 7.495 | 7.349 | 7.156 | 6.9827 | 6.7842 | 6.6046 | 6.4488 | 6.3438 | 6.2703 | 6.2313 | 4.4477 | 1.2226 | 0.676 | -4.7266
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | Steady Progression | Headroom (MW) | Thermal | 7.8834 | 7.8294 | 7.7464 | 2.566 | 2.5234 | 2.4732 | 2.4417 | 0.32953 | 0.2799 | 0.2296 | -0.93123 | -1.9896 | -2.0393 | -2.0905 | -2.1268 | -2.1756 | -2.1577 | -2.1611 | -2.6372
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | System Transformation | Headroom (MW) | N/A | 7.8877 | 7.8387 | 7.7423 | 7.6587 | 7.5708 | 7.4766 | 7.3607 | 7.2138 | 7.0658 | 6.9094 | 6.7636 | 6.6325 | 6.4962 | 6.3829 | 6.2921 | 6.186 | 5.8707 | 2.832 | 3.7786
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | 53.2354 | -1.3255 | WPD Best View | Headroom (MW) | Thermal | 7.8784 | 7.7936 | 7.6531 | 7.5185 | 7.3577 | 7.1421 | 6.8609 | 6.5594 | 6.2564 | 5.9457 | 5.6004 | 5.271 | 4.9479 | 4.6642 | 4.3991 | 4.095 | 1.6484 | -2.6297 | -2.6269
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Consumer Transformation | Headroom (MW) | Thermal | 3.4171 | 3.4033 | 3.2936 | 3.1757 | 3.0495 | 2.8808 | 2.6492 | 2.4155 | 2.178 | 1.9254 | 1.6496 | 1.3983 | 1.1345 | 0.88754 | 0.65172 | 0.3964 | -3.239 | -4.7275 | -7.4033
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Leading the Way | Headroom (MW) | Thermal | 3.4341 | 3.4774 | 3.4133 | 3.3465 | 3.2721 | 3.1938 | 3.0937 | 2.99 | 2.8683 | 2.7541 | 2.6371 | 2.5252 | 2.4395 | 2.3529 | 0.59593 | 0.50706 | -2.6585 | -5.7047 | -7.8384
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | Steady Progression | Headroom (MW) | N/A | 3.4411 | 3.4394 | 3.3709 | 3.3196 | 3.2777 | 3.2337 | 3.1878 | 3.1437 | 3.093 | 3.0355 | 2.9695 | 2.9155 | 2.8612 | 2.8166 | 2.7755 | 2.7246 | 2.6031 | 2.5129 | 0.88091
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | System Transformation | Headroom (MW) | Thermal | 3.4312 | 3.4447 | 3.3742 | 3.3048 | 3.2226 | 3.1405 | 3.0216 | 2.9057 | 2.771 | 2.6391 | 2.5016 | 2.3785 | 2.2641 | 2.1478 | 2.0494 | 1.9416 | 0.25445 | -0.22272 | -2.0621
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | 53.1635 | -1.3944 | WPD Best View | Headroom (MW) | Thermal | 3.4171 | 3.4033 | 3.2936 | 3.1757 | 3.0495 | 2.8808 | 2.6492 | 2.4155 | 2.178 | 1.9254 | 1.6496 | 1.3983 | 1.1345 | 0.88754 | 0.65172 | 0.3964 | -3.239 | -4.7275 | -7.4033
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Consumer Transformation | Headroom (MW) | Thermal | 10.5486 | 10.3766 | 10.0989 | 9.8645 | 9.6325 | 9.2871 | 8.782 | 8.2972 | 7.8184 | 7.322 | 6.7723 | 6.2516 | 5.7334 | 5.2133 | 2.8051 | 2.191 | -1.8833 | -6.9464 | -13.3732
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Leading the Way | Headroom (MW) | Thermal | 10.5825 | 10.4856 | 10.2981 | 10.2004 | 10.0963 | 9.9901 | 9.8057 | 9.6126 | 9.4001 | 5.8516 | 5.6585 | 5.487 | 5.3915 | 5.2138 | 3.2612 | 1.2659 | -3.4262 | -7.8008 | -15.3498
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | Steady Progression | Headroom (MW) | N/A | 10.5747 | 10.4887 | 10.3155 | 10.2274 | 10.1622 | 10.0901 | 9.9966 | 9.8962 | 9.785 | 9.6775 | 9.5462 | 9.4376 | 9.3493 | 9.2565 | 9.165 | 9.0757 | 9.3771 | 9.1676 | 7.1209
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | System Transformation | Headroom (MW) | N/A | 10.5712 | 10.4658 | 10.2615 | 10.1435 | 10.0002 | 9.8483 | 9.6049 | 9.3279 | 9.0442 | 8.778 | 8.4728 | 8.1977 | 7.9623 | 7.7436 | 7.5099 | 7.2703 | 5.6685 | 4.7141 | 0.98186
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | 53.1998 | -1.3839 | WPD Best View | Headroom (MW) | Thermal | 10.5486 | 10.3766 | 10.0989 | 9.8645 | 9.6325 | 9.2871 | 8.782 | 8.2972 | 7.8184 | 7.322 | 6.7723 | 6.2516 | 5.7334 | 5.2133 | 2.8051 | 2.191 | -1.8833 | -6.9464 | -13.3732
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Consumer Transformation | Headroom (MW) | Thermal | 10.2174 | 10.1225 | 10.0285 | 9.8895 | 9.7401 | 9.5312 | 9.256 | 8.9858 | 8.7075 | 8.4245 | 8.1259 | 7.8274 | 7.556 | 7.2989 | 7.0605 | 6.7838 | 4.3216 | 2.4948 | -0.59581
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Leading the Way | Headroom (MW) | N/A | 10.2393 | 10.1827 | 10.1572 | 10.0737 | 9.9972 | 9.9005 | 9.7661 | 9.6408 | 9.494 | 9.3613 | 9.2375 | 9.1431 | 9.0736 | 9.0437 | 9.015 | 8.9498 | 7.0224 | 9.819 | 8.5115
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | Steady Progression | Headroom (MW) | Thermal | 10.2337 | 10.1743 | 10.1242 | 10.0626 | 10.0022 | 9.94 | 9.8859 | 5.7341 | 1.5795 | -2.5757 | -4.6491 | -6.5338 | -6.5832 | -6.6275 | -6.6579 | -6.6956 | -6.668 | -6.6494 | -7.1596
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | System Transformation | Headroom (MW) | N/A | 10.2327 | 10.1708 | 10.114 | 10.0218 | 9.9333 | 9.8262 | 9.6947 | 9.563 | 9.4117 | 9.2656 | 9.1102 | 8.9762 | 8.8599 | 8.7652 | 8.6835 | 8.5927 | 8.316 | 7.7882 | 5.7051
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | 53.2702 | -1.4424 | WPD Best View | Headroom (MW) | Thermal | 10.2166 | 10.1209 | 10.0251 | 9.884 | 9.7318 | 9.5191 | 9.2392 | 7.9377 | 6.6262 | 5.3088 | 4.4999 | 3.7316 | 3.446 | 3.1743 | 2.922 | 2.6372 | 0.2011 | -1.5026 | -4.525
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Consumer Transformation | Headroom (MW) | Thermal | -11.5593 | -11.7841 | -12.2894 | -12.7649 | -13.2779 | -13.9752 | -15.0526 | -16.0562 | -16.9592 | -17.9415 | -20.9665 | -23.0543 | -28.9403 | -30.902 | -33.6073 | -35.538 | -50.4644 | -73.1485 | -94.1913
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Leading the Way | Headroom (MW) | Thermal | -11.4473 | -11.721 | -11.9809 | -12.2207 | -12.4892 | -12.7719 | -13.4182 | -13.9196 | -14.364 | -14.7881 | -15.3654 | -15.8488 | -21.0022 | -23.5584 | -23.2967 | -28.7154 | -46.1944 | -71.7883 | -91.6487
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | Steady Progression | Headroom (MW) | Thermal | -11.516 | -11.6687 | -12.0041 | -18.3429 | -18.5192 | -18.6693 | -18.8866 | -21.1545 | -22.3059 | -23.5427 | -24.9659 | -26.2266 | -26.4209 | -26.5854 | -26.7267 | -26.8868 | -26.5987 | -30.4149 | -33.9337
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | System Transformation | Headroom (MW) | Thermal | -11.5045 | -11.6516 | -11.9908 | -12.2546 | -12.5638 | -12.8708 | -13.4088 | -13.9044 | -14.347 | -14.8405 | -15.3983 | -15.8813 | -16.3365 | -16.6937 | -17.0303 | -17.3861 | -25.9324 | -36.6815 | -46.3882
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | 53.1658 | -1.1033 | WPD Best View | Headroom (MW) | Thermal | -5.6683 | -5.912 | -6.4547 | -6.9706 | -7.5156 | -8.2834 | -9.4275 | -10.5135 | -11.486 | -12.5563 | -15.6823 | -17.8226 | -23.7672 | -25.7791 | -28.5932 | -30.6079 | -47.3349 | -71.7643 | -94.1913
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Consumer Transformation | Headroom (MW) | Thermal | -1.3736 | -1.3992 | -1.4655 | -1.508 | -1.5633 | -1.6321 | -1.7235 | -1.8164 | -1.9174 | -2.0005 | -2.1062 | -3.1516 | -3.247 | -3.3452 | -3.4224 | -3.5019 | -6.0259 | -8.5606 | -11.4474
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Leading the Way | Headroom (MW) | Thermal | -1.3591 | -1.3848 | -1.4322 | -1.4632 | -1.489 | -1.5334 | -1.596 | -1.6585 | -1.7326 | -1.7783 | -1.8455 | -1.8923 | -1.9227 | -1.961 | 0.1517 | 0.11991 | -1.1993 | -5.1517 | -5.8311
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | Steady Progression | Headroom (MW) | Thermal | -1.3648 | -1.3885 | -1.4507 | -1.4779 | -1.5027 | -1.5275 | -1.5614 | -1.5882 | -1.6152 | -1.6503 | -1.9115 | -2.1557 | -2.1863 | -2.2171 | -2.2438 | -2.2647 | -2.1823 | -2.2579 | -2.4803
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | System Transformation | Headroom (MW) | Thermal | -1.3634 | -1.3941 | -1.4486 | -1.4866 | -1.5163 | -1.5559 | -1.6118 | -1.6598 | -1.7279 | -1.7758 | -1.8328 | -1.8827 | -1.9233 | -1.9668 | -2.0041 | -2.0362 | -3.2152 | -4.3696 | -5.9599
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | 53.1515 | -1.0128 | WPD Best View | Headroom (MW) | Thermal | -1.3736 | -1.3992 | -1.4655 | -1.508 | -1.5633 | -1.6321 | -1.7235 | -1.8164 | -1.9174 | -2.0005 | -2.1062 | -3.1516 | -3.247 | -3.3452 | -3.4224 | -3.5019 | -6.0259 | -8.5606 | -11.4474
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Consumer Transformation | Headroom (MW) | Thermal | 2.9291 | 2.9182 | 2.9041 | 2.8867 | 2.8737 | 2.862 | 2.8252 | 2.8045 | 2.7709 | 2.7629 | 2.7404 | 2.7389 | 2.7285 | 2.7291 | 2.7276 | 2.7013 | 1.446 | -1.7132 | -2.4382
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Leading the Way | Headroom (MW) | Thermal | 2.9295 | 2.9202 | 2.9158 | 2.9111 | 2.909 | 2.9195 | 2.9081 | 2.9209 | 2.9257 | 2.9463 | 2.9586 | 2.9905 | 2.9999 | 3.0188 | 3.0241 | -0.38494 | -0.62631 | -5.9636 | -9.2091
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | Steady Progression | Headroom (MW) | N/A | 2.9366 | 2.9246 | 2.9077 | 2.9042 | 2.9029 | 2.8936 | 2.8947 | 2.8968 | 2.8923 | 2.8983 | 2.8958 | 2.9072 | 2.9074 | 2.9255 | 2.9439 | 2.9625 | 3.0642 | 3.1349 | 2.9301
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | System Transformation | Headroom (MW) | Thermal | 2.9285 | 2.9158 | 2.9072 | 2.8951 | 2.8848 | 2.8838 | 2.8579 | 2.8516 | 2.8303 | 2.8217 | 2.8068 | 2.8218 | 2.8236 | 2.8403 | 2.8543 | 2.8751 | 2.9844 | 0.29039 | -0.08031
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | 53.2256 | -1.0971 | WPD Best View | Headroom (MW) | Thermal | 2.9291 | 2.9182 | 2.9041 | 2.8867 | 2.8737 | 2.862 | 2.8252 | 2.8045 | 2.7709 | 2.7629 | 2.7404 | 2.7389 | 2.7285 | 2.7291 | 2.7276 | 2.7013 | 1.446 | -1.7132 | -2.4382
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Consumer Transformation | Headroom (MW) | N/A | 11.3309 | 11.3138 | 11.2669 | 11.2157 | 11.1745 | 11.1331 | 11.0566 | 10.9832 | 10.9147 | 10.8483 | 10.7588 | 10.6783 | 10.5837 | 10.515 | 10.4495 | 9.4531 | 9.0744 | 6.1315 | 5.3178
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Leading the Way | Headroom (MW) | N/A | 11.3393 | 11.3324 | 11.3115 | 11.2866 | 11.2728 | 11.2629 | 11.2695 | 11.264 | 11.243 | 11.2608 | 11.227 | 11.2021 | 11.1763 | 11.1744 | 11.181 | 11.1761 | 8.9165 | 8.3558 | 6.4175
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | Steady Progression | Headroom (MW) | N/A | 11.3334 | 11.3246 | 11.3029 | 11.293 | 11.2796 | 11.284 | 11.2712 | 11.2668 | 11.2642 | 11.2542 | 11.2361 | 11.2444 | 11.2505 | 11.2525 | 11.2661 | 11.2758 | 11.4804 | 11.5702 | 11.381
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | System Transformation | Headroom (MW) | N/A | 11.3347 | 11.3245 | 11.299 | 11.2795 | 11.2566 | 11.2294 | 11.2052 | 11.176 | 11.1379 | 11.1157 | 11.083 | 11.058 | 11.0351 | 11.0334 | 11.0298 | 11.0246 | 11.2108 | 9.7676 | 9.3914
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | 53.1655 | -1.1036 | WPD Best View | Headroom (MW) | N/A | 11.3309 | 11.3138 | 11.2669 | 11.2157 | 11.1745 | 11.1331 | 11.0566 | 10.9832 | 10.9147 | 10.8483 | 10.7588 | 10.6783 | 10.5837 | 10.515 | 10.4495 | 9.4531 | 9.0744 | 6.1315 | 5.3178
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Consumer Transformation | Headroom (MW) | N/A | 11.5945 | 11.498 | 11.327 | 11.1841 | 11.03 | 10.8149 | 10.5113 | 10.2093 | 9.9135 | 9.5997 | 9.2462 | 8.8879 | 8.5492 | 8.2458 | 7.9494 | 7.6189 | 6.018 | 4.389 | 2.8353
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Leading the Way | Headroom (MW) | N/A | 11.6193 | 11.5507 | 11.4307 | 11.3625 | 11.2723 | 11.1801 | 11.0232 | 10.8615 | 10.6837 | 10.5133 | 10.3256 | 10.1518 | 10.0077 | 9.8947 | 9.802 | 9.6979 | 9.1028 | 6.9044 | 9.7461
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | Steady Progression | Headroom (MW) | N/A | 11.6195 | 11.5511 | 11.4404 | 11.378 | 11.3184 | 11.2757 | 11.2059 | 11.1372 | 11.0772 | 11.0031 | 10.905 | 10.8339 | 10.7631 | 10.6989 | 10.6394 | 10.5697 | 10.441 | 10.3286 | 9.8591
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | System Transformation | Headroom (MW) | N/A | 11.6149 | 11.5405 | 11.4071 | 11.3263 | 11.234 | 11.1374 | 10.9752 | 10.8195 | 10.645 | 10.4782 | 10.298 | 10.134 | 9.9818 | 9.842 | 9.7054 | 9.566 | 9.076 | 8.553 | 7.8816
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | 53.1475 | -1.1571 | WPD Best View | Headroom (MW) | N/A | 11.5945 | 11.498 | 11.327 | 11.1841 | 11.03 | 10.8149 | 10.5113 | 10.2093 | 9.9135 | 9.5997 | 9.2462 | 8.8879 | 8.5492 | 8.2458 | 7.9494 | 7.6189 | 6.018 | 4.389 | 2.8353
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Consumer Transformation | Headroom (MW) | Thermal | 13.5143 | 13.4424 | 13.3 | 13.1776 | 13.032 | 12.8278 | 12.5234 | 12.2437 | 11.9528 | 11.6581 | 10.3881 | 10.0577 | 9.7224 | 8.4758 | 8.1931 | 7.8872 | 2.9973 | -4.1673 | -10.3497
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Leading the Way | Headroom (MW) | Thermal | 13.558 | 13.3517 | 13.2672 | 13.2051 | 13.1254 | 13.0242 | 12.8552 | 12.7007 | 12.5202 | 12.3627 | 12.1784 | 12.0569 | 11.0073 | 9.6054 | 9.5244 | 7.7005 | 1.2027 | -5.8653 | -12.6247
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | Steady Progression | Headroom (MW) | Thermal | 13.5113 | 13.4706 | 13.3803 | 7.1849 | 7.1341 | 7.0822 | 7.0339 | 4.917 | 3.8268 | 2.7317 | 1.727 | 0.81598 | 0.74996 | 0.68231 | 0.61627 | 0.55154 | 0.33718 | -1.1264 | -1.5856
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | System Transformation | Headroom (MW) | N/A | 13.5289 | 13.4894 | 13.3908 | 13.3209 | 13.2345 | 13.1371 | 12.9879 | 12.8467 | 12.6849 | 12.5173 | 12.3442 | 12.199 | 12.0494 | 11.9038 | 11.7773 | 11.6326 | 8.8646 | 5.7253 | 2.4934
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | 53.1949 | -1.0232 | WPD Best View | Headroom (MW) | Thermal | 13.5143 | 13.4424 | 13.3 | 13.1776 | 13.032 | 12.8278 | 12.5234 | 12.2437 | 11.9528 | 11.6581 | 10.3881 | 10.0577 | 9.7224 | 8.4758 | 8.1931 | 7.8872 | 2.9973 | -4.1673 | -10.3497
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Consumer Transformation | Headroom (MW) | Thermal | 6.8397 | 6.8258 | 6.7613 | 6.7267 | 6.6925 | 6.6612 | 6.5972 | 6.5667 | 6.5071 | 6.4791 | 5.5142 | 5.4391 | 5.3741 | 5.2918 | 4.385 | 4.3716 | 2.1934 | 0.62206 | -3.2332
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Leading the Way | Headroom (MW) | Thermal | 6.8418 | 6.8242 | 6.761 | 6.7124 | 6.6798 | 6.6486 | 6.5137 | 6.4832 | 6.4142 | 6.3882 | 6.3311 | 6.1984 | 6.0706 | 5.035 | 5.0186 | 5.0008 | 3.6733 | -0.52275 | -5.9182
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | Steady Progression | Headroom (MW) | N/A | 6.8381 | 6.8183 | 6.7523 | 6.715 | 6.6808 | 6.6474 | 6.6028 | 6.5697 | 6.5337 | 6.5017 | 6.4769 | 6.4376 | 6.4062 | 6.3772 | 6.3489 | 6.3221 | 6.1704 | 6.0196 | 5.7127
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | System Transformation | Headroom (MW) | N/A | 6.8396 | 6.8256 | 6.7608 | 6.726 | 6.6913 | 6.6592 | 6.6227 | 6.5904 | 6.5574 | 6.5258 | 6.5124 | 6.475 | 6.4462 | 6.4198 | 6.3966 | 6.3769 | 5.393 | 5.2555 | 5.04
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | 53.1376 | -1.1097 | WPD Best View | Headroom (MW) | Thermal | 12.7306 | 12.698 | 12.5959 | 12.521 | 12.4548 | 12.353 | 12.2223 | 12.1094 | 11.9803 | 11.8643 | 10.7984 | 10.6708 | 10.5472 | 10.4147 | 9.3991 | 9.3017 | 5.3228 | 2.0063 | -3.2332
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Consumer Transformation | Headroom (MW) | Thermal | 8.4439 | 8.4717 | 8.5119 | 8.4786 | 8.4481 | 8.3775 | 8.2558 | 8.1241 | 7.9839 | 7.8255 | 7.6676 | 7.5181 | 7.366 | 7.2319 | 6.1887 | 6.0623 | 4.1078 | 1.018 | -2.1042
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Leading the Way | Headroom (MW) | Thermal | 8.4498 | 8.5177 | 8.6177 | 8.6305 | 8.6287 | 8.6315 | 8.5568 | 8.4777 | 8.3573 | 8.2423 | 8.1628 | 8.1187 | 8.0961 | 8.0804 | 6.3895 | 6.367 | 2.5627 | 0.69717 | -3.4699
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | Steady Progression | Headroom (MW) | N/A | 8.4487 | 8.4774 | 8.527 | 8.5313 | 8.5477 | 8.5624 | 8.5605 | 8.5535 | 8.545 | 8.5322 | 8.5191 | 8.5081 | 8.4994 | 8.4923 | 8.4873 | 8.4797 | 8.5857 | 8.6659 | 7.1563
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | System Transformation | Headroom (MW) | N/A | 8.447 | 8.4913 | 8.5576 | 8.5639 | 8.5578 | 8.564 | 8.5165 | 8.469 | 8.4125 | 8.3616 | 8.3049 | 8.248 | 8.1954 | 8.1617 | 8.1313 | 8.1021 | 6.7835 | 5.2682 | 3.5961
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | 53.1984 | -1.0408 | WPD Best View | Headroom (MW) | Thermal | 8.4439 | 8.4717 | 8.5119 | 8.4786 | 8.4481 | 8.3775 | 8.2558 | 8.1241 | 7.9839 | 7.8255 | 7.6676 | 7.5181 | 7.366 | 7.2319 | 6.1887 | 6.0623 | 4.1078 | 1.018 | -2.1042
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Consumer Transformation | Headroom (MW) | N/A | 11.7425 | 11.7257 | 11.6856 | 11.6543 | 11.6152 | 11.5609 | 11.482 | 11.4094 | 11.4958 | 11.4659 | 11.4049 | 11.358 | 11.3184 | 11.2895 | 11.2575 | 11.2051 | 11.0602 | 10.4676 | 8.5639
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Leading the Way | Headroom (MW) | N/A | 11.7547 | 11.7475 | 11.728 | 11.7147 | 11.6922 | 11.6753 | 11.6319 | 11.6114 | 11.8051 | 11.8572 | 11.8771 | 11.9057 | 11.9471 | 11.9784 | 11.9966 | 11.9919 | 10.5578 | 10.1422 | 9.6252
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | Steady Progression | Headroom (MW) | N/A | 11.7417 | 11.7336 | 11.7166 | 11.7091 | 11.7004 | 11.6934 | 11.6864 | 11.6734 | 11.7505 | 11.767 | 11.7663 | 11.7626 | 11.7695 | 11.7835 | 11.7957 | 11.7971 | 12.0853 | 12.2082 | 12.0512
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | System Transformation | Headroom (MW) | N/A | 11.7456 | 11.7359 | 11.7158 | 11.7008 | 11.6741 | 11.6548 | 11.6182 | 11.5828 | 11.6934 | 11.6954 | 11.6657 | 11.646 | 11.6358 | 11.6524 | 11.6595 | 11.6535 | 11.9286 | 11.7862 | 10.2076
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | 53.2164 | -1.1404 | WPD Best View | Headroom (MW) | N/A | 11.7425 | 11.7257 | 11.6856 | 11.6543 | 11.6152 | 11.5609 | 11.482 | 11.4094 | 11.4958 | 11.4659 | 11.4049 | 11.358 | 11.3184 | 11.2895 | 11.2575 | 11.2051 | 11.0602 | 10.4676 | 8.5639
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Consumer Transformation | Headroom (MW) | Thermal | 68.917 | 68.4439 | 67.7395 | 46.5337 | 45.8259 | 44.7737 | 43.0791 | 41.4052 | 39.8177 | 38.1803 | 36.4066 | 34.8267 | 33.436 | 31.9785 | 30.5 | 28.7916 | 19.9869 | 8.6712 | -3.2707
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Leading the Way | Headroom (MW) | N/A | 69.0064 | 68.7274 | 68.3844 | 68.0419 | 67.7207 | 67.4025 | 66.4063 | 65.9179 | 65.1581 | 64.6374 | 63.8826 | 63.2716 | 62.9355 | 62.277 | 62.0271 | 61.6591 | 57.3993 | 52.2466 | 48.3629
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | Steady Progression | Headroom (MW) | N/A | 69.0273 | 68.7549 | 68.3448 | 68.0881 | 67.8351 | 67.5991 | 67.2553 | 66.9903 | 66.7098 | 66.4535 | 66.1014 | 65.7357 | 65.5594 | 65.334 | 65.1428 | 64.9163 | 64.9853 | 64.3616 | 62.1112
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | System Transformation | Headroom (MW) | N/A | 68.9836 | 68.6664 | 68.2177 | 67.7889 | 67.3262 | 66.8706 | 66.0952 | 65.3413 | 64.4538 | 63.5386 | 62.5851 | 61.7997 | 61.2234 | 60.6281 | 60.1669 | 59.6045 | 58.2948 | 55.5302 | 50.0103
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | 53.2336 | -1.4438 | WPD Best View | Headroom (MW) | N/A | 68.9163 | 68.4422 | 67.7362 | 67.0342 | 66.3236 | 65.2677 | 63.5683 | 61.8884 | 60.2931 | 58.6466 | 56.8622 | 55.2693 | 53.8644 | 52.3922 | 50.8997 | 49.1834 | 40.4047 | 29.2121 | 17.3384
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Consumer Transformation | Headroom (MW) | N/A | 9.3242 | 9.2466 | 9.1204 | 9.0119 | 8.9105 | 8.7569 | 8.5474 | 8.3535 | 8.1795 | 8.0041 | 7.8199 | 7.6598 | 7.5239 | 7.3963 | 7.2633 | 7.1117 | 6.0553 | 4.0914 | 2.5887
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Leading the Way | Headroom (MW) | N/A | 9.3253 | 9.2816 | 9.2116 | 9.1548 | 9.1141 | 9.0819 | 8.9874 | 8.9575 | 8.9053 | 8.8831 | 8.8348 | 8.7534 | 8.6729 | 8.5872 | 8.589 | 8.5905 | 8.3539 | 7.7636 | 6.6059
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | Steady Progression | Headroom (MW) | N/A | 9.3249 | 9.2884 | 9.2025 | 9.1651 | 9.119 | 9.0762 | 9.0376 | 8.9936 | 8.9577 | 8.9214 | 8.8748 | 8.8359 | 8.817 | 8.8056 | 8.8067 | 8.7818 | 8.6693 | 8.5513 | 8.2589
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | System Transformation | Headroom (MW) | N/A | 9.3251 | 9.2779 | 9.1845 | 9.1064 | 9.0342 | 8.9619 | 8.8366 | 8.725 | 8.5969 | 8.4762 | 8.3691 | 8.2787 | 8.2079 | 8.1625 | 8.1283 | 8.0997 | 8.1027 | 7.7506 | 7.0674
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | 53.2801 | -1.6731 | WPD Best View | Headroom (MW) | N/A | 9.3234 | 9.245 | 9.117 | 9.0064 | 8.9023 | 8.7449 | 8.5306 | 8.3307 | 8.1489 | 7.9644 | 7.7695 | 7.5963 | 7.4463 | 7.304 | 7.1571 | 6.9974 | 5.9671 | 4.1264 | 2.6918
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Consumer Transformation | Headroom (MW) | N/A | 13.7861 | 13.6521 | 13.4258 | 13.2216 | 13.0017 | 12.6673 | 12.183 | 11.7166 | 11.2516 | 10.7715 | 10.2356 | 9.7605 | 9.3605 | 8.9296 | 8.5033 | 8.0019 | 5.481 | 2.9217 | 0.51785
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Leading the Way | Headroom (MW) | N/A | 13.8156 | 13.742 | 13.6279 | 13.543 | 13.4588 | 13.3665 | 13.1785 | 13.0094 | 12.8233 | 12.6449 | 12.4582 | 12.3748 | 12.4242 | 12.3592 | 12.3336 | 12.255 | 11.6672 | 10.4713 | 9.007
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | Steady Progression | Headroom (MW) | N/A | 13.8296 | 13.7546 | 13.6379 | 13.575 | 13.5099 | 13.4463 | 13.3783 | 13.3083 | 13.226 | 13.1477 | 13.0353 | 12.9516 | 12.9051 | 12.8554 | 12.8013 | 12.7391 | 12.788 | 12.8111 | 12.3074
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | System Transformation | Headroom (MW) | N/A | 13.8103 | 13.7204 | 13.5767 | 13.4613 | 13.328 | 13.1889 | 12.9498 | 12.7094 | 12.442 | 12.1849 | 11.8937 | 11.6722 | 11.5041 | 11.3126 | 11.1439 | 10.9649 | 10.373 | 9.7565 | 8.8856
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | 53.2334 | -1.4448 | WPD Best View | Headroom (MW) | N/A | 13.7861 | 13.6521 | 13.4258 | 13.2216 | 13.0017 | 12.6673 | 12.183 | 11.7166 | 11.2516 | 10.7715 | 10.2356 | 9.7605 | 9.3605 | 8.9296 | 8.5033 | 8.0019 | 5.481 | 2.9217 | 0.51785
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Consumer Transformation | Headroom (MW) | N/A | 23.6439 | 23.5821 | 23.4595 | 23.3915 | 23.3246 | 23.2596 | 22.9698 | 22.6443 | 22.3353 | 22.0223 | 21.6896 | 21.3761 | 21.0839 | 20.7862 | 20.4864 | 20.1624 | 18.415 | 16.5119 | 14.6585
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Leading the Way | Headroom (MW) | N/A | 23.6439 | 23.5764 | 23.4543 | 23.3782 | 23.3115 | 23.2474 | 22.8816 | 22.8222 | 22.6193 | 22.5629 | 22.3459 | 22.2318 | 22.1327 | 22.0105 | 21.9713 | 21.9322 | 21.5244 | 20.4011 | 19.2323
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | Steady Progression | Headroom (MW) | N/A | 22.8617 | 22.8509 | 22.8405 | 22.8249 | 22.8153 | 22.7987 | 22.7797 | 22.7589 | 22.7306 | 22.6957 | 22.6625 | 22.6257 | 22.5891 | 22.5523 | 22.5066 | 22.4519 | 22.1852 | 21.9198 | 21.5448
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | System Transformation | Headroom (MW) | N/A | 23.6439 | 23.582 | 23.4593 | 23.3912 | 23.3238 | 23.2583 | 23.1923 | 23.1298 | 23.0195 | 22.8323 | 22.6368 | 22.4673 | 22.3121 | 22.1543 | 22.0199 | 21.8757 | 21.2923 | 20.5794 | 19.739
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | 53.2334 | -1.4312 | WPD Best View | Headroom (MW) | N/A | 23.6439 | 23.5821 | 23.4595 | 23.3915 | 23.3246 | 23.2596 | 22.9698 | 22.6443 | 22.3353 | 22.0223 | 21.6896 | 21.3761 | 21.0839 | 20.7862 | 20.4864 | 20.1624 | 18.415 | 16.5119 | 14.6585
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Consumer Transformation | Headroom (MW) | Thermal | -2.551 | -2.5669 | -2.5903 | -2.606 | -2.6234 | -2.6434 | -2.6751 | -2.7031 | -2.7067 | -2.7105 | -2.6956 | -2.6675 | -2.6205 | -2.5741 | -2.5262 | -2.4941 | -2.5858 | -3.0772 | -3.6896
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Leading the Way | Headroom (MW) | Thermal | -2.548 | -2.5505 | -2.5674 | -2.5608 | -2.5546 | -2.5439 | -2.5354 | -2.5222 | -2.5327 | -2.5306 | -2.5348 | -2.5489 | -2.561 | -2.5752 | -2.5522 | -2.5305 | -2.577 | -2.7189 | -0.49441
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | Steady Progression | Headroom (MW) | Thermal | -2.55 | -2.5579 | -2.5743 | -2.5889 | -2.5924 | -2.5936 | -2.5928 | -2.594 | -2.5855 | -2.5704 | -2.5661 | -2.5432 | -2.5453 | -2.5506 | -2.5547 | -2.5575 | -2.55 | -2.5434 | -2.6433
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | System Transformation | Headroom (MW) | Thermal | -2.5506 | -2.5602 | -2.587 | -2.5963 | -2.6127 | -2.623 | -2.6493 | -2.662 | -2.6761 | -2.6785 | -2.6834 | -2.6798 | -2.6412 | -2.599 | -2.5299 | -2.5218 | -2.4596 | -2.4552 | -2.526
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | 53.2436 | -1.5801 | WPD Best View | Headroom (MW) | Thermal | -2.551 | -2.5669 | -2.5903 | -2.606 | -2.6234 | -2.6434 | -2.6751 | -2.7031 | -2.7067 | -2.7105 | -2.6956 | -2.6675 | -2.6205 | -2.5741 | -2.5262 | -2.4941 | -2.5858 | -3.0772 | -3.6896
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Consumer Transformation | Headroom (MW) | Fault level | -24.7732 | -24.8658 | -25.0035 | -25.1415 | -25.2999 | -25.5402 | -25.8879 | -26.2467 | -26.605 | -27.0039 | -27.4328 | -27.871 | -28.3243 | -28.7751 | -29.2298 | -29.6888 | -31.8063 | -33.6349 | -35.2572
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Leading the Way | Headroom (MW) | Fault level | -24.5935 | -24.649 | -24.7364 | -24.8056 | -24.887 | -24.979 | -25.152 | -25.325 | -25.5227 | -25.7318 | -25.9596 | -26.1837 | -26.407 | -26.6585 | -26.894 | -27.0992 | -27.9345 | -28.6661 | -29.3297
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | Steady Progression | Headroom (MW) | Fault level | -20.4629 | -20.4904 | -20.5143 | -20.532 | -20.5555 | -20.5739 | -20.6028 | -20.6401 | -20.6807 | -20.7254 | -20.7861 | -20.8429 | -20.9009 | -20.9608 | -21.0233 | -21.0853 | -21.353 | -21.5959 | -21.873
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | System Transformation | Headroom (MW) | Fault level | -23.8993 | -23.9416 | -24.0024 | -24.0645 | -24.1387 | -24.2197 | -24.3709 | -24.5229 | -24.6984 | -24.8811 | -25.0772 | -25.2604 | -25.4542 | -25.6511 | -25.8438 | -26.0492 | -26.919 | -27.5298 | -28.0138
Chesterfield 132kV | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | 11 | 53.248 | -1.4256 | WPD Best View | Headroom (MW) | Fault level | -23.5493 | -23.6374 | -23.7683 | -23.8994 | -24.05 | -24.2785 | -24.609 | -24.95 | -25.2907 | -25.6699 | -26.0775 | -26.4942 | -26.925 | -27.3535 | -27.7858 | -28.2221 | -30.235 | -31.9732 | -33.5154
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Consumer Transformation | Headroom (MW) | N/A | 7.6282 | 7.5867 | 7.5314 | 7.4794 | 7.4456 | 7.3844 | 7.2854 | 7.2187 | 7.151 | 7.1091 | 7.0513 | 7.0329 | 7.0241 | 7.0259 | 7.0176 | 6.9835 | 6.5753 | 5.6893 | 4.7041
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Leading the Way | Headroom (MW) | N/A | 7.636 | 7.6173 | 7.5812 | 7.5596 | 7.5432 | 7.5279 | 7.4128 | 7.401 | 7.361 | 7.3572 | 7.3207 | 7.2427 | 7.1634 | 7.0755 | 7.0968 | 7.117 | 6.9132 | 6.6133 | 6.2342
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | Steady Progression | Headroom (MW) | N/A | 7.6433 | 7.6109 | 7.5673 | 7.5454 | 7.5261 | 7.502 | 7.4909 | 7.4767 | 7.464 | 7.4578 | 7.4392 | 7.4338 | 7.4187 | 7.4067 | 7.3961 | 7.3872 | 7.3508 | 7.2938 | 7.0469
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | System Transformation | Headroom (MW) | N/A | 7.6323 | 7.6053 | 7.5551 | 7.5157 | 7.4832 | 7.4566 | 7.3971 | 7.3474 | 7.2888 | 7.2539 | 7.2143 | 7.1972 | 7.1926 | 7.2119 | 7.2597 | 7.2999 | 7.4875 | 7.4418 | 6.9321
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | 53.2165 | -1.4661 | WPD Best View | Headroom (MW) | N/A | 7.6282 | 7.5867 | 7.5314 | 7.4794 | 7.4456 | 7.3844 | 7.2854 | 7.2187 | 7.151 | 7.1091 | 7.0513 | 7.0329 | 7.0241 | 7.0259 | 7.0176 | 6.9835 | 6.5753 | 5.6893 | 4.7041
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Consumer Transformation | Headroom (MW) | Thermal | 5.8242 | 5.7762 | 5.7054 | 5.6207 | 5.5406 | 5.4023 | 5.2105 | 5.0152 | 4.8364 | 4.6465 | 4.4275 | 4.2444 | 4.0579 | 3.8634 | 3.6627 | 3.4029 | 2.6743 | 1.3159 | -1.268
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Leading the Way | Headroom (MW) | N/A | 5.8469 | 5.8119 | 5.8101 | 5.7773 | 5.7535 | 5.7275 | 5.6663 | 5.6013 | 5.5343 | 5.4807 | 5.4291 | 5.3821 | 5.3765 | 5.2989 | 5.2566 | 5.1324 | 3.2195 | 2.3901 | 1.4545
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | Steady Progression | Headroom (MW) | N/A | 5.8425 | 5.8238 | 5.7907 | 5.7795 | 5.7759 | 5.7715 | 5.7531 | 5.738 | 5.7006 | 5.6749 | 5.643 | 5.6129 | 5.6086 | 5.5867 | 5.5813 | 5.5677 | 6.1538 | 6.0442 | 5.7195
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | System Transformation | Headroom (MW) | N/A | 5.8409 | 5.8016 | 5.7838 | 5.7516 | 5.7137 | 5.6734 | 5.5927 | 5.4946 | 5.392 | 5.2877 | 5.1926 | 5.0997 | 5.0317 | 4.9606 | 4.8975 | 4.8343 | 5.1853 | 4.8015 | 2.954
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | 53.2071 | -1.4198 | WPD Best View | Headroom (MW) | Thermal | 5.8242 | 5.7762 | 5.7054 | 5.6207 | 5.5406 | 5.4023 | 5.2105 | 5.0152 | 4.8364 | 4.6465 | 4.4275 | 4.2444 | 4.0579 | 3.8634 | 3.6627 | 3.4029 | 2.6743 | 1.3159 | -1.268
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Consumer Transformation | Headroom (MW) | Thermal | 26.5488 | 26.1466 | 21.2046 | 20.4683 | 19.5369 | 18.1137 | 15.9156 | 13.6862 | 11.4165 | 9.0615 | 2.2063 | -0.23383 | -2.6278 | -5.7759 | -7.9461 | -27.2896 | -42.0871 | -59.1503 | -72.8411
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Leading the Way | Headroom (MW) | Thermal | 26.6317 | 26.3281 | 21.5594 | 21.0113 | 20.605 | 20.0798 | 18.5558 | 17.7287 | 16.5226 | 15.4433 | 10.6993 | 12.2884 | 11.2218 | -6.8033 | 2.8616 | 3.4538 | -3.8014 | 9.5226 | -5.5476
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | Steady Progression | Headroom (MW) | Thermal | 26.6067 | 22.2003 | 17.4583 | 16.9969 | 12.52 | 12.0961 | 4.4422 | -6.2294 | -15.9159 | -24.5848 | -31.6452 | -38.1432 | -42.7515 | -47.313 | -49.7991 | -50.2191 | -61.8982 | -73.0497 | -78.1281
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | System Transformation | Headroom (MW) | Thermal | 26.5992 | 26.2919 | 21.4863 | 20.9432 | 20.4559 | 19.8718 | 18.9189 | 17.9281 | 16.6688 | 15.4247 | 14.1417 | 12.9602 | 11.8411 | 10.8112 | 9.868 | -9.9291 | -13.6555 | -20.1037 | -23.6589
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | 53.1558 | -1.1995 | WPD Best View | Headroom (MW) | Thermal | 26.5488 | 26.1466 | 21.2046 | 20.4683 | 19.5369 | 18.1137 | 15.9277 | 13.6862 | 11.4165 | 9.0615 | 2.2063 | -0.23383 | -2.6278 | -5.7759 | -7.9461 | -27.2896 | -42.0871 | -59.1503 | -72.8411
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Consumer Transformation | Headroom (MW) | Fault level | -41.1934 | -41.2442 | -47.1109 | -47.2167 | -47.3297 | -47.5101 | -47.7675 | -48.0184 | -48.2905 | -48.5734 | -48.8898 | -49.2301 | -49.5579 | -49.8643 | -50.1805 | -50.5257 | -53.3028 | -56.149 | -58.7755
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Leading the Way | Headroom (MW) | Fault level | -40.9021 | -40.9303 | -46.7151 | -46.7638 | -46.8186 | -46.8899 | -47.0082 | -47.133 | -47.2713 | -47.4207 | -47.5892 | -43.8886 | -44.0484 | -44.2371 | -30.0072 | -31.6144 | -33.3888 | -36.4661 | -38.4666
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | Steady Progression | Headroom (MW) | Fault level | -34.0467 | -34.0598 | -38.8618 | -38.8756 | -38.8895 | -38.903 | -43.7144 | -48.5275 | -53.3375 | -58.1618 | -62.3969 | -66.255 | -71.0834 | -75.9113 | -78.3528 | -78.3991 | -88.247 | -100.5181 | -103.2717
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | System Transformation | Headroom (MW) | Fault level | -39.748 | -39.7753 | -45.3971 | -45.4414 | -45.4906 | -45.5574 | -45.6641 | -45.7826 | -45.9063 | -46.0372 | -46.1808 | -46.3172 | -46.447 | -46.5896 | -46.7264 | -46.8757 | -47.6023 | -49.2804 | -49.8776
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | 53.1954 | -1.2081 | WPD Best View | Headroom (MW) | Fault level | -39.1583 | -39.2066 | -44.7835 | -44.8841 | -44.9915 | -45.163 | -45.4076 | -45.6461 | -45.9048 | -46.1738 | -46.4745 | -46.798 | -47.1096 | -47.4009 | -47.7015 | -48.0296 | -50.6695 | -53.3751 | -55.8718
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Consumer Transformation | Headroom (MW) | Fault level | 8.8181 | 8.707 | 8.5491 | 8.3443 | 8.1123 | 7.7677 | 7.2637 | 6.7594 | 6.2406 | 5.6616 | 5.0183 | 4.3567 | 3.7108 | 3.0989 | 2.5009 | 1.869 | -1.0566 | -3.6404 | -6.9337
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Leading the Way | Headroom (MW) | N/A | 8.7906 | 8.6583 | 8.5799 | 8.4762 | 8.3524 | 8.2009 | 7.9482 | 7.6812 | 7.3517 | 6.9937 | 6.622 | 6.2411 | 5.9063 | 5.6265 | 5.3755 | 5.1245 | 4.2823 | 3.1733 | 2.1306
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | Steady Progression | Headroom (MW) | N/A | 7.3311 | 7.3014 | 7.2721 | 7.2427 | 7.212 | 7.18 | 7.1375 | 7.0894 | 7.0288 | 6.9618 | 6.8757 | 6.7879 | 6.7041 | 6.623 | 6.5405 | 6.4478 | 6.0882 | 5.727 | 5.3026
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | System Transformation | Headroom (MW) | N/A | 8.5434 | 8.4899 | 8.4204 | 8.3276 | 8.2227 | 8.0986 | 7.882 | 7.6642 | 7.4062 | 7.1385 | 6.8612 | 6.5837 | 6.31 | 6.0475 | 5.7792 | 5.4998 | 4.3067 | 3.4253 | 2.6926
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | 53.1415 | -1.1911 | WPD Best View | Headroom (MW) | Fault level | 8.3824 | 8.2769 | 8.1267 | 7.9321 | 7.7115 | 7.3839 | 6.9049 | 6.4255 | 5.9323 | 5.3819 | 4.7704 | 4.1414 | 3.5274 | 2.9458 | 2.3773 | 1.7767 | -1.0044 | -3.4606 | -6.5911
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Consumer Transformation | Headroom (MW) | Fault level | -15.5458 | -15.6653 | -15.8353 | -16.2056 | -16.6062 | -17.142 | -17.8545 | -18.5592 | -19.3068 | -20.0811 | -20.9509 | -21.7902 | -22.6245 | -23.4476 | -24.2602 | -25.1222 | -30.1522 | -33.6965 | -34.886
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Leading the Way | Headroom (MW) | Fault level | -15.4124 | -15.4632 | -15.5343 | -15.765 | -16.0348 | -16.3343 | -16.745 | -17.1595 | -17.6409 | -18.1314 | -18.6668 | -19.1686 | -19.6234 | -20.0911 | -20.503 | -20.9285 | -22.769 | -19.2122 | -22.0935
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | Steady Progression | Headroom (MW) | Fault level | -12.8164 | -12.8486 | -12.8736 | -13.0213 | -17.9539 | -18.1053 | -21.8444 | -26.7925 | -30.5556 | -34.3324 | -36.9121 | -39.2752 | -39.478 | -39.6784 | -39.8734 | -40.0722 | -40.9328 | -41.3694 | -41.8913
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | System Transformation | Headroom (MW) | Fault level | -14.9779 | -15.0298 | -15.1065 | -15.3385 | -15.5953 | -15.8771 | -16.2568 | -16.6354 | -17.0655 | -17.4987 | -17.9649 | -18.4108 | -18.8528 | -19.2954 | -19.7338 | -20.198 | -22.1635 | -23.2743 | -22.1582
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | 53.156 | -1.1994 | WPD Best View | Headroom (MW) | Fault level | -14.7778 | -14.8914 | -15.053 | -15.405 | -15.7858 | -16.2951 | -16.9724 | -17.6424 | -18.353 | -19.0891 | -19.9159 | -20.7137 | -21.5068 | -22.2893 | -23.0617 | -23.8811 | -28.6626 | -32.0318 | -33.1626
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Consumer Transformation | Headroom (MW) | Thermal | 10.6315 | 10.5892 | 10.5034 | 10.4575 | 10.4494 | 10.31 | 9.9414 | 9.577 | 9.23 | 8.8668 | 8.4724 | 8.0985 | 7.6971 | 7.34 | 6.9905 | 6.593 | 4.6009 | 1.5613 | -0.4783
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Leading the Way | Headroom (MW) | N/A | 10.6321 | 10.5734 | 10.4894 | 10.4213 | 10.4281 | 10.384 | 10.1843 | 10.1456 | 10.0556 | 10.0258 | 9.8621 | 9.7004 | 9.5235 | 9.3011 | 9.2808 | 12.2205 | 11.362 | 10.185 | 7.9626
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | Steady Progression | Headroom (MW) | Thermal | 10.631 | 6.4863 | 6.3991 | 6.349 | 6.3294 | 6.2832 | 6.2201 | 4.1272 | 2.0285 | 0.96181 | -0.043757 | -0.96003 | -1.0024 | -1.0413 | -1.0792 | -1.1157 | -1.3041 | -1.5497 | -2.0337
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | System Transformation | Headroom (MW) | N/A | 10.6314 | 10.5891 | 10.5032 | 10.4572 | 10.4487 | 10.4028 | 10.3521 | 10.2893 | 10.0754 | 9.8685 | 9.6588 | 9.463 | 9.2797 | 9.1052 | 8.9453 | 8.7769 | 8.1036 | 7.3737 | 6.5012
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | 53.1378 | -1.2176 | WPD Best View | Headroom (MW) | Thermal | 10.6315 | 10.5892 | 10.5034 | 10.4575 | 10.4494 | 10.31 | 9.9414 | 9.577 | 9.23 | 8.8668 | 8.4724 | 8.0985 | 7.6971 | 7.34 | 6.9905 | 6.593 | 4.6009 | 1.5613 | -0.4783
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Consumer Transformation | Headroom (MW) | Thermal | 9.5048 | 9.4777 | 9.4212 | 9.392 | 9.3671 | 9.3378 | 9.2002 | 8.9699 | 8.7443 | 8.5258 | 8.3524 | 8.1262 | 7.9026 | 6.7615 | 6.5689 | 6.3567 | 4.4806 | 1.0969 | -1.0487
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Leading the Way | Headroom (MW) | Thermal | 9.5055 | 9.4656 | 9.4103 | 9.364 | 9.3417 | 9.3133 | 8.9636 | 8.8523 | 8.6942 | 8.5912 | 8.432 | 8.2402 | 8.0284 | 7.7986 | 7.7111 | 7.6379 | 5.7174 | 3.955 | -0.46648
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | Steady Progression | Headroom (MW) | N/A | 9.5041 | 9.4758 | 9.4179 | 9.3851 | 9.3576 | 9.327 | 9.2823 | 9.2519 | 9.2174 | 9.1879 | 9.1544 | 9.126 | 9.0963 | 9.0695 | 9.0437 | 9.0192 | 8.895 | 8.7404 | 8.4253
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | System Transformation | Headroom (MW) | N/A | 9.5047 | 9.4775 | 9.4208 | 9.3913 | 9.366 | 9.3359 | 9.3006 | 9.2701 | 9.2386 | 9.2099 | 9.1186 | 9.0427 | 8.9731 | 8.9226 | 8.8772 | 8.829 | 8.6922 | 7.114 | 6.5663
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | 53.1485 | -1.2919 | WPD Best View | Headroom (MW) | Thermal | 9.5048 | 9.4777 | 9.4212 | 9.392 | 9.3671 | 9.3378 | 9.2123 | 8.9699 | 8.7443 | 8.5258 | 8.3524 | 8.1262 | 7.9026 | 6.7615 | 6.5689 | 6.3567 | 4.4806 | 1.0969 | -1.0487
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Consumer Transformation | Headroom (MW) | N/A | 25.8404 | 25.7122 | 25.4802 | 25.3292 | 25.1752 | 25.0013 | 24.7825 | 24.5796 | 24.3793 | 24.1959 | 24.0035 | 23.8754 | 23.7064 | 23.5457 | 23.3703 | 23.2379 | 22.1878 | 19.9682 | 17.3006
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Leading the Way | Headroom (MW) | N/A | 25.8699 | 25.7622 | 25.5682 | 25.4467 | 25.3312 | 25.2121 | 25.0839 | 24.9596 | 24.8433 | 24.7408 | 24.6476 | 24.6574 | 24.6049 | 24.525 | 24.4604 | 24.4322 | 22.5798 | 20.2198 | 18.1699
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | Steady Progression | Headroom (MW) | Thermal | 25.8284 | 25.7262 | 25.5142 | 19.2521 | 15.0431 | 14.9306 | 11.7571 | 8.562 | 5.384 | 2.2043 | -0.20027 | -2.3587 | -5.5231 | -8.6864 | -10.0838 | -10.1316 | -13.7093 | -18.0212 | -18.5867
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | System Transformation | Headroom (MW) | N/A | 25.8436 | 25.7318 | 25.5255 | 25.3961 | 25.263 | 25.1251 | 24.9731 | 24.8122 | 24.6532 | 24.4945 | 24.3571 | 24.2844 | 24.1686 | 24.0493 | 23.9543 | 23.8987 | 23.5761 | 23.0386 | 20.9522
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | 53.106 | -1.3031 | WPD Best View | Headroom (MW) | N/A | 25.8404 | 25.7122 | 25.4802 | 25.3292 | 25.1752 | 25.0013 | 24.7825 | 24.5796 | 24.3793 | 24.1959 | 24.0035 | 23.8754 | 23.7064 | 23.5457 | 23.3703 | 23.2379 | 22.1878 | 19.9682 | 17.3006
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Consumer Transformation | Headroom (MW) | Thermal | 15.4358 | 15.2736 | 8.8102 | 8.5167 | 8.2135 | 7.7702 | 7.1083 | 6.6329 | 6.0509 | 5.4619 | 4.8201 | 4.2422 | 3.7587 | 3.1928 | 2.6233 | -15.0159 | -19.5305 | -27.0309 | -32.4341
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Leading the Way | Headroom (MW) | Thermal | 15.4676 | 15.3413 | 9.0302 | 8.9289 | 8.7959 | 8.6758 | 8.3567 | 8.3688 | 8.1801 | -8.9046 | -9.0801 | -9.2946 | -9.4121 | -9.6838 | -9.7829 | -12.8744 | -16.6339 | 1.0383 | -0.39169
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | Steady Progression | Headroom (MW) | Thermal | 15.4586 | 15.3816 | 9.082 | 8.9984 | 8.9058 | 8.8087 | 6.6571 | 4.5697 | 2.4009 | 0.24925 | -1.0551 | -2.2048 | -2.2368 | -2.3022 | -2.3548 | -2.4215 | -2.3702 | -2.5009 | -3.3243
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | System Transformation | Headroom (MW) | Thermal | 15.4576 | 15.369 | 9.0087 | 8.8587 | 8.6575 | 8.4753 | 8.138 | 7.9277 | 7.5577 | 7.2412 | 6.8681 | 6.5808 | 6.401 | 6.1805 | 5.983 | -11.2198 | -11.9003 | -15.4938 | -18.5357
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | 53.2673 | -1.3861 | WPD Best View | Headroom (MW) | Thermal | 15.4354 | 15.2952 | 8.8434 | 8.5741 | 8.2882 | 7.8715 | 7.2751 | 6.8474 | 6.3119 | 5.7651 | 5.1585 | 4.6248 | 4.1801 | 3.6481 | 3.1184 | -14.4627 | -18.5449 | -25.482 | -30.4959
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Consumer Transformation | Headroom (MW) | Thermal | 9.5308 | 9.4669 | 9.3156 | 9.1897 | 9.0505 | 8.8529 | 8.5443 | 8.3722 | 8.1195 | 7.8639 | 7.5867 | 7.3437 | 7.1693 | 6.9529 | 6.7353 | 6.4537 | 4.8361 | 0.58984 | -2.7663
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Leading the Way | Headroom (MW) | Thermal | 9.5368 | 9.4872 | 9.4307 | 9.3968 | 9.3504 | 9.3095 | 9.1366 | 9.2262 | 9.1648 | 9.1546 | 9.0751 | 8.929 | 8.8423 | 8.6807 | 8.6932 | 7.4014 | 5.5599 | 1.7313 | -0.70673
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | Steady Progression | Headroom (MW) | N/A | 9.5262 | 9.4975 | 9.4384 | 9.4085 | 9.3595 | 9.3125 | 9.2632 | 9.268 | 9.2159 | 9.1716 | 9.1056 | 9.0735 | 9.0782 | 9.0611 | 9.0499 | 9.0374 | 9.1105 | 8.9895 | 8.5677
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | System Transformation | Headroom (MW) | N/A | 9.5307 | 9.5027 | 9.4103 | 9.3403 | 9.245 | 9.1633 | 9.0045 | 8.9387 | 8.7681 | 8.6306 | 8.4649 | 8.3465 | 8.2921 | 8.2141 | 8.152 | 8.0728 | 7.8928 | 6.0788 | 3.9095
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | 53.3032 | -1.3663 | WPD Best View | Headroom (MW) | Thermal | 9.5305 | 9.4884 | 9.3488 | 9.2471 | 9.1251 | 8.9541 | 8.711 | 8.5867 | 8.3806 | 8.1671 | 7.925 | 7.7263 | 7.5906 | 7.4082 | 7.2305 | 7.0069 | 5.8217 | 2.1388 | -0.82819
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Consumer Transformation | Headroom (MW) | Fault level | -9.6002 | -9.6625 | -9.7523 | -9.8832 | -10.018 | -10.2278 | -10.5361 | -10.8269 | -11.1322 | -11.4503 | -11.8061 | -12.1555 | -12.5241 | -12.9084 | -13.2979 | -13.7084 | -16.6395 | -19.4169 | -20.4474
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Leading the Way | Headroom (MW) | Fault level | -9.5147 | -9.5619 | -9.6021 | -9.6507 | -9.7228 | -9.7939 | -9.9253 | -10.0413 | -10.1848 | -10.3193 | -10.4679 | -10.6049 | -10.7713 | -10.9769 | -11.1761 | -12.7964 | -14.5817 | -5.7264 | -3.4393
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | Steady Progression | Headroom (MW) | Fault level | -7.9165 | -7.9278 | -7.9452 | -7.964 | -7.9769 | -7.9956 | -10.4121 | -12.8321 | -15.2626 | -17.6912 | -19.0954 | -20.3706 | -20.4168 | -20.4642 | -20.5119 | -20.5712 | -20.8041 | -21.0432 | -21.3205
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | System Transformation | Headroom (MW) | Fault level | -9.2469 | -9.2751 | -9.3185 | -9.3656 | -9.4351 | -9.505 | -9.6385 | -9.7691 | -9.9274 | -10.0786 | -10.2567 | -10.4147 | -10.5786 | -10.7467 | -10.9179 | -11.1079 | -11.9135 | -13.4932 | -13.5094
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | 53.2671 | -1.3851 | WPD Best View | Headroom (MW) | Fault level | -9.1259 | -9.1851 | -9.2706 | -9.395 | -9.5231 | -9.7225 | -10.0156 | -10.292 | -10.5823 | -10.8846 | -11.2228 | -11.5549 | -11.9054 | -12.2707 | -12.641 | -13.0312 | -15.8175 | -18.4576 | -19.4373
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Consumer Transformation | Headroom (MW) | Thermal | 28.3015 | 28.1373 | 27.882 | 27.7552 | 27.594 | 26.995 | 26.1245 | 25.166 | 24.1932 | 23.1536 | 21.9945 | 20.7951 | 16.9172 | 15.7055 | 14.6092 | 13.4148 | 3.6986 | -8.6867 | -19.9484
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Leading the Way | Headroom (MW) | Thermal | 28.3905 | 28.3614 | 28.3686 | 28.5559 | 28.6984 | 28.4669 | 27.8526 | 27.3778 | 26.7859 | 26.2528 | 27.0479 | 26.315 | 25.5415 | 24.5846 | 24.0835 | 22.8186 | 13.87 | 7.9752 | -2.7711
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | Steady Progression | Headroom (MW) | N/A | 28.3369 | 28.2293 | 28.0494 | 28.0857 | 21.9691 | 21.8781 | 21.7627 | 16.5234 | 12.3116 | 12.1666 | 9.0548 | 6.2696 | 6.1772 | 6.09 | 6.053 | 5.917 | 6.2421 | 6.1847 | 4.1693
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | System Transformation | Headroom (MW) | N/A | 28.3408 | 28.2491 | 28.1008 | 28.1509 | 28.1546 | 27.9458 | 27.5647 | 27.242 | 26.7769 | 26.3046 | 25.7474 | 25.247 | 24.7943 | 24.3902 | 24.0442 | 23.7032 | 22.8778 | 17.5298 | 12.0019
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | 53.2773 | -1.2272 | WPD Best View | Headroom (MW) | Thermal | 28.2975 | 28.1287 | 27.8651 | 27.7298 | 27.5573 | 26.9428 | 26.0773 | 24.1494 | 22.2274 | 21.2896 | 19.6109 | 17.9137 | 14.1385 | 13.0188 | 12.016 | 10.9485 | 2.193 | -8.9654 | -19.2192
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Consumer Transformation | Headroom (MW) | Thermal | 3.9628 | 4.0432 | 4.0762 | 4.046 | 3.9373 | 3.817 | 3.6283 | 3.4481 | 3.2552 | 3.0562 | 2.7942 | 2.5742 | 1.4235 | 1.2163 | 1.044 | 0.84356 | -1.2509 | -4.8098 | -7.1196
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Leading the Way | Headroom (MW) | Thermal | 3.9997 | 4.1551 | 4.2759 | 4.3127 | 4.2617 | 4.2174 | 4.1474 | 4.0653 | 3.9475 | 3.8387 | 3.7168 | 3.6305 | 3.5662 | 3.5196 | 3.5124 | 3.4685 | 0.75945 | -2.3188 | -4.2937
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | Steady Progression | Headroom (MW) | N/A | 3.9645 | 4.0294 | 4.078 | 4.0968 | 4.0881 | 4.0956 | 4.0909 | 4.0883 | 4.0687 | 4.0522 | 4.0208 | 4.0095 | 3.9951 | 3.974 | 3.9698 | 3.9509 | 4.0533 | 4.185 | 3.826
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | System Transformation | Headroom (MW) | N/A | 3.9708 | 4.0752 | 4.1405 | 4.1553 | 4.1042 | 4.074 | 4.0047 | 3.9377 | 3.8451 | 3.7554 | 3.6561 | 3.573 | 3.5024 | 3.4392 | 3.3871 | 3.3271 | 3.1773 | 1.5673 | 0.06495
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | 53.2791 | -1.2405 | WPD Best View | Headroom (MW) | Thermal | 3.9628 | 4.0432 | 4.0762 | 4.046 | 3.9373 | 3.817 | 3.6283 | 3.4481 | 3.2552 | 3.0562 | 2.7942 | 2.5742 | 1.4235 | 1.2163 | 1.044 | 0.84356 | -1.2509 | -4.8098 | -7.1196
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Consumer Transformation | Headroom (MW) | Thermal | 3.9777 | 3.8975 | 3.7441 | 3.6262 | 3.5666 | 3.4272 | 3.2184 | 2.9862 | 2.7083 | 2.4467 | 2.2204 | 1.9414 | 0.74155 | 0.41928 | 0.12312 | -0.18931 | -2.2869 | -4.7105 | -4.8272
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Leading the Way | Headroom (MW) | Thermal | 3.9878 | 3.9303 | 3.8056 | 3.7334 | 3.7205 | 3.6623 | 3.4783 | 3.3617 | 3.1703 | 2.9965 | 4.2165 | 3.9851 | 3.7788 | 3.5904 | 3.4163 | 2.4344 | 2.774 | -0.44445 | -2.6297
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | Steady Progression | Headroom (MW) | N/A | 3.9824 | 3.9233 | 3.8058 | 3.7342 | 3.71 | 3.6496 | 3.5924 | 3.5599 | 3.503 | 3.4526 | 2.7005 | 2.0251 | 1.9808 | 1.9312 | 1.896 | 1.8658 | 1.8404 | 1.8055 | 1.307
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | System Transformation | Headroom (MW) | N/A | 3.9819 | 3.92 | 3.7874 | 3.7059 | 3.6634 | 3.5875 | 3.4702 | 3.4079 | 3.2878 | 3.1728 | 3.0644 | 2.9716 | 2.8918 | 2.8156 | 2.7609 | 2.702 | 2.5047 | 1.1148 | 2.7358
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | 53.2741 | -1.1997 | WPD Best View | Headroom (MW) | Thermal | 3.9769 | 3.8959 | 3.7407 | 3.6207 | 3.5584 | 3.4152 | 3.2016 | 2.9634 | 2.6777 | 2.4069 | 1.9822 | 1.5184 | 0.30442 | -0.032555 | -0.3426 | -0.6631 | -2.7346 | -5.0258 | -5.0743
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Consumer Transformation | Headroom (MW) | Thermal | 3.2145 | 3.189 | 3.1355 | 3.1045 | 3.074 | 3.0441 | 2.9905 | 2.9628 | 2.9128 | 2.8267 | 2.7068 | 2.6148 | 2.5157 | 2.4276 | 2.342 | 2.2416 | 1.6043 | 0.79536 | -0.044239
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Leading the Way | Headroom (MW) | N/A | 3.2158 | 3.1802 | 3.1281 | 3.0826 | 3.0522 | 3.0227 | 2.9032 | 2.8758 | 2.8215 | 2.7982 | 2.7439 | 2.6523 | 2.5594 | 2.4602 | 2.4509 | 2.4413 | 2.1942 | 7.407 | 6.7044
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | Steady Progression | Headroom (MW) | Thermal | 3.2133 | 3.1867 | 3.132 | 3.0989 | 3.0679 | 3.0373 | 2.9964 | 0.91619 | -1.1674 | -1.1962 | -2.1583 | -3.036 | -3.0646 | -3.0908 | -3.1159 | -3.1399 | -3.2614 | -3.3992 | -3.6609
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | System Transformation | Headroom (MW) | N/A | 3.2144 | 3.1888 | 3.1351 | 3.1039 | 3.0729 | 3.0423 | 3.0089 | 2.9795 | 2.9489 | 2.9206 | 2.8931 | 2.8668 | 2.8403 | 2.8172 | 2.7961 | 2.775 | 2.6858 | 2.4539 | 2.0264
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | 53.3283 | -1.3421 | WPD Best View | Headroom (MW) | Thermal | 3.2133 | 3.1868 | 3.1322 | 3.1011 | 3.0703 | 3.04 | 3.0106 | 1.9562 | 0.90242 | 0.87484 | 0.38305 | -0.067405 | -0.091602 | -0.11464 | -0.1364 | -0.15708 | -0.2481 | -0.33194 | -0.43634
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Consumer Transformation | Headroom (MW) | N/A | 8.2445 | 8.2059 | 8.2939 | 8.4596 | 8.6112 | 8.5016 | 8.3618 | 8.101 | 7.8526 | 7.5979 | 7.3006 | 7.02 | 6.7274 | 6.4266 | 6.1281 | 5.8289 | 4.4199 | 3.3854 | 1.3741
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Leading the Way | Headroom (MW) | N/A | 8.2618 | 8.235 | 8.4108 | 8.7015 | 8.9675 | 8.9336 | 8.7973 | 8.6257 | 8.4353 | 8.2435 | 8.027 | 7.7856 | 7.5785 | 7.2965 | 7.0493 | 6.8111 | 5.518 | 3.3781 | 1.8377
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | Steady Progression | Headroom (MW) | N/A | 8.2553 | 8.2272 | 8.3057 | 8.4643 | 8.6073 | 8.6584 | 8.6964 | 8.7091 | 8.7315 | 8.7419 | 8.7338 | 8.7428 | 8.7584 | 8.7737 | 8.7927 | 8.7311 | 8.8416 | 9.031 | 8.7216
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | System Transformation | Headroom (MW) | N/A | 8.256 | 8.2271 | 8.3385 | 8.5471 | 8.7396 | 8.7738 | 8.7772 | 8.753 | 8.6581 | 8.555 | 8.3586 | 8.1568 | 7.9624 | 7.7686 | 7.5772 | 7.3957 | 6.93 | 6.6156 | 6.042
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | 53.3133 | -1.165 | WPD Best View | Headroom (MW) | N/A | 8.2438 | 8.2043 | 8.2905 | 8.4541 | 8.603 | 8.4896 | 8.345 | 8.1592 | 7.9891 | 7.805 | 7.5799 | 7.3708 | 7.1483 | 6.9186 | 6.6914 | 6.4636 | 5.3908 | 4.4794 | 2.5363
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Consumer Transformation | Headroom (MW) | Thermal | 3.8675 | 3.8376 | 3.7876 | 3.7378 | 3.6916 | 3.621 | 3.5225 | 3.4245 | 3.3365 | 3.2484 | 3.1373 | 2.9648 | 1.9697 | 1.8276 | 1.6956 | 1.5573 | -0.03082 | -3.2074 | -5.1978
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Leading the Way | Headroom (MW) | Thermal | 3.8827 | 3.8633 | 3.8384 | 3.8208 | 3.8037 | 3.7907 | 3.764 | 3.7434 | 3.7213 | 3.72 | 3.7022 | 3.6249 | 3.4898 | 3.3096 | 3.25 | 3.2652 | 1.0354 | -0.61135 | -2.7832
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | Steady Progression | Headroom (MW) | Thermal | 3.8808 | 3.8659 | 3.8288 | 3.8149 | -2.3487 | -2.3677 | -2.3772 | -5.4698 | -7.5285 | -7.5428 | -8.8732 | -10.0772 | -10.0709 | -10.061 | -10.0506 | -10.038 | -9.8734 | -9.9275 | -10.1379
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | System Transformation | Headroom (MW) | N/A | 3.8793 | 3.8538 | 3.8197 | 3.7904 | 3.7594 | 3.7277 | 3.6734 | 3.6235 | 3.5649 | 3.5184 | 3.4629 | 3.4387 | 3.4134 | 3.4105 | 3.4073 | 3.4138 | 3.5108 | 2.0619 | 0.68243
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | 53.1962 | -1.2442 | WPD Best View | Headroom (MW) | Thermal | 3.8675 | 3.8376 | 3.7876 | 3.7378 | 3.6916 | 3.621 | 3.5225 | 3.4245 | 3.3365 | 3.2484 | 3.1373 | 2.9648 | 1.9697 | 1.8276 | 1.6956 | 1.5573 | -0.03082 | -3.2074 | -5.1978
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Consumer Transformation | Headroom (MW) | N/A | 10.1497 | 10.0793 | 9.9598 | 9.8963 | 9.8285 | 9.6993 | 9.5181 | 9.3586 | 9.2429 | 9.093 | 8.9503 | 8.7951 | 8.6546 | 8.5034 | 8.3916 | 8.2479 | 6.3582 | 4.9754 | 0.98144
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Leading the Way | Headroom (MW) | N/A | 10.1579 | 10.1127 | 10.025 | 10.0201 | 10.008 | 9.9554 | 9.8776 | 9.8211 | 9.8051 | 9.7712 | 9.7567 | 9.7518 | 9.684 | 9.5236 | 9.5199 | 9.5134 | 6.704 | 5.6799 | 3.5085
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | Steady Progression | Headroom (MW) | N/A | 10.1558 | 10.112 | 10.0143 | 9.9918 | 9.9596 | 9.9201 | 9.8789 | 9.8349 | 9.8195 | 9.7741 | 9.7463 | 9.7206 | 9.6936 | 9.6781 | 9.6761 | 9.6623 | 9.7567 | 9.6052 | 9.2287
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | System Transformation | Headroom (MW) | N/A | 10.1534 | 10.0994 | 9.9947 | 9.9635 | 9.9303 | 9.8556 | 9.7455 | 9.6557 | 9.5872 | 9.4977 | 9.4275 | 9.3554 | 9.2992 | 9.2543 | 9.2308 | 9.2048 | 9.1844 | 8.8314 | 5.5655
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | 53.3089 | -1.3165 | WPD Best View | Headroom (MW) | N/A | 10.1483 | 10.076 | 9.953 | 9.8853 | 9.812 | 9.6752 | 9.4845 | 9.3131 | 9.1817 | 9.0135 | 8.8495 | 8.6681 | 8.4994 | 8.3187 | 8.1791 | 8.0194 | 6.1818 | 5.0453 | 1.1876
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Consumer Transformation | Headroom (MW) | N/A | 68.7146 | 68.6155 | 67.3141 | 67.1558 | 66.9993 | 66.6525 | 66.1258 | 65.6125 | 65.1221 | 64.4995 | 62.7788 | 61.2286 | 65.1143 | 61.9918 | 59.5776 | 57.0373 | 29.9959 | 18.6016 | 2.645
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Leading the Way | Headroom (MW) | Thermal | 68.767 | 68.1696 | 67.9908 | 67.9341 | 67.8999 | 67.8439 | 67.4575 | 67.2987 | 67.1058 | 66.9794 | 66.6763 | 64.3622 | 67.3023 | 63.662 | 59.9487 | 56.1841 | 29.9399 | 7.2251 | -17.3785
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | Steady Progression | Headroom (MW) | N/A | 68.7151 | 68.6143 | 67.9863 | 64.8053 | 64.7377 | 64.6472 | 64.5155 | 64.3952 | 64.2641 | 64.1455 | 63.4803 | 62.8871 | 62.792 | 62.7106 | 62.6507 | 62.6035 | 62.9855 | 52.567 | 50.8004
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | System Transformation | Headroom (MW) | N/A | 68.7319 | 68.663 | 67.3862 | 67.3046 | 67.2062 | 67.0999 | 66.925 | 66.671 | 66.4137 | 66.1337 | 65.8694 | 65.6416 | 71.6051 | 71.4727 | 71.3705 | 71.2253 | 68.8932 | 64.6349 | 54.9518
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | 52.4536 | -1.4678 | WPD Best View | Headroom (MW) | N/A | 68.7586 | 68.7508 | 67.5485 | 64.4426 | 64.4154 | 64.3247 | 64.1357 | 63.8606 | 63.6642 | 63.2753 | 62.5751 | 61.9617 | 67.7566 | 67.4661 | 67.1862 | 66.8282 | 63.8316 | 55.7941 | 45.1904
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Consumer Transformation | Headroom (MW) | Thermal | 11.6561 | 11.624 | 11.5724 | 11.5234 | 11.4824 | 11.4328 | 11.3654 | 11.3043 | 11.2456 | 11.2083 | 10.1973 | 10.131 | 10.0877 | 9.1405 | 9.1494 | 9.1605 | 4.3732 | -1.7906 | -9.4079
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Leading the Way | Headroom (MW) | Thermal | 11.662 | 11.6439 | 11.5912 | 11.5685 | 11.526 | 11.5059 | 11.4665 | 11.4369 | 11.4045 | 11.389 | 11.3423 | 11.3234 | 10.4242 | 9.1978 | 7.5718 | 5.9115 | 0.83695 | -6.9097 | -15.8114
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | Steady Progression | Headroom (MW) | N/A | 11.654 | 11.6291 | 11.5773 | 11.5466 | 11.527 | 11.5083 | 11.4915 | 11.477 | 11.4505 | 11.4416 | 11.4269 | 11.4196 | 11.427 | 11.4405 | 11.4526 | 11.4794 | 11.6987 | 10.5533 | 10.2842
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | System Transformation | Headroom (MW) | N/A | 11.6562 | 11.6311 | 11.5692 | 11.5445 | 11.5035 | 11.4789 | 11.4451 | 11.4118 | 11.3829 | 11.3623 | 11.3467 | 11.3252 | 11.3293 | 11.3521 | 11.3915 | 11.4371 | 8.2441 | 5.5647 | 1.2709
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | 52.4289 | -1.401 | WPD Best View | Headroom (MW) | N/A | 11.6562 | 11.6339 | 11.5838 | 11.5517 | 11.5202 | 11.5031 | 11.4876 | 11.4732 | 11.4697 | 11.48 | 11.484 | 11.5128 | 11.5513 | 11.6064 | 11.6512 | 11.6912 | 11.7432 | 10.2088 | 7.4583
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Consumer Transformation | Headroom (MW) | N/A | 14.8393 | 14.9175 | 14.8945 | 14.9028 | 14.9116 | 14.8916 | 14.8605 | 14.8446 | 14.818 | 14.8017 | 14.7558 | 14.7301 | 14.7045 | 14.6795 | 14.6707 | 14.6062 | 13.9196 | 12.8543 | 11.6872
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Leading the Way | Headroom (MW) | N/A | 14.8398 | 14.9535 | 14.9459 | 14.9626 | 14.9905 | 14.968 | 14.9097 | 14.8917 | 14.857 | 14.84 | 14.7951 | 14.7097 | 14.626 | 14.5347 | 14.5223 | 14.5089 | 14.2214 | 13.8659 | 11.8984
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | Steady Progression | Headroom (MW) | N/A | 14.8388 | 14.8861 | 14.4874 | 14.4829 | 14.4857 | 14.4612 | 14.4336 | 14.4122 | 14.3887 | 14.3668 | 14.3428 | 14.3214 | 14.2991 | 14.2783 | 14.2567 | 14.2356 | 14.1179 | 14.0231 | 13.7591
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | System Transformation | Headroom (MW) | N/A | 14.8392 | 14.9173 | 14.894 | 14.9019 | 14.9101 | 14.8893 | 14.8691 | 14.8512 | 14.835 | 14.8146 | 14.7925 | 14.7721 | 14.7502 | 14.7302 | 14.7124 | 14.6967 | 14.6213 | 14.4886 | 14.1714
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | 52.4499 | -1.4938 | WPD Best View | Headroom (MW) | N/A | 14.8398 | 14.959 | 14.9507 | 14.9739 | 15.0011 | 14.9779 | 14.968 | 14.9488 | 14.93 | 14.9111 | 14.8891 | 14.8623 | 14.845 | 14.8299 | 14.8157 | 14.8013 | 14.6899 | 14.2224 | 12.0016
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Consumer Transformation | Headroom (MW) | Thermal | 16.9783 | 16.9343 | 16.8341 | 16.7827 | 16.7103 | 16.5436 | 16.3315 | 16.1148 | 15.9196 | 15.7516 | 15.5611 | 14.5628 | 12.7688 | 10.9956 | 8.9132 | 6.8324 | -11.7657 | -12.4935 | -13.5126
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Leading the Way | Headroom (MW) | Thermal | 16.9815 | 16.931 | 16.8338 | 16.7701 | 16.7221 | 16.6709 | 16.5093 | 16.4621 | 16.3771 | 16.3318 | 16.2426 | 14.2476 | 12.236 | 10.2019 | 8.1264 | 6.0507 | -13.1023 | -24.1033 | -35.1243
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | Steady Progression | Headroom (MW) | N/A | 16.9756 | 16.9284 | 16.8256 | 16.7701 | 16.7167 | 16.6618 | 16.5973 | 16.5442 | 16.4876 | 16.4346 | 16.3786 | 16.3333 | 16.2817 | 16.2332 | 16.1861 | 16.1407 | 15.9325 | 7.076 | 6.6618
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | System Transformation | Headroom (MW) | N/A | 16.9782 | 16.9341 | 16.8337 | 16.7819 | 16.7306 | 16.6768 | 16.6204 | 16.5285 | 16.3921 | 16.2693 | 16.1538 | 16.0647 | 15.9751 | 15.9062 | 15.8469 | 15.7975 | 15.6497 | 15.1898 | 14.3976
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | 52.4538 | -1.4675 | WPD Best View | Headroom (MW) | N/A | 16.9805 | 16.9396 | 16.8423 | 16.7936 | 16.7453 | 16.6629 | 16.5019 | 16.3331 | 16.1796 | 16.063 | 15.9574 | 15.893 | 15.8025 | 15.7301 | 15.6481 | 15.547 | 14.8368 | 12.5027 | 11.269
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Consumer Transformation | Headroom (MW) | N/A | 11.5305 | 11.4935 | 10.4929 | 10.4935 | 10.5039 | 10.4528 | 10.3363 | 10.1778 | 10.065 | 9.926 | 9.7608 | 9.6007 | 9.4531 | 9.3332 | 9.236 | 9.1023 | 7.6788 | 6.1063 | 1.862
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Leading the Way | Headroom (MW) | N/A | 11.5718 | 11.0083 | 11.1129 | 11.21 | 11.2985 | 11.3927 | 11.455 | 11.4495 | 11.5067 | 11.5097 | 11.4911 | 11.4512 | 11.4208 | 11.3358 | 11.3591 | 11.3782 | 10.2018 | 7.1904 | 5.7677
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | Steady Progression | Headroom (MW) | N/A | 11.5374 | 11.5257 | 11.5773 | 11.633 | 11.7 | 11.7698 | 11.8258 | 11.8578 | 11.9006 | 11.9268 | 11.9421 | 11.9579 | 11.9904 | 12.022 | 12.0692 | 12.1155 | 12.8756 | 12.856 | 12.5235
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | System Transformation | Headroom (MW) | N/A | 11.548 | 11.5345 | 10.5696 | 10.6234 | 10.672 | 10.7248 | 10.7272 | 10.6791 | 10.6672 | 10.6109 | 10.5579 | 10.5173 | 10.4947 | 10.4818 | 10.4948 | 10.5038 | 12.0247 | 11.6712 | 8.3346
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | 52.486 | -1.4991 | WPD Best View | Headroom (MW) | N/A | 11.5718 | 11.5721 | 10.6516 | 10.7469 | 10.8354 | 10.9278 | 10.9872 | 10.9768 | 11.0165 | 11.0057 | 10.9658 | 10.9181 | 10.8723 | 10.8614 | 10.8613 | 10.844 | 10.1014 | 8.1376 | 5.5795
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Consumer Transformation | Headroom (MW) | N/A | 18.0854 | 18.0212 | 17.8952 | 17.8284 | 17.7661 | 17.7067 | 17.6071 | 17.5461 | 17.4489 | 17.1869 | 16.8787 | 16.5792 | 22.4752 | 22.218 | 21.9832 | 21.7108 | 20.165 | 18.3001 | 16.3912
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Leading the Way | Headroom (MW) | N/A | 18.0869 | 18.0079 | 17.8819 | 17.7979 | 17.7378 | 17.6812 | 17.4921 | 17.4335 | 17.3355 | 17.2839 | 17.1801 | 17.0053 | 22.9703 | 22.7668 | 22.7442 | 22.7098 | 22.1572 | 21.5568 | 20.2661
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | Steady Progression | Headroom (MW) | N/A | 18.0842 | 18.0199 | 17.8937 | 14.7477 | 14.6834 | 14.621 | 14.5424 | 14.4789 | 14.4117 | 14.3507 | 13.7647 | 13.2298 | 13.1688 | 13.1116 | 13.0611 | 13.0073 | 12.7357 | 12.4336 | 11.9468
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | System Transformation | Headroom (MW) | N/A | 18.0853 | 18.0211 | 17.8948 | 17.8278 | 17.765 | 17.705 | 17.6382 | 17.5755 | 17.5115 | 17.4515 | 17.3935 | 17.3374 | 23.4308 | 23.3773 | 23.2999 | 23.1652 | 22.7283 | 22.0956 | 21.1522
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | 52.4255 | -1.4463 | WPD Best View | Headroom (MW) | N/A | 18.0853 | 18.0211 | 17.895 | 14.7515 | 14.6883 | 14.628 | 14.566 | 14.5038 | 14.4434 | 14.1905 | 13.6539 | 13.1504 | 19.0606 | 18.8133 | 18.5847 | 18.3196 | 16.8353 | 15.0975 | 13.2569
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Consumer Transformation | Headroom (MW) | N/A | 19.9928 | 19.9098 | 19.7579 | 19.6546 | 19.55 | 19.3994 | 19.211 | 19.0284 | 18.8673 | 18.6941 | 18.5225 | 18.3573 | 18.2382 | 18.1072 | 17.9779 | 17.8399 | 16.9734 | 15.7418 | 14.4353
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Leading the Way | Headroom (MW) | N/A | 20.0066 | 19.9541 | 19.8576 | 19.7885 | 19.7369 | 19.6784 | 19.575 | 19.5284 | 19.4607 | 19.4215 | 19.3525 | 19.2438 | 19.1232 | 18.9903 | 18.967 | 18.943 | 18.5493 | 17.6223 | 16.5094
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | Steady Progression | Headroom (MW) | N/A | 19.997 | 19.9437 | 19.8378 | 19.7703 | 19.7137 | 19.6569 | 19.6025 | 19.5432 | 19.4769 | 19.4226 | 19.3645 | 19.3156 | 19.2743 | 19.2339 | 19.2121 | 19.1967 | 19.0037 | 18.7874 | 18.4271
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | System Transformation | Headroom (MW) | N/A | 19.9989 | 19.9472 | 19.8208 | 19.7319 | 19.6547 | 19.5646 | 19.4449 | 19.3333 | 19.2023 | 19.0871 | 18.9674 | 18.8765 | 18.7907 | 18.7228 | 18.674 | 18.6214 | 18.5063 | 18.1203 | 17.4219
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | 52.4059 | -1.5387 | WPD Best View | Headroom (MW) | N/A | 19.9928 | 19.9098 | 19.7579 | 19.6546 | 19.55 | 19.3994 | 19.211 | 19.0284 | 18.8673 | 18.6941 | 18.5225 | 18.3573 | 18.2382 | 18.1072 | 17.9779 | 17.8399 | 16.9734 | 15.7418 | 14.4353
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Consumer Transformation | Headroom (MW) | Thermal | 19.1445 | 18.5766 | 18.1673 | 17.8489 | 17.5537 | 17.1183 | 15.692 | 13.5164 | 12.4154 | 10.9868 | 5.8764 | -16.8259 | -31.1274 | -37.8244 | -47.5325 | -55.1879 | -102.7122 | -143.7376 | -180.9943
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Leading the Way | Headroom (MW) | Thermal | 18.1896 | 17.5425 | 16.2774 | 15.6129 | 15.5113 | 14.3919 | -4.0775 | -4.731 | -6.0723 | -7.0341 | -7.5784 | -14.0314 | -25.3313 | -30.3964 | -45.1065 | -56.1283 | -102.0654 | -148.8535 | -195.0258
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | Steady Progression | Headroom (MW) | Thermal | 19.1709 | 18.6356 | 18.2926 | 18.1438 | 18.0107 | 17.9045 | 13.9153 | 9.9108 | 6.1368 | 2.0207 | -0.77265 | -4.972 | -7.5295 | -10.0592 | -13.6914 | -15.5096 | -26.4467 | -54.5409 | -61.8996
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | System Transformation | Headroom (MW) | Thermal | 19.1747 | 19.0009 | 18.6591 | 18.4751 | 18.2968 | 18.1342 | 17.2793 | 16.3292 | 15.4483 | 14.2835 | 15.4509 | -2.4237 | -3.2226 | -3.9566 | -4.763 | -4.3129 | -26.5041 | -44.2791 | -66.6476
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | 52.2593 | -1.1548 | WPD Best View | Headroom (MW) | Thermal | 19.584 | 19.3832 | 18.9868 | 18.7547 | 18.527 | 18.3315 | 16.2373 | 14.2229 | 11.8968 | 9.6779 | 9.9934 | -9.344 | -9.322 | -9.2546 | -9.7979 | -11.0954 | -39.0289 | -57.6663 | -82.2482
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Consumer Transformation | Headroom (MW) | Thermal | 14.9975 | 14.967 | 14.8854 | 14.7542 | 14.6431 | 14.4808 | 14.496 | 14.5052 | 14.2661 | 14.0149 | 12.7778 | 12.5499 | 12.3311 | 11.1783 | 10.9984 | 11.8324 | 7.7517 | 2.9645 | -1.9041
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Leading the Way | Headroom (MW) | N/A | 15.0158 | 15.0322 | 15.0173 | 14.9281 | 14.8636 | 14.8048 | 15.025 | 15.2472 | 15.0941 | 14.9333 | 14.7376 | 13.696 | 13.596 | 13.5314 | 11.7887 | 12.7238 | 8.7016 | 5.2986 | 0.83355
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | Steady Progression | Headroom (MW) | Thermal | 15.0108 | 14.9877 | 14.9225 | 14.8763 | 14.8565 | 14.8408 | 11.8721 | 8.8997 | 5.7923 | 2.693 | 0.88054 | -0.75098 | -0.77499 | -0.7889 | -1.5152 | -1.5349 | -1.5657 | -1.5207 | -2.019
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | System Transformation | Headroom (MW) | N/A | 15.0103 | 14.9953 | 14.9488 | 14.8789 | 14.8373 | 14.8094 | 14.9595 | 15.0962 | 14.9915 | 14.889 | 14.7744 | 14.7317 | 14.6809 | 14.62 | 14.5708 | 15.5509 | 14.388 | 12.5764 | 10.4837
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | 52.2612 | -1.1752 | WPD Best View | Headroom (MW) | Thermal | 15.0103 | 14.9947 | 14.9481 | 14.8773 | 14.835 | 14.8057 | 12.9035 | 10.9876 | 8.8288 | 6.671 | 5.3104 | 4.1259 | 4.0644 | 3.9907 | 3.2159 | 4.1808 | 2.9642 | 1.2533 | -0.7645
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Consumer Transformation | Headroom (MW) | Thermal | 13.45 | 13.3966 | 13.3307 | 13.3216 | 13.2808 | 13.2114 | 13.1891 | 13.1755 | 13.1521 | 13.1172 | 12.0935 | 10.2839 | 10.1826 | 10.0793 | 4.4561 | 4.3815 | 1.1828 | -2.9402 | -8.3179
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Leading the Way | Headroom (MW) | Thermal | 13.4696 | 13.4161 | 13.3909 | 13.4194 | 13.4106 | 13.3783 | 13.4413 | 13.4979 | 13.5066 | 13.5264 | 13.5015 | 11.7934 | 11.7919 | 10.8471 | 4.4961 | 5.8207 | 2.4341 | -3.6987 | -7.9893
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | Steady Progression | Headroom (MW) | N/A | 13.4546 | 13.3997 | 13.3447 | 13.3567 | 13.3542 | 13.3554 | 13.3955 | 13.4583 | 13.5262 | 13.594 | 13.2084 | 12.8505 | 12.9384 | 13.0219 | 13.1123 | 13.1934 | 13.3927 | 6.0883 | 6.0856
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | System Transformation | Headroom (MW) | N/A | 13.4593 | 13.4072 | 13.3701 | 13.3931 | 13.4 | 13.3993 | 13.4771 | 13.5759 | 13.6718 | 13.7841 | 13.8918 | 14.0207 | 14.1345 | 14.2683 | 14.4012 | 14.542 | 6.2595 | 4.7825 | 1.6966
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | 52.3521 | -1.1647 | WPD Best View | Headroom (MW) | N/A | 13.4539 | 13.3982 | 13.3409 | 13.3414 | 13.3346 | 13.3269 | 13.4141 | 13.5188 | 13.6209 | 13.7357 | 13.6196 | 13.555 | 13.6957 | 13.8592 | 14.0216 | 14.19 | 5.8272 | 4.6023 | 1.626
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Consumer Transformation | Headroom (MW) | Thermal | 14.5746 | 14.2038 | 14.1563 | 14.1373 | 14.1204 | 14.1019 | 12.9866 | 11.9434 | 11.3492 | 10.3103 | 9.5538 | 8.29 | 6 | 4.6522 | 3.6239 | 3.7271 | 1.5159 | -2.0109 | -5.8889
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Leading the Way | Headroom (MW) | Thermal | 13.5529 | 12.9965 | 11.9278 | 11.3654 | 11.3534 | 10.3139 | 7.7157 | 6.6773 | 5.3925 | 4.3582 | 2.9092 | 2.1212 | 1.4712 | 0.58818 | 0.58194 | -0.16282 | -1.7735 | -5.0907 | -8.4133
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | Steady Progression | Headroom (MW) | N/A | 14.5718 | 14.1981 | 14.1474 | 14.1224 | 14.1013 | 14.0793 | 13.0702 | 12.0229 | 11.3332 | 10.2881 | 9.7373 | 8.7489 | 7.8676 | 6.9817 | 5.9432 | 5.9955 | 4.3896 | 2.9155 | 1.1592
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | System Transformation | Headroom (MW) | N/A | 14.5746 | 14.5555 | 14.508 | 14.489 | 14.4719 | 14.4532 | 13.566 | 12.522 | 11.8387 | 10.7978 | 10.1204 | 9.2461 | 8.3709 | 7.4995 | 6.4664 | 6.5657 | 5.9265 | 4.6084 | 2.4548
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | 52.2596 | -1.1549 | WPD Best View | Headroom (MW) | N/A | 14.9835 | 14.933 | 14.8363 | 14.7709 | 14.6908 | 14.6117 | 14.4873 | 14.3588 | 14.2067 | 14.0684 | 13.928 | 13.7888 | 13.6624 | 13.5324 | 13.4184 | 13.4684 | 12.3323 | 12.0032 | 9.2986
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Consumer Transformation | Headroom (MW) | Thermal | 4.0816 | 4.0665 | 4.0253 | 3.994 | 3.9728 | 3.9487 | 3.9006 | 3.879 | 3.8446 | 3.845 | 3.8372 | 2.899 | 1.9695 | 1.9751 | 2.0366 | 1.147 | -2.2945 | -8.3957 | -14.9986
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Leading the Way | Headroom (MW) | Thermal | 4.0856 | 4.0763 | 4.0521 | 4.0431 | 4.0439 | 4.0627 | 4.0686 | 4.1045 | 4.1441 | 4.204 | 4.1883 | 4.1304 | 4.0737 | 3.1233 | 1.918 | -2.3503 | -6.0082 | -12.3525 | -17.9972
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | Steady Progression | Headroom (MW) | N/A | 4.0826 | 4.0655 | 4.0308 | 4.0151 | 4.002 | 3.9919 | 3.9794 | 3.977 | 3.9678 | 3.9745 | 3.9715 | 3.9773 | 3.9914 | 4.0159 | 4.0598 | 4.1134 | 4.1319 | 3.2984 | 3.1087
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | System Transformation | Headroom (MW) | Thermal | 4.0821 | 4.064 | 4.0275 | 4.0002 | 3.9749 | 3.9646 | 3.9286 | 3.9096 | 3.8742 | 3.8571 | 3.8472 | 3.8619 | 3.8794 | 3.9189 | 3.9754 | 4.0378 | 2.1932 | -0.40842 | -5.5482
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | 52.2348 | -1.0811 | WPD Best View | Headroom (MW) | Thermal | 4.084 | 4.0693 | 4.0381 | 4.0188 | 4.0032 | 4.0059 | 3.9878 | 3.9915 | 3.9907 | 4.0074 | 4.0228 | 4.0683 | 4.1139 | 4.1715 | 4.2435 | 1.6793 | -1.6998 | -5.5194 | -9.9573
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Consumer Transformation | Headroom (MW) | Thermal | 5.3772 | 5.3475 | 5.2963 | 5.2627 | 5.226 | 5.1807 | 5.1052 | 5.0411 | 4.9896 | 4.9516 | 4.9003 | 2.6969 | 0.58308 | -1.5301 | -3.5813 | -5.6317 | -22.2591 | -32.8276 | -35.1512
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Leading the Way | Headroom (MW) | Thermal | 5.3838 | 5.3725 | 5.3351 | 5.327 | 5.3189 | 5.3126 | 5.3005 | 5.3132 | 5.3292 | 5.363 | 5.3741 | 3.3667 | 1.0614 | -1.2594 | -4.197 | -6.2487 | -22.3768 | -36.1975 | -50.0512
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | Steady Progression | Headroom (MW) | Thermal | 5.3805 | 5.3631 | 5.3264 | 5.3089 | 5.2845 | 5.2704 | 5.2572 | 5.2402 | 5.2322 | 5.2207 | 5.2126 | 3.9859 | 2.2261 | 0.45935 | -1.6052 | -3.6687 | -13.4016 | -23.9043 | -24.0788
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | System Transformation | Headroom (MW) | Thermal | 5.3797 | 5.3614 | 5.3129 | 5.2904 | 5.2589 | 5.228 | 5.1806 | 5.1475 | 5.0923 | 5.056 | 5.0183 | 5.0014 | 4.993 | 4.9973 | 5.0126 | 5.032 | 3.9159 | 1.5935 | -1.3016
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | 52.305 | -1.1295 | WPD Best View | Headroom (MW) | Thermal | 5.3797 | 5.3611 | 5.3125 | 5.2896 | 5.2578 | 5.2262 | 5.1779 | 5.1438 | 5.0868 | 5.0482 | 5.0077 | 4.9867 | 4.973 | 4.9709 | 4.9785 | 4.9904 | 3.8474 | 1.5753 | -1.2823
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Consumer Transformation | Headroom (MW) | Thermal | 2.2162 | 2.1919 | 2.1358 | 2.1002 | 2.0731 | 2.0281 | 1.9646 | 0.99473 | 0.9229 | 0.90512 | -0.12508 | -0.1961 | -1.2047 | -2.2268 | -3.1296 | -4.0557 | -11.9076 | -19.3963 | -30.2785
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Leading the Way | Headroom (MW) | Thermal | 2.2217 | 2.2059 | 2.1704 | 2.1516 | 2.1455 | 2.1463 | 2.137 | 2.1534 | 2.1539 | 2.1943 | 3.2562 | 3.2529 | 1.0642 | 1.0655 | -1.5077 | -4.0276 | -13.228 | -23.1864 | -34.2526
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | Steady Progression | Headroom (MW) | Thermal | 2.2195 | 2.197 | 2.1524 | 2.1304 | 2.1104 | 2.0845 | 2.0722 | 2.06 | 2.0396 | 2.0253 | 2.0155 | 2.0057 | 2.0058 | 2.0115 | 2.0251 | 2.0528 | 2.1949 | 1.0087 | -0.47706
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | System Transformation | Headroom (MW) | Thermal | 2.2185 | 2.1943 | 2.1464 | 2.1112 | 2.0847 | 2.0555 | 2.0136 | 1.9778 | 1.9413 | 1.9119 | 3.8668 | 2.9282 | 2.9261 | 2.9311 | 2.951 | 2.9825 | -0.31389 | -4.2433 | -10.6245
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | 52.3547 | -1.0455 | WPD Best View | Headroom (MW) | Thermal | 2.2185 | 2.1943 | 2.1464 | 2.1112 | 2.0847 | 2.0555 | 2.0136 | 1.9778 | 1.9413 | 1.9119 | 3.8668 | 2.9282 | 2.9261 | 2.9311 | 2.951 | 2.9825 | -0.31389 | -4.2433 | -10.6245
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Consumer Transformation | Headroom (MW) | Thermal | 6.2108 | 6.1667 | 6.1008 | 6.0423 | 6.0008 | 5.93 | 5.8132 | 5.7408 | 5.6543 | 5.606 | 4.6023 | 4.5389 | 4.5076 | 3.5441 | 3.5598 | 3.5471 | -0.85959 | -5.2897 | -8.6135
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Leading the Way | Headroom (MW) | Thermal | 6.2235 | 6.2064 | 6.1471 | 6.1416 | 6.1388 | 6.1366 | 6.123 | 6.1639 | 6.1958 | 6.2752 | 6.3431 | 5.4965 | 5.5853 | 5.6825 | 5.7884 | 5.8028 | 2.4366 | -1.3753 | -4.9048
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | Steady Progression | Headroom (MW) | N/A | 6.2144 | 6.1879 | 6.1316 | 6.0973 | 6.0652 | 6.0456 | 6.0321 | 6.016 | 6.0088 | 5.9885 | 5.9649 | 5.9741 | 5.9795 | 6.0028 | 6.052 | 6.1023 | 6.4568 | 6.6869 | 6.3746
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | System Transformation | Headroom (MW) | N/A | 6.2136 | 6.1865 | 6.1088 | 6.0756 | 6.0324 | 5.9875 | 5.9173 | 5.8634 | 5.8018 | 5.7509 | 5.6954 | 5.6747 | 5.681 | 5.6967 | 5.748 | 4.8646 | 5.1967 | 3.7349 | 3.1147
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | 52.1735 | -1.2078 | WPD Best View | Headroom (MW) | Thermal | 6.2176 | 6.1959 | 6.1279 | 6.1089 | 6.0842 | 6.063 | 6.0165 | 6.0079 | 5.985 | 5.9986 | 6.0013 | 5.0916 | 5.131 | 5.1782 | 5.2616 | 5.3016 | 2.0837 | -0.41468 | -3.6211
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Consumer Transformation | Headroom (MW) | Thermal | 46.027 | 45.8498 | 45.5305 | 45.2582 | 44.978 | 44.5536 | 43.9504 | 43.3701 | 42.7739 | 42.1547 | 11.6858 | 10.8974 | 9.1712 | 7.4309 | 6.5582 | 5.6136 | -3.0411 | -11.1247 | -19.6968
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Leading the Way | Headroom (MW) | Thermal | 46.0836 | 45.9881 | 45.817 | 45.6923 | 45.5542 | 45.4362 | 45.2138 | 45.019 | 31.9702 | 29.111 | 11.6336 | 11.0308 | 10.3883 | 9.7645 | 5.6849 | 2.2834 | -8.1349 | -17.5417 | -23.6178
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | Steady Progression | Headroom (MW) | N/A | 46.0849 | 45.984 | 45.7956 | 33.3937 | 33.3013 | 33.2179 | 33.1079 | 33.0122 | 32.9036 | 32.8237 | 32.6925 | 32.5931 | 32.4905 | 32.4188 | 32.3552 | 32.2595 | 31.5821 | 29.9747 | 29.1221
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | System Transformation | Headroom (MW) | Thermal | 46.0708 | 45.9435 | 45.7258 | 45.5529 | 45.3784 | 45.1828 | 44.8659 | 44.5605 | 44.1913 | 43.9034 | 13.8502 | 13.5464 | 13.2439 | 13.0013 | 12.7324 | 12.4187 | 9.63 | 5.6172 | -0.72701
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | 52.5287 | -1.3953 | WPD Best View | Headroom (MW) | Thermal | 46.0708 | 45.9435 | 45.7258 | 45.5529 | 45.3784 | 45.1828 | 44.8659 | 44.5605 | 44.1913 | 43.9034 | 13.8502 | 13.5464 | 13.2439 | 13.0013 | 12.7324 | 12.4187 | 9.63 | 5.6172 | -0.72701
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Consumer Transformation | Headroom (MW) | Thermal | 8.4117 | 8.3531 | 8.2379 | 8.1411 | 8.048 | 7.9003 | 7.6904 | 7.4885 | 7.2593 | 6.9887 | 6.6606 | 6.2992 | 5.0001 | 4.6013 | 4.1772 | 3.7106 | 0.072521 | -4.0952 | -8.1106
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Leading the Way | Headroom (MW) | Thermal | 8.433 | 8.4048 | 8.3458 | 8.2925 | 8.2444 | 8.2064 | 8.1303 | 8.0531 | 7.9115 | 5.1641 | 4.8733 | 4.524 | 4.1382 | 3.7346 | 1.6384 | 0.26876 | -4.7593 | -8.6143 | -10.9903
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | Steady Progression | Headroom (MW) | N/A | 8.4285 | 8.4011 | 8.3354 | 8.2996 | 8.2742 | 8.246 | 8.2014 | 8.1695 | 8.1352 | 8.0971 | 8.0601 | 8.0253 | 7.9856 | 7.9465 | 7.9195 | 7.8651 | 7.4837 | 7.3162 | 6.992
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | System Transformation | Headroom (MW) | N/A | 8.4269 | 8.3875 | 8.3136 | 8.2482 | 8.1948 | 8.1273 | 8.023 | 7.9157 | 7.792 | 7.6814 | 7.5631 | 7.4585 | 7.3412 | 7.2219 | 7.1088 | 6.9698 | 6.2216 | 4.3062 | 0.19648
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | 52.5827 | -1.3385 | WPD Best View | Headroom (MW) | N/A | 8.4269 | 8.3875 | 8.3136 | 8.2482 | 8.1948 | 8.1273 | 8.023 | 7.9157 | 7.792 | 7.6814 | 7.5631 | 7.4585 | 7.3412 | 7.2219 | 7.1088 | 6.9698 | 6.2216 | 4.3062 | 0.19648
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Consumer Transformation | Headroom (MW) | Thermal | 9.4903 | 9.3717 | 9.1676 | 8.9921 | 8.805 | 8.5283 | 8.135 | 7.7566 | 7.3896 | 7.0411 | 6.6043 | 6.1774 | 5.7503 | 4.4088 | 3.9602 | 3.4822 | -1.5344 | -5.4504 | -10.007
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Leading the Way | Headroom (MW) | Thermal | 9.5256 | 9.4582 | 9.3461 | 9.2748 | 9.1848 | 9.1047 | 8.9585 | 8.841 | 8.664 | 8.5523 | 8.3394 | 8.086 | 7.8293 | 7.609 | 5.6256 | 3.5938 | -1.7965 | -7.3482 | -11.0483
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | Steady Progression | Headroom (MW) | N/A | 9.5313 | 9.4579 | 9.3352 | 9.2727 | 9.2057 | 9.1505 | 9.0851 | 9.0213 | 8.947 | 8.9052 | 8.811 | 8.7464 | 8.6835 | 8.651 | 8.6143 | 8.573 | 8.277 | 6.8371 | 6.3087
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | System Transformation | Headroom (MW) | N/A | 9.5189 | 9.4311 | 9.2872 | 9.1797 | 9.0586 | 8.9305 | 8.7179 | 8.5199 | 8.2743 | 8.097 | 7.8663 | 7.667 | 7.4819 | 7.3585 | 7.2027 | 7.0281 | 4.9876 | 2.8902 | 0.65568
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | 52.5561 | -1.3744 | WPD Best View | Headroom (MW) | N/A | 9.5189 | 9.4311 | 9.2872 | 9.1797 | 9.0586 | 8.9305 | 8.7179 | 8.5199 | 8.2743 | 8.097 | 7.8663 | 7.667 | 7.4819 | 7.3585 | 7.2027 | 7.0281 | 4.9876 | 2.8902 | 0.65568
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Consumer Transformation | Headroom (MW) | N/A | 76.9306 | 76.7728 | 76.2703 | 75.9051 | 75.7005 | 75.1255 | 74.0885 | 73.1454 | 71.9888 | 69.836 | 68.4023 | 66.8956 | 65.3838 | 63.0968 | 61.88 | 58.7719 | 47.1486 | 34.5361 | 19.7006
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Leading the Way | Headroom (MW) | N/A | 77.0171 | 76.9225 | 76.5961 | 76.4766 | 76.6662 | 76.546 | 75.8077 | 75.3351 | 74.7175 | 74.2282 | 73.3071 | 71.4807 | 70.6899 | 72.8827 | 70.9156 | 70.6119 | 58.2948 | 44.0373 | 32.1711
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | Steady Progression | Headroom (MW) | N/A | 76.9169 | 76.766 | 76.3741 | 76.2241 | 76.256 | 76.146 | 75.9034 | 75.7047 | 75.4991 | 75.2752 | 74.4856 | 73.8546 | 73.6263 | 73.4642 | 73.3245 | 73.207 | 72.8887 | 72.1908 | 68.8226
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | System Transformation | Headroom (MW) | N/A | 76.955 | 76.8384 | 76.4578 | 76.3281 | 76.3474 | 76.1617 | 75.6167 | 75.113 | 74.58 | 74.0809 | 73.5502 | 73.0869 | 72.6289 | 72.251 | 71.9738 | 70.7519 | 68.6338 | 65.6776 | 59.1207
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | 52.5116 | -1.4883 | WPD Best View | Headroom (MW) | N/A | 76.9997 | 76.9297 | 76.5684 | 76.4611 | 76.5929 | 76.3798 | 75.7748 | 75.2073 | 74.6087 | 72.8294 | 71.7841 | 70.8097 | 69.9822 | 68.4907 | 68.0677 | 66.6895 | 56.0143 | 49.3634 | 35.5597
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Consumer Transformation | Headroom (MW) | Thermal | 6.1165 | 6.0912 | 6.0484 | 6.0105 | 5.9844 | 5.9357 | 5.8575 | 5.7872 | 5.7222 | 4.7539 | 4.6623 | 4.5887 | 4.5312 | 3.5371 | 3.5206 | 2.5593 | -1.1163 | -5.0755 | -10.0628
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Leading the Way | Headroom (MW) | Thermal | 6.1297 | 6.1121 | 6.0878 | 6.0726 | 6.0591 | 6.0497 | 6.0247 | 6.0189 | 6.0072 | 6.0231 | 6.0154 | 5.0852 | 5.0802 | 5.0797 | 3.4095 | 3.4173 | -1.3023 | -6.3532 | -10.2334
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | Steady Progression | Headroom (MW) | N/A | 6.1271 | 6.1048 | 6.0763 | 6.0622 | 6.0496 | 6.0303 | 6.0203 | 6.0143 | 5.997 | 5.9847 | 5.9702 | 5.9627 | 5.96 | 5.9641 | 5.98 | 5.9954 | 6.0911 | 6.0893 | 4.6973
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | System Transformation | Headroom (MW) | N/A | 6.1267 | 6.1034 | 6.0722 | 6.0457 | 6.0191 | 5.9978 | 5.9531 | 5.9146 | 5.8757 | 5.8426 | 5.7926 | 5.7743 | 5.7648 | 5.7457 | 5.7593 | 4.8415 | 3.6598 | 2.2397 | 0.6354
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | 52.5021 | -1.5755 | WPD Best View | Headroom (MW) | Thermal | 6.1165 | 6.0911 | 6.0481 | 6.0106 | 5.9846 | 5.9363 | 5.8584 | 5.7894 | 5.7261 | 4.7609 | 4.6825 | 4.6038 | 4.5504 | 3.5605 | 3.5469 | 2.5834 | -1.1258 | -5.1252 | -10.1481
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Consumer Transformation | Headroom (MW) | N/A | 16.3006 | 16.2547 | 16.1603 | 16.1085 | 16.2653 | 16.2362 | 16.1745 | 16.1264 | 16.0872 | 16.061 | 16.0094 | 15.8693 | 15.6256 | 15.3847 | 15.1446 | 14.923 | 13.6396 | 11.9359 | 10.2505
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Leading the Way | Headroom (MW) | N/A | 16.3025 | 16.2547 | 16.1609 | 16.1055 | 16.3384 | 16.3163 | 16.2382 | 16.1967 | 16.1559 | 16.1441 | 16.093 | 16.0241 | 15.9512 | 15.8709 | 15.8381 | 15.8254 | 15.618 | 15.0809 | 14.0045
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | Steady Progression | Headroom (MW) | N/A | 16.2991 | 16.2524 | 16.1575 | 16.105 | 16.2047 | 16.1702 | 16.1184 | 16.0811 | 16.044 | 16.0084 | 15.9683 | 15.9297 | 15.8909 | 15.8534 | 15.8167 | 15.7909 | 15.6592 | 15.4737 | 15.1913
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | System Transformation | Headroom (MW) | N/A | 16.3006 | 16.2547 | 16.1602 | 16.1084 | 16.265 | 16.2356 | 16.1848 | 16.1359 | 16.1082 | 16.0802 | 16.0452 | 16.0102 | 15.9684 | 15.9286 | 15.8941 | 15.8784 | 15.7984 | 15.2431 | 14.4506
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | 52.5213 | -1.4668 | WPD Best View | Headroom (MW) | N/A | 16.3025 | 16.2578 | 16.1639 | 16.1128 | 16.3457 | 16.3235 | 16.2739 | 16.2324 | 16.2003 | 16.1886 | 16.1492 | 16.1097 | 16.0732 | 16.0389 | 16.0061 | 15.9934 | 15.9089 | 15.0809 | 14.0045
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Consumer Transformation | Headroom (MW) | N/A | 14.8271 | 14.857 | 14.7954 | 14.6941 | 14.5739 | 14.3621 | 14.0718 | 13.7896 | 13.5332 | 13.2675 | 12.9916 | 12.7291 | 12.4866 | 12.2408 | 12.0166 | 11.7754 | 9.5646 | 5.7938 | 4.2279
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Leading the Way | Headroom (MW) | N/A | 14.8469 | 14.8816 | 14.8996 | 14.9176 | 14.9122 | 14.8177 | 14.6837 | 14.5568 | 14.4198 | 14.3143 | 14.2193 | 14.1668 | 14.1264 | 13.9639 | 13.9517 | 13.9382 | 12.0231 | 8.8786 | 5.5857
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | Steady Progression | Headroom (MW) | N/A | 14.8122 | 14.8253 | 14.8039 | 14.8111 | 14.8226 | 14.8116 | 14.7785 | 14.7632 | 14.7315 | 14.6813 | 14.6244 | 14.5782 | 14.5332 | 14.4985 | 14.4663 | 14.4405 | 14.4106 | 14.283 | 13.8895
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | System Transformation | Headroom (MW) | N/A | 14.827 | 14.8568 | 14.8529 | 14.8755 | 14.8501 | 14.7717 | 14.6316 | 14.4973 | 14.3463 | 14.1985 | 14.0496 | 13.9204 | 13.8032 | 13.693 | 13.6024 | 13.5091 | 13.2178 | 11.4909 | 10.799
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | 52.5013 | -1.4434 | WPD Best View | Headroom (MW) | N/A | 14.8469 | 14.8979 | 14.9159 | 14.9463 | 14.9037 | 14.8052 | 14.666 | 14.5319 | 14.3852 | 14.2675 | 14.158 | 14.0882 | 14.0295 | 13.9635 | 13.8937 | 13.8108 | 11.9722 | 11.2012 | 8.0399
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Consumer Transformation | Headroom (MW) | N/A | 16.578 | 16.549 | 16.4662 | 16.4346 | 16.4007 | 16.4079 | 16.3354 | 16.3082 | 16.0278 | 15.6775 | 15.2712 | 14.8652 | 14.5032 | 14.2914 | 14.115 | 13.9493 | 13.1755 | 11.979 | 8.2992
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Leading the Way | Headroom (MW) | N/A | 16.5862 | 16.5522 | 16.4745 | 16.4312 | 16.4031 | 16.4307 | 16.219 | 16.1984 | 16.102 | 16.0915 | 15.7708 | 15.4369 | 15.22 | 14.9761 | 15.0748 | 15.169 | 13.7109 | 11.3068 | 9.8369
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | Steady Progression | Headroom (MW) | N/A | 16.5718 | 16.5371 | 16.4496 | 16.4098 | 16.3699 | 16.3597 | 16.3085 | 16.2716 | 16.2329 | 16.2008 | 16.1654 | 16.1383 | 16.1062 | 16.1143 | 16.1304 | 16.1478 | 16.1863 | 16.0797 | 15.7175
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | System Transformation | Headroom (MW) | N/A | 16.5778 | 16.5486 | 16.4654 | 16.4332 | 16.3985 | 16.4043 | 16.3669 | 16.3365 | 16.3039 | 16.2806 | 16.26 | 16.2447 | 16.2219 | 16.2614 | 16.311 | 16.3608 | 16.5635 | 16.4442 | 14.3775
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | 52.53 | -1.4364 | WPD Best View | Headroom (MW) | N/A | 16.5859 | 16.5632 | 16.4849 | 16.4577 | 16.4286 | 16.4549 | 16.4278 | 16.4047 | 16.3845 | 16.0746 | 15.7018 | 15.3597 | 15.1219 | 15.0999 | 15.1278 | 15.1737 | 15.1101 | 13.2576 | 10.9338
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Consumer Transformation | Headroom (MW) | N/A | 14.1928 | 14.2033 | 14.1774 | 14.1831 | 14.1611 | 14.0802 | 13.86 | 13.6507 | 13.4315 | 13.1915 | 12.9134 | 12.6262 | 12.3502 | 12.1233 | 11.8915 | 11.658 | 10.6289 | 9.4777 | 8.28
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Leading the Way | Headroom (MW) | N/A | 14.2098 | 14.2289 | 14.222 | 14.2827 | 14.3828 | 14.4537 | 14.3259 | 14.1884 | 14.0238 | 13.8225 | 13.5767 | 13.3277 | 13.0986 | 12.973 | 12.8507 | 12.7364 | 12.043 | 12.2688 | 11.3896
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | Steady Progression | Headroom (MW) | N/A | 14.18 | 14.177 | 14.1363 | 14.1575 | 14.1949 | 14.2231 | 14.1937 | 14.1774 | 14.1614 | 14.1483 | 14.0379 | 14.0177 | 13.9676 | 13.9373 | 13.9015 | 13.8564 | 13.7747 | 13.6526 | 13.2674
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | System Transformation | Headroom (MW) | N/A | 14.1928 | 14.2032 | 14.1772 | 14.2202 | 14.2809 | 14.3289 | 14.2221 | 14.1322 | 14.0303 | 13.93 | 13.8265 | 13.7198 | 13.6132 | 13.5131 | 13.4227 | 13.3298 | 13.0354 | 12.6144 | 12.0111
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | 52.5119 | -1.4883 | WPD Best View | Headroom (MW) | N/A | 14.2098 | 14.237 | 14.23 | 14.3026 | 14.4027 | 14.4537 | 14.3259 | 14.1884 | 14.0238 | 13.8225 | 13.5767 | 13.3277 | 13.0986 | 12.973 | 12.8507 | 12.7364 | 12.043 | 12.2688 | 11.3896
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Consumer Transformation | Headroom (MW) | N/A | 12.9156 | 12.8176 | 12.6227 | 12.4743 | 12.3151 | 12.1034 | 11.7894 | 11.4833 | 11.1868 | 10.8846 | 10.5544 | 10.2171 | 9.8871 | 9.5196 | 9.1918 | 7.9069 | 5.2563 | 4.4253 | 2.706
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Leading the Way | Headroom (MW) | N/A | 12.9419 | 12.893 | 12.7514 | 12.667 | 12.5706 | 12.4779 | 12.3162 | 12.1758 | 12.0087 | 11.8327 | 11.6319 | 11.44 | 11.2135 | 14.0191 | 13.7908 | 13.5256 | 10.2021 | 6.8554 | 5.5878
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | Steady Progression | Headroom (MW) | N/A | 12.9267 | 12.8693 | 12.7506 | 12.6786 | 12.6143 | 12.551 | 12.4839 | 12.3969 | 12.3324 | 12.2517 | 11.7194 | 11.2279 | 11.1683 | 11.0967 | 11.0299 | 10.9759 | 10.7668 | 10.6125 | 10.0597
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | System Transformation | Headroom (MW) | N/A | 12.93 | 12.8717 | 12.7299 | 12.645 | 12.5339 | 12.4233 | 12.2583 | 12.0965 | 11.9156 | 11.7489 | 11.5763 | 11.4175 | 11.2574 | 11.1091 | 10.9843 | 10.8323 | 10.3591 | 11.6453 | 10.847
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | 52.5264 | -1.515 | WPD Best View | Headroom (MW) | N/A | 12.9381 | 12.8827 | 12.7255 | 12.631 | 12.5275 | 12.4063 | 12.2229 | 12.0605 | 11.8887 | 11.7153 | 11.516 | 11.3207 | 11.1086 | 10.855 | 10.6425 | 10.3918 | 6.1059 | 6.6802 | 5.34
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Consumer Transformation | Headroom (MW) | Thermal | 20.1 | 19.8652 | 19.4333 | -6.3544 | -6.683 | -7.1556 | -7.6504 | -35.9837 | -36.4328 | -36.909 | -38.4201 | -43.6027 | -65.3895 | -66.7365 | -99.2732 | -99.4432 | -112.6893 | -136.0846 | -155.3502
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Leading the Way | Headroom (MW) | Thermal | 20.1559 | 19.372 | -6.4082 | -6.5715 | -6.7241 | -6.9295 | -6.9741 | -7.0437 | -7.0294 | -34.9191 | -67.3054 | -70.2922 | -87.4505 | -88.6163 | -102.2532 | -121.441 | -173.9223 | -195.8805 | -213.0226
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | Steady Progression | Headroom (MW) | Thermal | 20.1427 | 19.9643 | 19.6626 | 19.4919 | 19.3477 | -6.2577 | -6.3229 | -6.4042 | -6.4236 | -6.5048 | -6.5895 | -6.6289 | -6.6692 | -6.6797 | -6.6532 | -6.5276 | -6.4485 | -20.7627 | -23.5985
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | System Transformation | Headroom (MW) | Thermal | 20.1288 | 19.9591 | 19.6055 | -6.0743 | -6.2921 | -6.5494 | -6.7456 | -6.9674 | -7.142 | -7.3766 | -7.5841 | -7.728 | -7.8542 | -7.9303 | -40.214 | -40.0659 | -58.9342 | -65.9423 | -78.9171
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | 52.4387 | -1.2763 | WPD Best View | Headroom (MW) | Thermal | 20.1286 | 19.9589 | 19.6051 | -6.0754 | -6.2936 | -6.5519 | -6.7397 | -6.9632 | -7.134 | -7.3765 | -7.5875 | -7.7366 | -7.8785 | -7.9546 | -40.2492 | -40.1128 | -57.3113 | -62.9808 | -74.1072
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Consumer Transformation | Headroom (MW) | Thermal | 15.9295 | 15.8172 | 15.6314 | 15.4654 | 15.2851 | 15.0299 | 14.7784 | 14.4808 | 14.2297 | 13.9 | 12.5838 | 12.256 | 11.9305 | 10.7043 | 10.4659 | 10.3228 | 5.7886 | -1.2266 | -7.4786
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Leading the Way | Headroom (MW) | Thermal | 15.9503 | 15.8823 | 15.7483 | 15.6573 | 15.5524 | 15.4065 | 15.3545 | 15.2246 | 15.1305 | 14.9263 | 14.6822 | 14.5873 | 13.5943 | 12.2754 | 12.2539 | 10.6586 | 5.7075 | -0.13826 | -5.7566
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | Steady Progression | Headroom (MW) | N/A | 15.9518 | 15.8779 | 15.7553 | 15.6831 | 15.6064 | 15.5416 | 15.5334 | 15.4899 | 15.5113 | 15.4676 | 15.4262 | 15.4023 | 15.3734 | 15.3534 | 15.3412 | 15.3875 | 15.4615 | 14.2482 | 13.9995
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | System Transformation | Headroom (MW) | N/A | 15.944 | 15.8686 | 15.724 | 15.6165 | 15.5086 | 15.3805 | 15.3191 | 15.2049 | 15.1531 | 15.0226 | 14.9122 | 14.8219 | 14.733 | 14.6572 | 14.5919 | 14.6414 | 12.275 | 9.3464 | 6.1044
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | 52.4554 | -1.2167 | WPD Best View | Headroom (MW) | N/A | 15.944 | 15.8686 | 15.724 | 15.6165 | 15.5086 | 15.3805 | 15.3191 | 15.2049 | 15.1531 | 15.0226 | 14.9122 | 14.8219 | 14.733 | 14.6572 | 14.5919 | 14.6414 | 12.275 | 9.3464 | 6.1044
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Consumer Transformation | Headroom (MW) | N/A | 14.1896 | 14.1647 | 14.1134 | 14.0916 | 14.065 | 14.0445 | 14.0768 | 14.1252 | 14.1578 | 14.2127 | 14.2457 | 13.3997 | 13.4522 | 13.5087 | 13.5993 | 13.7544 | 10.805 | 7.5121 | 3.8684
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Leading the Way | Headroom (MW) | Thermal | 14.1901 | 13.5298 | 13.4797 | 13.4605 | 13.4449 | 13.4354 | 13.5182 | 13.6291 | 13.7484 | 13.8961 | 14.0265 | 14.1772 | 14.3367 | 14.4835 | 12.0262 | 12.2395 | 8.5722 | 3.3719 | -0.49191
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | Steady Progression | Headroom (MW) | N/A | 14.188 | 14.1605 | 14.1042 | 14.0758 | 14.0491 | 14.0241 | 14.0422 | 14.0652 | 14.0915 | 14.1157 | 14.143 | 14.1754 | 14.202 | 14.2409 | 14.2832 | 14.3647 | 14.2732 | 14.5277 | 13.7853
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | System Transformation | Headroom (MW) | N/A | 14.1882 | 14.1607 | 14.1045 | 14.0769 | 14.0505 | 14.0265 | 14.0634 | 14.1157 | 14.1653 | 14.2215 | 14.2784 | 14.3452 | 14.4177 | 14.4851 | 14.5675 | 14.7161 | 12.9226 | 11.8747 | 10.3845
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | 52.4492 | -1.2506 | WPD Best View | Headroom (MW) | N/A | 14.188 | 14.1608 | 14.1045 | 14.0767 | 14.0502 | 14.026 | 14.0719 | 14.1236 | 14.1788 | 14.2294 | 14.2856 | 14.3514 | 14.4135 | 14.4873 | 14.5664 | 14.7109 | 14.6231 | 14.8635 | 13.9111
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Consumer Transformation | Headroom (MW) | Thermal | 14.4127 | 14.3151 | 14.1204 | 13.9812 | 13.8596 | 13.6626 | 13.387 | 13.1374 | 12.9067 | 12.7053 | 12.4775 | 12.2727 | 11.1707 | 10.9935 | 10.8548 | 10.6728 | 4.9103 | -1.4394 | -10.8092
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Leading the Way | Headroom (MW) | Thermal | 14.4474 | 14.3918 | 14.2564 | 14.2033 | 14.1712 | 14.1211 | 14.0458 | 13.9953 | 13.9843 | 13.9855 | 13.9632 | 13.9638 | 13.9685 | 13.9749 | 10.5962 | 7.1445 | 2.9918 | -7.9203 | -15.5802
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | Steady Progression | Headroom (MW) | N/A | 14.4348 | 14.3577 | 14.2351 | 14.1648 | 14.1241 | 14.0692 | 13.994 | 13.9333 | 13.8662 | 13.8045 | 13.7339 | 13.6861 | 13.6481 | 13.6186 | 13.6151 | 13.6128 | 13.7094 | 12.462 | 10.6173
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | System Transformation | Headroom (MW) | Thermal | 14.4285 | 14.3617 | 14.2089 | 14.1249 | 14.0413 | 13.9361 | 13.7645 | 13.6045 | 13.4322 | 13.2719 | 13.1179 | 12.9975 | 12.8876 | 12.8201 | 12.7694 | 12.7194 | 10.119 | 7.0874 | -1.1551
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | 52.5363 | -1.2548 | WPD Best View | Headroom (MW) | N/A | 14.4285 | 14.3614 | 14.2085 | 14.1241 | 14.0402 | 13.9342 | 13.7619 | 13.6008 | 13.4267 | 13.264 | 13.1072 | 12.9827 | 12.8676 | 12.7936 | 12.7353 | 12.6778 | 10.0414 | 7.0601 | 0.12813
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Consumer Transformation | Headroom (MW) | Thermal | 59.89 | 59.8773 | 58.1513 | 57.985 | 57.7866 | 57.4589 | 55.8384 | 55.0596 | 54.2583 | 53.3795 | 51.5346 | 50.6651 | 20.4813 | 19.6509 | 13.2867 | 1.3619 | -7.776 | -21.0569 | -31.931
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Leading the Way | Headroom (MW) | Thermal | 59.9097 | 59.8894 | 58.3508 | 58.2363 | 57.2862 | 57.1983 | 56.7299 | 37.9081 | 26.7992 | 16.3379 | 13.6199 | 13.158 | 12.7193 | 10.0586 | 5.0875 | -0.32899 | -9.3912 | -22.2317 | -30.83
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | Steady Progression | Headroom (MW) | N/A | 59.8752 | 59.8267 | 59.6514 | 59.5738 | 59.508 | 59.4558 | 59.3334 | 59.2747 | 59.202 | 59.1133 | 59.0043 | 57.1745 | 57.0378 | 56.9094 | 56.7851 | 56.6893 | 56.0053 | 51.3383 | 49.9184
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | System Transformation | Headroom (MW) | Thermal | 59.8898 | 59.8766 | 58.2525 | 58.1562 | 58.0458 | 57.9552 | 56.7942 | 56.6213 | 56.3129 | 55.9792 | 55.5423 | 55.1232 | 25.4325 | 25.11 | 24.8119 | 14.3822 | 8.2589 | 1.5062 | -4.7402
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | 52.3882 | -1.2617 | WPD Best View | Headroom (MW) | N/A | 59.8752 | 59.8268 | 59.6515 | 59.5829 | 59.5179 | 59.4659 | 59.3983 | 59.3399 | 59.2862 | 59.1986 | 59.0773 | 57.2413 | 57.113 | 56.9891 | 56.8709 | 56.7834 | 53.4338 | 51.0068 | 47.1461
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Consumer Transformation | Headroom (MW) | Thermal | 14.4028 | 14.3875 | 14.3094 | 14.2803 | 14.2457 | 14.1243 | 13.8456 | 13.5695 | 13.2912 | 13.0112 | 12.7417 | 12.5037 | 12.2711 | 12.0617 | 11.8633 | 11.6758 | 8.4443 | 4.1953 | -1.004
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Leading the Way | Headroom (MW) | Thermal | 14.4136 | 14.3902 | 14.3156 | 14.2684 | 14.2394 | 14.2072 | 14.0035 | 13.9764 | 13.8908 | 13.8739 | 11.4952 | 11.4174 | 11.3753 | 11.3425 | 11.2887 | 7.8403 | 4.4124 | -1.2968 | -4.0252
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | Steady Progression | Headroom (MW) | N/A | 14.3947 | 14.3713 | 14.2896 | 14.2532 | 14.2163 | 14.1787 | 14.124 | 14.0882 | 14.0472 | 14.0141 | 13.974 | 13.9406 | 13.9046 | 13.8735 | 13.8434 | 13.8324 | 13.6798 | 13.4637 | 12.9815
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | System Transformation | Headroom (MW) | N/A | 14.4027 | 14.3872 | 14.3085 | 14.2789 | 14.2432 | 14.2082 | 14.1675 | 14.1169 | 13.9582 | 13.8115 | 13.6801 | 13.5594 | 13.4621 | 13.3936 | 13.3296 | 13.3005 | 13.2102 | 10.2189 | 6.8378
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | 52.3668 | -1.2204 | WPD Best View | Headroom (MW) | N/A | 14.3947 | 14.3713 | 14.2896 | 14.2564 | 14.2203 | 14.1828 | 14.1466 | 14.111 | 14.0768 | 14.0445 | 14.0119 | 13.9802 | 13.9498 | 13.9223 | 13.8972 | 13.8928 | 13.8141 | 12.9555 | 9.7752
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Consumer Transformation | Headroom (MW) | Thermal | 14.6603 | 14.7082 | 13.1566 | 13.07 | 12.9557 | 12.798 | 11.5404 | 11.2954 | 11.0327 | 10.6968 | 9.3956 | 9.0151 | 8.6329 | 8.2457 | 7.8842 | 6.596 | 2.2511 | -4.0371 | -7.9149
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Leading the Way | Headroom (MW) | Thermal | 14.6672 | 14.7279 | 13.3588 | 13.3586 | 12.4856 | 12.4763 | 12.3811 | 12.3023 | 12.1814 | 11.959 | 11.7131 | 11.4751 | 11.234 | 8.7782 | 8.5162 | 6.5646 | 1.4229 | -4.644 | -8.2655
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | Steady Progression | Headroom (MW) | N/A | 14.6551 | 14.6771 | 14.6812 | 14.6944 | 14.7168 | 14.7529 | 14.7497 | 14.7768 | 14.799 | 14.7915 | 14.7746 | 13.0242 | 12.9705 | 12.9165 | 12.8638 | 12.8186 | 12.4854 | 11.0508 | 10.5544
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | System Transformation | Headroom (MW) | N/A | 14.6603 | 14.7082 | 13.2592 | 13.2434 | 13.2189 | 13.2128 | 12.1464 | 12.0734 | 11.9741 | 11.8338 | 11.6719 | 11.5244 | 11.3787 | 11.2439 | 11.1059 | 10.9865 | 8.0825 | 4.8854 | 2.8707
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | 52.3753 | -1.2882 | WPD Best View | Headroom (MW) | N/A | 14.6551 | 14.6771 | 14.6812 | 14.6979 | 14.7204 | 14.7564 | 14.7752 | 14.8024 | 14.8319 | 14.8245 | 14.7828 | 13.0242 | 12.9705 | 12.9165 | 12.8638 | 12.8186 | 12.4854 | 11.0508 | 10.5544
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Consumer Transformation | Headroom (MW) | N/A | 14.3357 | 14.2903 | 14.1941 | 14.1435 | 14.0939 | 14.0454 | 13.9612 | 13.7034 | 13.4431 | 13.1802 | 12.906 | 12.655 | 12.4083 | 12.1744 | 11.9372 | 11.6722 | 10.1108 | 7.3672 | 5.5701
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Leading the Way | Headroom (MW) | N/A | 14.3377 | 14.2801 | 14.1852 | 14.118 | 14.0701 | 14.0235 | 13.8541 | 13.8093 | 13.7278 | 13.6901 | 13.5967 | 13.4506 | 13.2951 | 13.1229 | 13.1068 | 13.0902 | 12.5976 | 11.5332 | 9.2848
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | Steady Progression | Headroom (MW) | N/A | 14.3342 | 14.2871 | 14.1894 | 14.135 | 14.0836 | 14.033 | 13.9686 | 13.9185 | 13.8646 | 13.8165 | 13.7646 | 13.7185 | 13.6714 | 13.6282 | 13.5867 | 13.5471 | 13.3489 | 13.116 | 12.6748
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | System Transformation | Headroom (MW) | N/A | 14.3356 | 14.2901 | 14.1936 | 14.1426 | 14.0924 | 14.0429 | 13.9891 | 13.9398 | 13.8894 | 13.8427 | 13.6991 | 13.5481 | 13.4228 | 13.3035 | 13.2074 | 13.1106 | 12.765 | 12.2006 | 11.3501
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | 52.3689 | -1.2657 | WPD Best View | Headroom (MW) | N/A | 14.3342 | 14.2871 | 14.1894 | 14.1374 | 14.086 | 14.0354 | 13.9853 | 13.9353 | 13.8863 | 13.8383 | 13.7914 | 13.7457 | 13.7015 | 13.6591 | 13.6187 | 13.5807 | 13.4266 | 13.2927 | 13.1087
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Consumer Transformation | Headroom (MW) | N/A | 58.8037 | 58.5812 | 58.3481 | 58.3814 | 58.4275 | 58.4098 | 58.2822 | 58.1159 | 57.6014 | 57.1152 | 56.2284 | 55.3298 | 54.6749 | 53.8166 | 53.0068 | 52.0838 | 46.4636 | 44.1428 | 48.8666
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Leading the Way | Headroom (MW) | N/A | 58.8532 | 58.586 | 58.4517 | 58.5436 | 58.7056 | 58.8464 | 58.0036 | 58.1521 | 57.9189 | 57.8449 | 63.5978 | 62.9462 | 75.7441 | 74.9555 | 74.8808 | 74.1391 | 73.0255 | 68.7441 | 62.1553
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | Steady Progression | Headroom (MW) | N/A | 58.7685 | 58.541 | 58.2347 | 58.188 | 58.1482 | 58.1123 | 58.0365 | 57.9911 | 57.8393 | 57.7023 | 57.5525 | 57.4001 | 57.3149 | 57.1683 | 57.0272 | 56.8881 | 56.5507 | 55.9272 | 54.069
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | System Transformation | Headroom (MW) | N/A | 58.8027 | 58.5797 | 58.3402 | 58.3767 | 58.4083 | 58.4187 | 58.4796 | 58.5158 | 58.3339 | 58.1734 | 64.0858 | 63.9031 | 77.2471 | 77.0352 | 76.8434 | 76.648 | 76.7729 | 74.5467 | 71.1034
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | 52.3934 | -1.4827 | WPD Best View | Headroom (MW) | N/A | 58.8035 | 58.5837 | 58.3529 | 58.3997 | 58.4467 | 58.445 | 58.4762 | 58.3099 | 57.8407 | 57.3002 | 56.2334 | 55.3095 | 54.6212 | 53.7469 | 52.9014 | 51.9647 | 47.4628 | 46.6925 | 52.9076
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Consumer Transformation | Headroom (MW) | N/A | 16.6435 | 16.5963 | 16.4993 | 16.4463 | 16.3977 | 16.3469 | 16.2572 | 16.0703 | 15.8607 | 15.6715 | 15.4808 | 15.3174 | 15.1748 | 15.0278 | 14.878 | 14.7059 | 13.5474 | 11.9533 | 10.2605
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Leading the Way | Headroom (MW) | N/A | 16.6441 | 16.5792 | 16.4823 | 16.407 | 16.36 | 16.3097 | 16.1315 | 16.085 | 16.006 | 15.9682 | 15.8894 | 15.7582 | 15.6201 | 15.4679 | 15.4548 | 15.4406 | 15.0191 | 14.5113 | 13.399
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | Steady Progression | Headroom (MW) | N/A | 16.643 | 16.5949 | 16.4975 | 16.441 | 16.3907 | 16.3387 | 16.2696 | 16.2192 | 16.1651 | 16.1167 | 16.0635 | 16.0171 | 15.969 | 15.9252 | 15.8828 | 15.8423 | 15.6389 | 15.4079 | 14.9662
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | System Transformation | Headroom (MW) | N/A | 16.6434 | 16.5961 | 16.4988 | 16.4453 | 16.396 | 16.3441 | 16.2871 | 16.2368 | 16.1872 | 16.115 | 15.9581 | 15.8392 | 15.7277 | 15.6434 | 15.5791 | 15.5121 | 15.3431 | 14.8612 | 14.0181
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | 52.403 | -1.4642 | WPD Best View | Headroom (MW) | N/A | 16.6431 | 16.5951 | 16.498 | 16.4447 | 16.3957 | 16.3443 | 16.2939 | 16.1095 | 15.897 | 15.6994 | 15.5049 | 15.3285 | 15.158 | 15.0017 | 14.8388 | 14.6696 | 13.6477 | 12.3453 | 10.8378
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Consumer Transformation | Headroom (MW) | N/A | 15.7907 | 15.7306 | 15.6132 | 15.6015 | 15.6504 | 15.6944 | 15.6932 | 15.7089 | 15.6439 | 15.6297 | 15.3571 | 15.0832 | 14.7964 | 14.5517 | 14.3251 | 14.0979 | 12.9016 | 11.1859 | 9.1388
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Leading the Way | Headroom (MW) | N/A | 15.7926 | 15.7204 | 15.6048 | 15.5965 | 15.6867 | 15.7692 | 15.5314 | 15.5832 | 15.5284 | 15.5322 | 15.3447 | 15.1227 | 14.8674 | 14.5772 | 14.5565 | 14.5285 | 13.8067 | 13.6611 | 12.1537
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | Steady Progression | Headroom (MW) | N/A | 15.7893 | 15.7284 | 15.6092 | 15.5798 | 15.5968 | 15.6106 | 15.5976 | 15.588 | 15.5513 | 15.52 | 15.4831 | 15.4506 | 15.4164 | 15.3827 | 15.3521 | 15.3217 | 15.2009 | 14.9714 | 14.4584
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | System Transformation | Headroom (MW) | N/A | 15.7907 | 15.7303 | 15.6125 | 15.6003 | 15.6484 | 15.6911 | 15.7227 | 15.7355 | 15.7068 | 15.6866 | 15.6675 | 15.6505 | 15.6274 | 15.597 | 15.5754 | 15.5563 | 15.4672 | 15.1583 | 13.9461
Coventry 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | 52.3885 | -1.5066 | WPD Best View | Headroom (MW) | N/A | 15.7907 | 15.7306 | 15.6132 | 15.6015 | 15.6504 | 15.6944 | 15.7328 | 15.7486 | 15.7269 | 15.6858 | 15.3571 | 15.0832 | 14.7964 | 14.5517 | 14.3251 | 14.0979 | 12.9016 | 11.1859 | 9.1388
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Consumer Transformation | Headroom (MW) | N/A | 13.9938 | 13.9706 | 13.9224 | 13.8981 | 13.8728 | 13.847 | 13.8124 | 13.7877 | 13.671 | 13.4841 | 13.2965 | 13.1209 | 12.9538 | 12.7761 | 12.6051 | 12.4071 | 11.2853 | 9.9299 | 8.5276
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Leading the Way | Headroom (MW) | N/A | 13.9999 | 13.9742 | 13.926 | 13.8991 | 13.8736 | 13.8473 | 13.7995 | 13.7747 | 13.7444 | 13.7228 | 13.6945 | 13.6533 | 13.6075 | 13.5534 | 13.5439 | 13.534 | 13.2438 | 12.4075 | 11.4863
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | Steady Progression | Headroom (MW) | N/A | 13.9893 | 13.9661 | 13.9182 | 13.8933 | 13.8675 | 13.8407 | 13.8129 | 13.7877 | 13.7615 | 13.7364 | 13.7108 | 13.6868 | 13.6627 | 13.6398 | 13.6174 | 13.5958 | 13.4983 | 13.3985 | 13.213
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | System Transformation | Headroom (MW) | N/A | 13.9938 | 13.9706 | 13.9223 | 13.898 | 13.8724 | 13.8465 | 13.8204 | 13.795 | 13.7689 | 13.744 | 13.7197 | 13.6961 | 13.6729 | 13.6259 | 13.5507 | 13.4726 | 13.1623 | 12.7103 | 12.0903
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4077 | -1.491 | WPD Best View | Headroom (MW) | N/A | 13.9938 | 13.9706 | 13.9224 | 13.8981 | 13.8728 | 13.847 | 13.8225 | 13.7978 | 13.671 | 13.4841 | 13.2965 | 13.1209 | 12.9538 | 12.7761 | 12.6051 | 12.4071 | 11.2853 | 9.9299 | 8.5276
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Consumer Transformation | Headroom (MW) | N/A | 12.4524 | 12.4461 | 12.4299 | 12.4244 | 12.4157 | 12.3681 | 12.2816 | 12.193 | 12.1092 | 12.0181 | 11.9152 | 11.8489 | 12.0036 | 11.9496 | 11.9026 | 11.8389 | 11.3831 | 10.7626 | 10.0279
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Leading the Way | Headroom (MW) | N/A | 12.4607 | 12.4527 | 12.4363 | 12.4295 | 12.4201 | 12.4106 | 12.2112 | 12.2058 | 12.1943 | 12.1924 | 12.1776 | 12.1409 | 12.28 | 12.2537 | 12.2702 | 12.286 | 12.1547 | 11.7505 | 11.1506
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | Steady Progression | Headroom (MW) | N/A | 12.4461 | 12.4398 | 12.4239 | 12.4176 | 12.4085 | 12.3984 | 12.3888 | 12.3816 | 12.3736 | 12.3664 | 12.3592 | 12.3518 | 12.4217 | 12.4217 | 12.4221 | 12.423 | 12.4003 | 12.404 | 12.343
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | System Transformation | Headroom (MW) | N/A | 12.4524 | 12.446 | 12.4297 | 12.424 | 12.4151 | 12.4062 | 12.3982 | 12.3917 | 12.3412 | 12.3051 | 12.2763 | 12.241 | 12.4461 | 12.4376 | 12.4418 | 12.4353 | 12.4237 | 12.2673 | 11.8986
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | 52.4032 | -1.5015 | WPD Best View | Headroom (MW) | N/A | 12.4524 | 12.4461 | 12.4299 | 12.4244 | 12.4157 | 12.3681 | 12.2816 | 12.193 | 12.1092 | 12.0181 | 11.9152 | 11.8489 | 12.0036 | 11.9496 | 11.9026 | 11.8389 | 11.3831 | 10.7626 | 10.0279
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Consumer Transformation | Headroom (MW) | N/A | 10.9666 | 10.9414 | 10.8807 | 10.8436 | 10.9789 | 11.1047 | 11.2148 | 11.348 | 11.3803 | 11.4114 | 11.4083 | 11.4327 | 11.4467 | 11.4472 | 11.4687 | 11.4979 | 10.7991 | 9.2674 | 8.8217
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Leading the Way | Headroom (MW) | N/A | 10.9713 | 10.9547 | 10.9018 | 10.8879 | 11.091 | 11.2949 | 11.4223 | 11.601 | 11.6189 | 11.6588 | 11.683 | 11.6586 | 11.6333 | 11.5935 | 11.5953 | 10.5924 | 10.6692 | 9.1761 | 8.8201
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | Steady Progression | Headroom (MW) | N/A | 10.2451 | 10.2421 | 10.2405 | 10.2393 | 10.2384 | 10.2375 | 10.2356 | 10.2334 | 10.2307 | 10.2216 | 10.2164 | 10.2131 | 10.2103 | 10.2078 | 10.2058 | 10.1977 | 10.1181 | 9.9745 | 9.7859
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | System Transformation | Headroom (MW) | N/A | 10.9659 | 10.9407 | 10.8748 | 10.8422 | 10.9656 | 11.0839 | 11.1914 | 11.3139 | 11.3215 | 11.3548 | 11.3823 | 11.4387 | 11.4531 | 11.4538 | 11.46 | 11.477 | 11.7697 | 10.6562 | 11.7129
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | 52.3675 | -1.4483 | WPD Best View | Headroom (MW) | N/A | 10.9668 | 10.9451 | 10.887 | 10.8638 | 11.0006 | 11.1432 | 11.2773 | 11.4086 | 11.4133 | 11.4268 | 11.4395 | 11.4648 | 11.4876 | 11.496 | 11.5088 | 11.5294 | 11.7861 | 11.5483 | 12.1313
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Consumer Transformation | Headroom (MW) | N/A | 19.7855 | 19.7251 | 19.8314 | 19.9965 | 19.9408 | 19.8775 | 19.8519 | 19.837 | 19.7653 | 19.7292 | 19.5996 | 19.3555 | 19.1284 | 18.8931 | 18.6562 | 18.3651 | 17.3762 | 21.6029 | 19.59
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Leading the Way | Headroom (MW) | N/A | 19.8134 | 19.7338 | 19.9294 | 20.1525 | 20.1032 | 20.0436 | 19.7367 | 19.7314 | 19.6559 | 19.5995 | 25.6374 | 25.4413 | 25.2359 | 25.0099 | 24.9601 | 24.9102 | 25.2143 | 24.7375 | 22.6458
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | Steady Progression | Headroom (MW) | N/A | 19.7646 | 19.702 | 19.7402 | 19.8412 | 19.7852 | 19.7361 | 19.7159 | 19.6816 | 19.6359 | 19.5937 | 19.5465 | 19.5062 | 19.4591 | 19.4159 | 19.3716 | 19.3247 | 19.4484 | 19.3701 | 18.9134
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | System Transformation | Headroom (MW) | N/A | 19.7854 | 19.7249 | 19.831 | 19.9958 | 19.9397 | 19.8757 | 19.8887 | 19.8717 | 19.8373 | 19.7968 | 25.9109 | 25.8665 | 25.8201 | 25.7775 | 25.7364 | 25.6946 | 26.1069 | 25.8402 | 24.9375
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | 52.3933 | -1.4832 | WPD Best View | Headroom (MW) | N/A | 19.7855 | 19.725 | 19.8313 | 19.9962 | 19.9403 | 19.8768 | 19.897 | 19.8814 | 19.8522 | 19.8148 | 19.5492 | 19.292 | 19.0507 | 18.8007 | 18.55 | 18.2508 | 17.288 | 21.6379 | 19.6931
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Consumer Transformation | Headroom (MW) | N/A | 46.683 | 46.4029 | 45.9036 | 45.4326 | 44.9398 | 44.2266 | 43.2224 | 42.2183 | 41.2225 | 40.1707 | 39.0392 | 37.9455 | 36.9157 | 35.8878 | 34.8675 | 33.7673 | 27.3946 | 20.7042 | 14.3623
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Leading the Way | Headroom (MW) | N/A | 46.7466 | 46.6017 | 46.2808 | 46.0615 | 45.8058 | 45.517 | 45.0543 | 44.5953 | 44.0559 | 43.6109 | 43.0907 | 42.6382 | 42.2119 | 41.9455 | 41.5948 | 39.5243 | 36.3197 | 31.9902 | 28.4379
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | Steady Progression | Headroom (MW) | N/A | 46.7606 | 46.6062 | 46.3208 | 46.1548 | 45.9869 | 45.826 | 45.6506 | 45.4633 | 45.2549 | 45.0295 | 44.7847 | 44.5674 | 44.3578 | 44.1658 | 43.987 | 43.7902 | 43.2438 | 42.7873 | 41.733
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | System Transformation | Headroom (MW) | N/A | 46.7378 | 46.5628 | 46.2109 | 45.9452 | 45.6425 | 45.3118 | 44.7865 | 44.2702 | 43.6792 | 43.1089 | 42.5219 | 41.9924 | 41.4827 | 40.9997 | 40.5344 | 40.0463 | 38.1028 | 34.9405 | 32.0261
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | 52.8163 | -1.6235 | WPD Best View | Headroom (MW) | N/A | 46.7388 | 46.5649 | 46.2167 | 45.9544 | 45.6583 | 45.3347 | 44.8195 | 44.3072 | 43.7342 | 43.1859 | 42.6246 | 42.1158 | 41.6416 | 41.1816 | 40.7326 | 40.2386 | 38.1159 | 34.77 | 31.7687
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Consumer Transformation | Headroom (MW) | Thermal | 39.2052 | 39.7534 | 39.1737 | 38.6113 | 38.0359 | 37.2785 | 36.2132 | 35.1726 | 34.1942 | 27.0572 | 25.986 | 24.1171 | 22.3098 | 21.3702 | 20.4607 | 19.409 | 8.7186 | -6.6725 | -22.536
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Leading the Way | Headroom (MW) | Thermal | 39.2753 | 40.203 | 39.8428 | 39.5543 | 39.318 | 39.0666 | 38.6502 | 38.31 | 37.9741 | 31.6919 | 31.5063 | 31.3325 | 31.1538 | 29.6846 | 26.919 | 22.5809 | 11.6152 | -1.6848 | -12.7659
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | Steady Progression | Headroom (MW) | N/A | 39.2826 | 39.702 | 39.3778 | 34.0676 | 27.7884 | 27.6468 | 27.4877 | 26.2927 | 26.0896 | 25.8716 | 24.9358 | 24.1107 | 23.9522 | 23.8026 | 23.7095 | 23.5879 | 23.3866 | 22.0885 | 19.2418
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | System Transformation | Headroom (MW) | N/A | 39.2624 | 39.8833 | 39.5087 | 39.2129 | 38.8616 | 38.5299 | 37.9911 | 37.4319 | 30.3458 | 29.7323 | 29.1111 | 28.6061 | 28.1591 | 27.7391 | 27.3523 | 26.9717 | 22.8528 | 13.2889 | 4.7012
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | 52.8172 | -1.6229 | WPD Best View | Headroom (MW) | Thermal | 39.2191 | 39.7662 | 39.2252 | 38.7044 | 38.1654 | 37.4582 | 36.4724 | 35.51 | 34.5639 | 27.4722 | 26.4439 | 24.6151 | 22.8429 | 21.9526 | 21.118 | 20.1996 | 10.5291 | -3.7745 | -18.7477
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Consumer Transformation | Headroom (MW) | Thermal | 8.9475 | 8.9173 | 8.8035 | 8.6543 | 8.5116 | 8.3084 | 8.0023 | 7.7216 | 7.453 | 7.1896 | 6.894 | 6.6493 | 5.4806 | 5.217 | 4.9578 | 4.6596 | 1.8835 | -2.3846 | -5.3367
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Leading the Way | Headroom (MW) | Thermal | 8.9476 | 8.9009 | 8.8418 | 8.7888 | 8.7575 | 8.727 | 8.5648 | 8.5369 | 8.469 | 8.4468 | 8.3715 | 8.2415 | 8.1055 | 7.9479 | 7.9446 | 5.5209 | 4.8843 | 1.7128 | -0.34656
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | Steady Progression | Headroom (MW) | N/A | 8.9474 | 8.917 | 8.8574 | 3.6953 | 3.663 | 3.6312 | 3.5834 | 2.5112 | 2.456 | 2.3869 | 1.6046 | 0.90712 | 0.8654 | 0.81559 | 0.78588 | 0.74923 | 0.64058 | 0.58448 | 0.16268
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | System Transformation | Headroom (MW) | N/A | 8.9475 | 8.9172 | 8.8578 | 8.8144 | 8.7241 | 8.6072 | 8.4459 | 8.2869 | 8.1029 | 7.9423 | 7.769 | 7.6212 | 7.4971 | 7.3716 | 7.2637 | 7.1386 | 6.635 | 4.7263 | 3.1226
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | 52.7931 | -1.5749 | WPD Best View | Headroom (MW) | Thermal | 8.9475 | 8.9173 | 8.8131 | 8.6843 | 8.5465 | 8.3483 | 8.0725 | 7.8158 | 7.5479 | 7.3044 | 7.026 | 6.7837 | 5.6293 | 5.378 | 5.139 | 4.8845 | 2.4202 | -1.4859 | -4.1424
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Consumer Transformation | Headroom (MW) | Thermal | 24.2581 | 24.76 | 24.4989 | 24.2897 | 24.0589 | 23.8084 | 23.4493 | 23.0894 | 22.7466 | 16.2442 | 15.8702 | 15.5526 | 15.251 | 14.9357 | 14.6133 | 14.2502 | 10.8336 | 4.5441 | -2.6079
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Leading the Way | Headroom (MW) | Thermal | 24.2916 | 25.0784 | 24.9009 | 24.772 | 24.6683 | 24.5726 | 24.4838 | 24.3372 | 24.2101 | 18.0155 | 17.971 | 17.958 | 17.9526 | 16.6719 | 16.596 | 14.7876 | 8.8827 | 2.5242 | -1.5176
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | Steady Progression | Headroom (MW) | N/A | 24.2896 | 24.6729 | 24.5115 | 24.424 | 18.2262 | 18.1645 | 18.1195 | 18.0496 | 17.9683 | 17.8865 | 17.8045 | 17.7369 | 17.6722 | 17.6218 | 17.5858 | 17.5363 | 17.4382 | 16.1597 | 15.5307
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | System Transformation | Headroom (MW) | N/A | 24.284 | 24.8254 | 24.6415 | 24.5037 | 24.3671 | 24.2746 | 24.0941 | 23.8935 | 17.214 | 16.9811 | 16.7484 | 16.5688 | 16.4086 | 16.2605 | 16.1103 | 15.9775 | 14.1205 | 9.4476 | 4.6499
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | 52.8638 | -1.6816 | WPD Best View | Headroom (MW) | Thermal | 24.2725 | 24.774 | 24.543 | 24.3549 | 24.1563 | 23.9526 | 23.6478 | 23.3402 | 23.0377 | 16.5708 | 16.2353 | 15.9603 | 15.7006 | 15.4328 | 15.1699 | 14.8853 | 12.0442 | 6.3368 | -0.30103
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Consumer Transformation | Headroom (MW) | N/A | 5.3551 | 5.3342 | 5.2896 | 5.2425 | 5.2051 | 5.1375 | 5.044 | 4.9491 | 4.8775 | 4.8023 | 4.7258 | 4.6638 | 4.6138 | 4.5572 | 4.5049 | 4.4368 | 2.706 | 2.0979 | 0.1892
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Leading the Way | Headroom (MW) | Thermal | 5.37 | 5.3523 | 5.3328 | 5.3164 | 5.3054 | 5.292 | 5.262 | 5.2297 | 5.2251 | 5.238 | 5.2527 | 5.2768 | 5.3044 | 5.3341 | 3.6447 | 3.6476 | 1.2231 | 0.63416 | -2.3325
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | Steady Progression | Headroom (MW) | N/A | 5.3696 | 5.3489 | 5.3267 | 5.3147 | 5.3036 | 5.2937 | 5.2758 | 5.2656 | 5.2472 | 5.2408 | 5.22 | 5.2154 | 5.2093 | 5.2037 | 5.2152 | 5.2144 | 5.2958 | 5.3585 | 3.9689
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | System Transformation | Headroom (MW) | N/A | 5.3678 | 5.3449 | 5.3177 | 5.2894 | 5.2594 | 5.2272 | 5.1803 | 5.1302 | 5.0816 | 5.0295 | 4.9805 | 4.9443 | 4.9166 | 4.8933 | 4.8798 | 4.8745 | 3.5824 | 3.4266 | 1.9151
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | 52.8502 | -1.5644 | WPD Best View | Headroom (MW) | N/A | 5.3551 | 5.3342 | 5.2896 | 5.2425 | 5.2051 | 5.1375 | 5.044 | 4.9491 | 4.8775 | 4.8023 | 4.7258 | 4.6638 | 4.6138 | 4.5572 | 4.5049 | 4.4368 | 2.706 | 2.0979 | 0.1892
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Consumer Transformation | Headroom (MW) | Thermal | 9.7842 | 9.8815 | 9.7214 | 9.5645 | 9.3999 | 9.1639 | 8.8572 | 8.5521 | 8.2568 | 7.9608 | 7.6356 | 6.3911 | 6.104 | 5.8 | 5.5244 | 5.2021 | 2.4352 | -1.7903 | -5.6409
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Leading the Way | Headroom (MW) | N/A | 9.8059 | 10.0111 | 9.9069 | 9.8168 | 9.7265 | 9.6147 | 9.4793 | 9.3457 | 9.2097 | 9.1313 | 9.0507 | 8.9959 | 8.931 | 8.8704 | 7.8733 | 7.7645 | 5.7648 | 2.5838 | 0.57035
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | Steady Progression | Headroom (MW) | N/A | 9.8156 | 9.9029 | 9.8218 | 9.7733 | 9.7351 | 9.697 | 9.6486 | 9.6059 | 9.5578 | 9.4969 | 9.4463 | 9.3909 | 9.345 | 9.3012 | 9.2623 | 9.2276 | 9.1517 | 9.1255 | 8.7193
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | System Transformation | Headroom (MW) | N/A | 9.8028 | 9.9355 | 9.8314 | 9.7451 | 9.6507 | 9.5605 | 9.4105 | 9.261 | 9.0869 | 8.9191 | 8.7528 | 8.6115 | 8.4765 | 8.3533 | 8.2381 | 8.1207 | 7.6545 | 4.828 | 4.1533
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | 52.7737 | -1.5316 | WPD Best View | Headroom (MW) | Thermal | 9.7836 | 9.8804 | 9.7192 | 9.5625 | 9.3972 | 9.1595 | 8.8477 | 8.5446 | 8.2406 | 7.9344 | 7.5965 | 6.347 | 6.0389 | 5.7242 | 5.4437 | 5.1328 | 2.4984 | -1.5837 | -5.3538
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Consumer Transformation | Headroom (MW) | Thermal | 59.2055 | 59.1761 | 58.9195 | 36.2322 | 36.3807 | 35.9399 | 35.3488 | 34.6724 | 34.0104 | 33.1768 | 32.139 | 30.1618 | 29.075 | 28.1565 | 27.2681 | 26.3553 | 17.4024 | 7.2844 | -2.8077
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Leading the Way | Headroom (MW) | N/A | 59.2435 | 59.324 | 59.2325 | 41.1629 | 41.7042 | 41.7175 | 41.7827 | 41.5767 | 41.2733 | 40.8708 | 40.1707 | 39.4666 | 38.687 | 38.2622 | 33.5237 | 29.6882 | 24.1146 | 13.7298 | 4.0147
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | Steady Progression | Headroom (MW) | Thermal | 59.2186 | 59.187 | 58.964 | 31.423 | 31.6682 | 31.6489 | 28.6161 | 25.5464 | 22.4777 | 19.3475 | 17.2242 | 15.2756 | 13.0893 | 10.8912 | 9.9501 | 9.8084 | 6.9433 | 2.537 | -1.559
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | System Transformation | Headroom (MW) | N/A | 59.2161 | 59.2385 | 59.0625 | 40.8333 | 41.1574 | 41.1129 | 41.0691 | 40.8522 | 40.6006 | 40.2835 | 39.8653 | 39.4979 | 39.1062 | 38.7432 | 38.4111 | 38.0857 | 34.4665 | 28.6884 | 23.5414
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | 52.7725 | -1.6462 | WPD Best View | Headroom (MW) | N/A | 69.4697 | 69.4926 | 69.3202 | 51.0926 | 51.4205 | 51.379 | 50.3066 | 49.0713 | 47.8131 | 46.4739 | 45.3487 | 44.3406 | 42.9283 | 41.5432 | 40.8014 | 40.448 | 35.1002 | 27.1461 | 21.9424
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Consumer Transformation | Headroom (MW) | N/A | 13.6704 | 13.6664 | 13.5606 | 13.4892 | 13.415 | 13.3269 | 13.2054 | 13.095 | 13.0021 | 12.9203 | 12.8395 | 12.7882 | 12.7552 | 12.7107 | 12.6757 | 12.6133 | 9.7695 | 7.4462 | 4.0756
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Leading the Way | Headroom (MW) | N/A | 13.6773 | 13.7061 | 13.6377 | 13.5948 | 13.5581 | 13.5299 | 13.5033 | 13.4802 | 13.4707 | 13.5042 | 13.5366 | 13.5931 | 13.6587 | 13.7159 | 12.0505 | 10.3617 | 8.7893 | 4.5218 | 0.96013
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | Steady Progression | Headroom (MW) | N/A | 13.6765 | 13.6715 | 13.5802 | 13.5336 | 13.4932 | 13.4558 | 13.412 | 13.3762 | 13.3381 | 13.2998 | 13.2733 | 13.2511 | 13.2397 | 13.2306 | 13.2391 | 13.2455 | 13.36 | 13.4583 | 11.8536
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | System Transformation | Headroom (MW) | N/A | 13.6741 | 13.6736 | 13.5874 | 13.5241 | 13.4603 | 13.4027 | 13.3248 | 13.2465 | 13.1611 | 13.0916 | 13.0224 | 12.984 | 12.9592 | 12.9469 | 12.9368 | 12.9484 | 11.765 | 10.1965 | 8.3475
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | 52.7582 | -1.7045 | WPD Best View | Headroom (MW) | N/A | 13.6739 | 13.6736 | 13.5894 | 13.5265 | 13.4643 | 13.4076 | 13.3232 | 13.2478 | 13.1768 | 13.1061 | 13.0411 | 13.0119 | 12.9883 | 12.9772 | 12.9691 | 12.9597 | 11.5955 | 9.924 | 8.0116
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Consumer Transformation | Headroom (MW) | N/A | 18.0224 | 17.956 | 17.9 | 17.8301 | 17.687 | 17.3936 | 17.0014 | 16.6138 | 16.214 | 15.793 | 15.3497 | 14.907 | 14.4885 | 14.0649 | 13.6296 | 13.1947 | 10.9634 | 8.6401 | 6.4444
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Leading the Way | Headroom (MW) | N/A | 18.0225 | 17.9553 | 17.9271 | 17.8553 | 17.7871 | 17.7206 | 17.6318 | 17.4484 | 17.1857 | 16.9331 | 16.6721 | 16.4447 | 16.2244 | 16.01 | 15.7967 | 15.5584 | 14.4 | 13.1905 | 12.0638
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | Steady Progression | Headroom (MW) | N/A | 18.0224 | 17.9558 | 17.879 | 17.8084 | 17.7389 | 17.6732 | 17.6072 | 17.5441 | 17.48 | 17.4176 | 17.3552 | 17.2939 | 17.205 | 17.0946 | 16.9926 | 16.8835 | 16.4652 | 16.0413 | 15.4273
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | System Transformation | Headroom (MW) | N/A | 18.0224 | 17.9561 | 17.9001 | 17.8303 | 17.7613 | 17.6918 | 17.5855 | 17.3838 | 17.141 | 16.9062 | 16.6637 | 16.4408 | 16.2181 | 15.9993 | 15.7904 | 15.5755 | 14.6344 | 13.6458 | 12.7246
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | 52.8042 | -1.6321 | WPD Best View | Headroom (MW) | N/A | 18.0224 | 17.9561 | 17.9001 | 17.8303 | 17.7613 | 17.6918 | 17.5855 | 17.3838 | 17.141 | 16.9062 | 16.6637 | 16.4408 | 16.2181 | 15.9993 | 15.7904 | 15.5755 | 14.6344 | 13.6458 | 12.7246
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Consumer Transformation | Headroom (MW) | N/A | 25.5592 | 25.6002 | 25.5053 | 25.7722 | 26.138 | 26.0787 | 26.0014 | 25.823 | 25.6537 | 25.3229 | 24.8092 | 23.326 | 22.6907 | 22.2403 | 21.8222 | 21.4067 | 17.5288 | 12.0574 | 7.5316
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Leading the Way | Headroom (MW) | N/A | 25.5903 | 25.709 | 25.7141 | 26.2146 | 26.8609 | 26.9688 | 27.1495 | 27.1499 | 27.1187 | 26.9354 | 26.4638 | 25.9306 | 25.3057 | 25.0382 | 22.1783 | 20.27 | 17.4272 | 12.5192 | 7.4926
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | Steady Progression | Headroom (MW) | Thermal | 25.5661 | 25.6061 | 25.5513 | 16.583 | 16.938 | 17.0218 | 14.0988 | 11.128 | 8.1614 | 5.1319 | 3.0976 | 1.2324 | -0.85344 | -2.9321 | -3.7797 | -3.8187 | -6.38 | -10.4607 | -12.3381
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | System Transformation | Headroom (MW) | N/A | 25.566 | 25.6553 | 25.6214 | 25.9808 | 26.4377 | 26.5202 | 26.6605 | 26.7238 | 26.8004 | 26.7875 | 26.681 | 26.5749 | 26.4307 | 26.2989 | 26.1858 | 26.0636 | 24.5689 | 21.3479 | 18.9711
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | 52.8023 | -1.6527 | WPD Best View | Headroom (MW) | N/A | 25.5668 | 25.6563 | 25.6241 | 25.9846 | 26.4438 | 26.5284 | 25.6467 | 24.6886 | 23.7441 | 22.7105 | 21.8927 | 21.1368 | 19.9708 | 18.8155 | 18.2908 | 18.1616 | 15.1191 | 9.8251 | 7.4551
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Consumer Transformation | Headroom (MW) | Thermal | 32.109 | 32.2432 | 31.2787 | 30.4333 | 30.2784 | 29.1851 | 27.1932 | 25.2779 | 23.4838 | 21.5599 | 19.43 | 17.338 | 14.3725 | 12.2552 | 7.411 | 5.1501 | -14.0071 | -36.0517 | -59.9872
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Leading the Way | Headroom (MW) | Thermal | 32.2778 | 32.9135 | 32.3083 | 31.9939 | 32.6586 | 32.4907 | 31.6978 | 30.8775 | 30.0165 | 29.425 | 28.5388 | 27.6053 | 26.6788 | 25.8738 | 21.5586 | 16.1539 | -4.3173 | -19.793 | -33.5816
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | Steady Progression | Headroom (MW) | Thermal | 32.2435 | 32.4603 | 15.5157 | 15.3451 | 15.7215 | 15.6799 | 9.2727 | 0.79087 | -7.677 | -16.1612 | -21.3521 | -26.1445 | -26.4633 | -26.8118 | -27.1406 | -27.4553 | -28.7068 | -31.5659 | -34.2595
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | System Transformation | Headroom (MW) | Thermal | 32.2336 | 32.5665 | 31.9181 | 31.5715 | 31.809 | 31.4736 | 30.4575 | 29.4449 | 28.3914 | 27.3941 | 26.3074 | 25.2977 | 24.3854 | 23.4556 | 22.6182 | 21.7218 | 15.1752 | 5.724 | -7.5765
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | 52.7585 | -1.5897 | WPD Best View | Headroom (MW) | Thermal | 32.1627 | 32.368 | 31.5563 | 30.8801 | 30.8828 | 30.1389 | 26.5483 | 22.9888 | 19.486 | 15.9136 | 13.053 | 10.3607 | 8.8149 | 7.183 | 3.7449 | 2.0449 | -11.334 | -27.2319 | -43.841
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Consumer Transformation | Headroom (MW) | Thermal | 10.5794 | 10.5188 | 10.4245 | 10.3797 | 10.2965 | 10.4403 | 10.2303 | 10.0361 | 9.8315 | 9.6501 | 9.4213 | 9.197 | 8.9558 | 8.7482 | 7.6412 | 7.4622 | 5.4459 | 3.1899 | -1.3537
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Leading the Way | Headroom (MW) | N/A | 10.5987 | 10.56 | 10.5033 | 10.5174 | 10.4859 | 10.8007 | 10.6964 | 10.5811 | 10.4506 | 10.3467 | 10.2494 | 10.1107 | 9.9828 | 9.917 | 9.8832 | 9.8308 | 7.0063 | 3.9543 | 2.0404
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | Steady Progression | Headroom (MW) | N/A | 10.5885 | 10.5564 | 10.5009 | 10.5103 | 10.4839 | 10.6564 | 10.6256 | 10.6007 | 10.5867 | 10.5647 | 10.5401 | 10.5266 | 10.5123 | 10.4876 | 10.4744 | 10.4668 | 10.4976 | 10.554 | 10.2296
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | System Transformation | Headroom (MW) | N/A | 10.5905 | 10.5508 | 10.4896 | 10.4887 | 10.4586 | 10.6802 | 10.5913 | 10.4949 | 10.3994 | 10.3356 | 10.2673 | 10.1906 | 10.1254 | 10.0602 | 10.0118 | 9.9713 | 9.8153 | 9.4032 | 7.5442
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | 52.7584 | -1.4809 | WPD Best View | Headroom (MW) | N/A | 10.5915 | 10.5453 | 10.4955 | 10.4981 | 10.4652 | 10.6931 | 10.6037 | 10.5173 | 10.4175 | 10.3695 | 10.302 | 10.242 | 10.182 | 10.1237 | 10.0763 | 10.0352 | 8.7771 | 8.1719 | 5.2526
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Consumer Transformation | Headroom (MW) | Thermal | 24.086 | 24.2767 | 23.9856 | 23.7166 | 23.4236 | 23.0628 | 22.5098 | 21.9794 | 21.4655 | 20.8785 | 20.2597 | 19.6485 | 19.0687 | 18.4414 | 16.8642 | 16.145 | 10.8945 | 4.7902 | -1.2541
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Leading the Way | Headroom (MW) | N/A | 24.1351 | 24.5244 | 24.3395 | 24.2077 | 24.0611 | 23.9392 | 23.7589 | 23.5435 | 23.3072 | 23.1115 | 22.8553 | 22.5845 | 22.3102 | 22.0454 | 20.0149 | 17.9317 | 12.3788 | 7.8671 | 3.7584
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | Steady Progression | Headroom (MW) | Thermal | 24.1268 | 24.3035 | 15.942 | 15.8623 | 15.7886 | 15.7303 | 12.5786 | 8.3759 | 4.1747 | -0.025196 | -2.4054 | -4.5719 | -4.6624 | -4.7523 | -4.8502 | -4.9472 | -5.3793 | -6.877 | -7.6774
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | System Transformation | Headroom (MW) | N/A | 24.1234 | 24.3716 | 24.1847 | 24.0396 | 23.8624 | 23.7222 | 23.4568 | 23.1869 | 22.8723 | 22.5707 | 22.2483 | 21.9479 | 21.6853 | 21.4141 | 21.1544 | 20.8648 | 18.2937 | 15.6633 | 11.8989
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | 52.7583 | -1.5895 | WPD Best View | Headroom (MW) | Thermal | 24.0884 | 24.2825 | 24.0104 | 23.7479 | 23.4567 | 23.1203 | 21.5756 | 20.0397 | 18.5157 | 16.9249 | 15.7159 | 14.5707 | 13.9894 | 13.3729 | 11.8187 | 11.1462 | 6.3848 | 0.94978 | -3.2982
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Consumer Transformation | Headroom (MW) | Thermal | -2.6962 | -2.7631 | -2.8631 | -2.9549 | -2.8142 | -2.9374 | -3.099 | -3.2617 | -3.395 | -3.5173 | -3.6611 | -3.7998 | -3.9196 | -4.0591 | -4.1675 | -4.304 | -7.1172 | -9.6107 | -13.0724
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Leading the Way | Headroom (MW) | Thermal | -2.6769 | -2.7174 | -2.7939 | -2.835 | -2.5707 | -2.6106 | -2.682 | -2.7295 | -2.7642 | -2.7473 | -2.767 | -2.7934 | -2.7963 | -2.8124 | -2.8313 | -2.8556 | -6.7471 | -7.6375 | -7.3743
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | Steady Progression | Headroom (MW) | Thermal | -2.6804 | -2.7251 | -2.796 | -2.8352 | -2.717 | -2.758 | -2.7906 | -2.8193 | -2.8395 | -2.8666 | -3.2123 | -3.5277 | -3.5328 | -3.5465 | -3.5466 | -3.5543 | -3.5329 | -3.4896 | -3.7844
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | System Transformation | Headroom (MW) | Thermal | -2.6817 | -2.7295 | -2.8161 | -2.8755 | -2.712 | -2.7736 | -2.8747 | -2.9704 | -3.0489 | -3.1219 | -3.2019 | -3.272 | -3.3176 | -3.3658 | -3.4047 | -3.4298 | -3.5755 | -5.2195 | -6.9982
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | 52.7408 | -1.5531 | WPD Best View | Headroom (MW) | Thermal | -2.6844 | -2.7457 | -2.8383 | -2.9048 | -2.7454 | -2.8295 | -2.9465 | -3.0647 | -3.1633 | -3.2506 | -3.3402 | -3.4297 | -3.485 | -3.562 | -3.6201 | -3.6878 | -5.1051 | -7.117 | -10.1412
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Consumer Transformation | Headroom (MW) | Thermal | 7.2314 | 7.1118 | 6.9239 | 6.753 | 7.1266 | 6.7343 | 6.22 | 5.7224 | 5.294 | 4.8479 | 4.3283 | 3.8217 | 2.3765 | 1.8609 | 1.3866 | 0.87954 | -2.947 | -8.0337 | -11.8752
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Leading the Way | Headroom (MW) | Thermal | 7.2634 | 7.1998 | 7.0978 | 7.0739 | 7.799 | 7.5999 | 7.3433 | 7.1165 | 6.8935 | 6.7803 | 6.5236 | 6.2967 | 6.0496 | 5.8562 | 5.6545 | 4.493 | 1.8437 | -0.66625 | -4.5867
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | Steady Progression | Headroom (MW) | N/A | 7.2596 | 7.1997 | 7.1045 | 7.1231 | 7.555 | 7.4987 | 7.4582 | 7.4353 | 7.4041 | 7.3688 | 7.3087 | 7.1781 | 7.0598 | 6.9293 | 6.8097 | 6.7043 | 6.2647 | 6.3014 | 5.8277
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | System Transformation | Headroom (MW) | Thermal | 7.2557 | 7.1798 | 7.0529 | 7.0569 | 7.5152 | 7.3004 | 7.0051 | 6.7243 | 6.474 | 6.2167 | 5.9232 | 5.661 | 5.3848 | 5.1107 | 4.8801 | 4.6284 | 3.5258 | 1.3914 | -0.74251
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | 52.733 | -1.4998 | WPD Best View | Headroom (MW) | Thermal | 7.2565 | 7.1812 | 7.056 | 6.9688 | 7.4275 | 7.2125 | 6.9176 | 6.6344 | 6.378 | 6.1226 | 5.8371 | 5.5848 | 5.3169 | 5.0531 | 4.8289 | 4.5829 | 3.4021 | 0.99131 | -1.1782
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Consumer Transformation | Headroom (MW) | N/A | 96.6398 | 96.2463 | 95.355 | 94.7883 | 94.3857 | 94.2961 | 93.2151 | 92.0074 | 90.7092 | 89.5567 | 88.8159 | 87.0348 | 85.2632 | 82.6512 | 81.0583 | 79.8174 | 68.6408 | 50.5808 | 33.4119
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Leading the Way | Headroom (MW) | N/A | 96.7336 | 96.3501 | 95.5551 | 95.0261 | 94.829 | 95.2043 | 94.0245 | 93.3064 | 92.4848 | 91.9016 | 92.6924 | 91.7171 | 89.8389 | 87.5621 | 85.4524 | 83.7986 | 77.6365 | 93.1613 | 83.3325
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | Steady Progression | Headroom (MW) | N/A | 90.4992 | 90.1508 | 89.3912 | 89.0026 | 88.7495 | 88.8216 | 88.3568 | 84.8888 | 82.458 | 82.1003 | 79.6529 | 77.4044 | 77.0354 | 76.6811 | 76.3501 | 76.0111 | 74.9077 | 72.2588 | 69.2975
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | System Transformation | Headroom (MW) | N/A | 96.6703 | 96.3338 | 95.5723 | 95.1329 | 94.8537 | 95.0243 | 94.4023 | 93.8225 | 93.2228 | 92.7129 | 93.7547 | 93.0939 | 92.4556 | 91.8562 | 91.3388 | 91.2684 | 87.3401 | 79.9731 | 71.6128
East Claydon 132kV | Bletchley | Bletchley | Bulk Supply Point | 33 | 52.0114 | -0.7439 | WPD Best View | Headroom (MW) | N/A | 96.7336 | 96.4068 | 95.6119 | 95.1573 | 94.9601 | 95.3355 | 94.6205 | 93.9024 | 93.2303 | 92.647 | 93.6234 | 93.0637 | 91.6432 | 89.8856 | 87.7759 | 86.1221 | 79.5609 | 94.5172 | 84.007
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Consumer Transformation | Headroom (MW) | N/A | 20.0136 | 19.9349 | 19.774 | 19.6854 | 19.5979 | 19.5118 | 19.3874 | 19.304 | 19.1833 | 19.1037 | 18.9718 | 18.6089 | 18.2533 | 17.8999 | 17.5337 | 17.1155 | 15.7078 | 13.3979 | 11.2161
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Leading the Way | Headroom (MW) | N/A | 20.0137 | 19.9208 | 19.7601 | 19.6526 | 19.5655 | 19.4799 | 19.2836 | 19.2012 | 19.0888 | 19.0121 | 18.9017 | 18.7475 | 18.5867 | 18.4131 | 18.3554 | 18.2973 | 18.5623 | 24.123 | 23.4139
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | Steady Progression | Headroom (MW) | N/A | 20.0135 | 19.9337 | 19.7725 | 19.6811 | 19.5934 | 19.5069 | 19.4059 | 19.3214 | 19.2329 | 19.1507 | 18.7667 | 18.4147 | 18.3335 | 18.2562 | 18.1804 | 18.106 | 17.7325 | 17.3363 | 16.7845
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | System Transformation | Headroom (MW) | N/A | 20.0136 | 19.9349 | 19.7738 | 19.6851 | 19.5973 | 19.5108 | 19.42 | 19.3355 | 19.2495 | 19.1673 | 19.0865 | 19.0073 | 18.9275 | 18.8534 | 18.7821 | 18.7136 | 18.6797 | 17.7913 | 16.8426
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | 52.0115 | -0.7443 | WPD Best View | Headroom (MW) | N/A | 20.0137 | 19.9366 | 19.776 | 19.6878 | 19.6008 | 19.5152 | 19.4313 | 19.3489 | 19.2689 | 19.1922 | 19.1201 | 19.0527 | 18.9895 | 18.9297 | 18.8719 | 18.8138 | 19.3225 | 24.7053 | 23.4139
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Consumer Transformation | Headroom (MW) | N/A | 12.7125 | 12.6877 | 12.6339 | 12.6045 | 12.5755 | 12.5471 | 12.519 | 12.4921 | 12.4655 | 12.4405 | 12.416 | 12.3936 | 12.3727 | 12.3531 | 12.335 | 12.3177 | 12.2201 | 12.0816 | 11.9019
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Leading the Way | Headroom (MW) | N/A | 12.7134 | 12.6891 | 12.6354 | 12.6057 | 12.5767 | 12.5482 | 12.5179 | 12.4911 | 12.4646 | 12.4404 | 12.4171 | 12.3949 | 12.3746 | 12.3557 | 12.3395 | 12.3237 | 12.2125 | 12.066 | 11.9008
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | Steady Progression | Headroom (MW) | N/A | 12.7118 | 12.6861 | 12.6322 | 12.6026 | 12.5733 | 12.5443 | 12.5158 | 12.4876 | 12.4596 | 12.4322 | 12.4052 | 12.3787 | 12.3528 | 12.3275 | 12.3029 | 12.279 | 12.1743 | 12.0829 | 11.9512
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | System Transformation | Headroom (MW) | N/A | 12.7125 | 12.6875 | 12.6336 | 12.604 | 12.5746 | 12.5457 | 12.5174 | 12.4894 | 12.4618 | 12.4348 | 12.4083 | 12.3827 | 12.358 | 12.3343 | 12.3117 | 12.2909 | 12.2035 | 12.109 | 11.9912
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | 52.0345 | -0.6772 | WPD Best View | Headroom (MW) | N/A | 12.7134 | 12.6894 | 12.6356 | 12.6063 | 12.5773 | 12.5488 | 12.5212 | 12.4943 | 12.4686 | 12.4444 | 12.422 | 12.4016 | 12.3831 | 12.3662 | 12.35 | 12.3342 | 12.2355 | 12.1186 | 11.999
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Consumer Transformation | Headroom (MW) | N/A | 14.6821 | 14.6371 | 14.5241 | 14.4602 | 14.3966 | 14.3348 | 14.2331 | 14.1762 | 14.0798 | 14.0266 | 13.8871 | 13.5802 | 13.2852 | 13.0038 | 12.7116 | 12.3978 | 11.0263 | 9.5987 | 7.0102
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Leading the Way | Headroom (MW) | N/A | 14.6894 | 14.6281 | 14.5164 | 14.4263 | 14.3624 | 14.3008 | 14.0838 | 14.0272 | 13.9242 | 13.8737 | 13.695 | 13.4343 | 13.164 | 12.8872 | 12.7733 | 12.6796 | 14.4642 | 13.469 | 11.175
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | Steady Progression | Headroom (MW) | N/A | 14.6767 | 14.6277 | 14.5132 | 14.4459 | 14.3817 | 14.3186 | 14.2382 | 14.1778 | 14.1115 | 14.0529 | 13.5628 | 13.1168 | 13.0586 | 13.005 | 12.9533 | 12.9032 | 12.6408 | 12.3253 | 11.8088
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | System Transformation | Headroom (MW) | N/A | 14.6821 | 14.6369 | 14.5236 | 14.4595 | 14.3952 | 14.3326 | 14.2665 | 14.2077 | 14.1464 | 14.0892 | 14.0337 | 13.9798 | 13.9253 | 13.876 | 13.8293 | 13.7855 | 13.3673 | 12.8104 | 10.8531
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | 52.048 | -0.7068 | WPD Best View | Headroom (MW) | N/A | 14.6894 | 14.649 | 14.5373 | 14.4738 | 14.4098 | 14.3482 | 14.2893 | 14.2328 | 14.1788 | 14.1283 | 14.0106 | 13.8871 | 13.7681 | 13.6628 | 13.5489 | 13.4552 | 14.4642 | 13.469 | 11.175
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Consumer Transformation | Headroom (MW) | N/A | 15.3833 | 15.3483 | 15.2733 | 15.2311 | 15.1897 | 15.1492 | 15.0978 | 15.0595 | 15.0103 | 14.9744 | 14.9252 | 14.8844 | 14.845 | 14.8063 | 14.78 | 14.7547 | 14.575 | 13.8811 | 13.1695
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Leading the Way | Headroom (MW) | N/A | 15.3911 | 15.3517 | 15.2776 | 15.2283 | 15.1876 | 15.1463 | 15.0662 | 15.0272 | 14.9785 | 14.9435 | 14.8981 | 14.8396 | 14.781 | 14.7202 | 14.6979 | 14.6754 | 14.456 | 14.2005 | 13.9299
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | Steady Progression | Headroom (MW) | N/A | 15.3775 | 15.3414 | 15.2653 | 15.2228 | 15.1816 | 15.1411 | 15.0965 | 15.0571 | 15.0161 | 14.9778 | 14.9384 | 14.9014 | 14.8634 | 14.8272 | 14.7915 | 14.7568 | 14.6319 | 14.4644 | 14.2293
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | System Transformation | Headroom (MW) | N/A | 15.3832 | 15.3482 | 15.273 | 15.2305 | 15.1887 | 15.1476 | 15.1057 | 15.066 | 15.0257 | 14.9869 | 14.9498 | 14.9136 | 14.8776 | 14.8434 | 14.8111 | 14.7807 | 14.6937 | 14.5324 | 14.3308
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | 52.0413 | -0.6874 | WPD Best View | Headroom (MW) | N/A | 15.3911 | 15.3572 | 15.2831 | 15.2406 | 15.2 | 15.1587 | 15.1185 | 15.0795 | 15.0423 | 15.0072 | 14.9752 | 14.9465 | 14.9207 | 14.8972 | 14.8749 | 14.8524 | 14.7122 | 14.5446 | 14.367
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Consumer Transformation | Headroom (MW) | Fault level | -11.5981 | -11.6361 | -11.7167 | -11.8188 | -11.9399 | -12.1265 | -12.3966 | -12.6466 | -12.9044 | -13.1519 | -14.4269 | -14.7374 | -15.0706 | -16.3484 | -16.6237 | -16.9253 | -21.6757 | -29.494 | -35.1382
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Leading the Way | Headroom (MW) | Fault level | -11.4984 | -11.5224 | -11.5513 | -11.615 | -11.6644 | -11.7411 | -11.8871 | -11.989 | -12.1024 | -12.1893 | -12.3185 | -12.4451 | -13.527 | -14.76 | -16.3301 | -17.9224 | -23.8389 | -29.9411 | -35.9862
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | Steady Progression | Headroom (MW) | Fault level | -9.5641 | -9.5845 | -9.5943 | -9.6063 | -9.6172 | -9.6359 | -9.659 | -9.6779 | -9.7056 | -9.7362 | -9.786 | -9.8264 | -9.86 | -9.8923 | -9.923 | -9.9672 | -10.149 | -11.2997 | -11.6042
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | System Transformation | Headroom (MW) | Fault level | -11.1772 | -11.2003 | -11.2259 | -11.2777 | -11.328 | -11.3974 | -11.5175 | -11.6297 | -11.758 | -11.8911 | -12.0457 | -12.1788 | -12.3035 | -12.4415 | -12.5634 | -12.7083 | -15.3372 | -18.9822 | -21.5342
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | 51.9905 | -0.753 | WPD Best View | Headroom (MW) | Fault level | -11.0022 | -11.0252 | -11.0528 | -11.1138 | -11.1611 | -11.2344 | -11.3741 | -11.4717 | -11.5801 | -11.6633 | -11.7869 | -11.9081 | -12.9433 | -14.1231 | -15.6254 | -17.149 | -22.8102 | -28.6491 | -34.4333
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Consumer Transformation | Headroom (MW) | N/A | 5.4927 | 5.4725 | 5.4327 | 5.4157 | 5.6222 | 5.603 | 5.5806 | 5.5685 | 5.5721 | 5.5776 | 5.562 | 5.5509 | 5.5321 | 5.5133 | 5.5066 | 5.9403 | 5.7909 | 5.5124 | 5.0323
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Leading the Way | Headroom (MW) | N/A | 5.4932 | 5.4722 | 5.4325 | 5.4155 | 5.7046 | 5.6844 | 5.6464 | 5.6442 | 5.6341 | 5.6561 | 5.6162 | 5.5451 | 5.4695 | 5.3878 | 5.3736 | 5.7969 | 5.572 | 5.3373 | 5.096
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | Steady Progression | Headroom (MW) | N/A | 5.4921 | 5.4717 | 5.4317 | 5.4131 | 5.5571 | 5.5381 | 5.5189 | 5.5164 | 5.5132 | 5.5092 | 5.4995 | 5.4905 | 5.4814 | 5.4726 | 5.4638 | 5.4553 | 5.3586 | 5.2909 | 5.1542
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | System Transformation | Headroom (MW) | N/A | 5.4927 | 5.4724 | 5.4326 | 5.4156 | 5.622 | 5.6026 | 5.5839 | 5.5715 | 5.5816 | 5.5864 | 5.5814 | 5.5761 | 5.5633 | 5.5514 | 5.543 | 5.9751 | 5.8849 | 5.786 | 5.6646
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | 52.0414 | -0.7463 | WPD Best View | Headroom (MW) | N/A | 5.4932 | 5.4731 | 5.4333 | 5.4181 | 5.7072 | 5.687 | 5.6686 | 5.6663 | 5.6715 | 5.6935 | 5.6779 | 5.6622 | 5.6469 | 5.6322 | 5.618 | 6.0413 | 5.9474 | 5.7142 | 5.2351
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Consumer Transformation | Headroom (MW) | N/A | 16.4955 | 16.4063 | 16.2835 | 16.1561 | 16.0164 | 15.7938 | 15.4911 | 15.1948 | 14.9019 | 14.5623 | 16.5321 | 16.185 | 15.825 | 15.4834 | 15.1438 | 14.7685 | 12.8352 | 9.9915 | 7.2743
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Leading the Way | Headroom (MW) | N/A | 16.405 | 16.3469 | 16.2701 | 16.2011 | 16.1309 | 16.0485 | 15.9154 | 15.8259 | 15.7101 | 15.6098 | 17.76 | 17.6304 | 17.4843 | 17.3322 | 17.1798 | 17.0009 | 16.1956 | 15.3401 | 13.5439
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | Steady Progression | Headroom (MW) | Fault level | 6.4793 | 6.4585 | 6.4379 | 6.4201 | 6.3986 | 6.3821 | 6.3563 | 2.7389 | 0.31052 | 0.27346 | -1.3093 | -2.7498 | -2.7954 | -2.8341 | -2.8786 | -2.9277 | -3.1496 | -3.4366 | -3.7764
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | System Transformation | Headroom (MW) | N/A | 15.9428 | 15.9022 | 15.8486 | 15.7948 | 15.7254 | 15.6479 | 15.5118 | 15.3889 | 15.2239 | 15.0734 | 17.1418 | 16.9686 | 16.803 | 16.6526 | 16.5011 | 16.3275 | 15.5507 | 14.8996 | 14.332
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | 51.9975 | -0.7186 | WPD Best View | Headroom (MW) | N/A | 15.6971 | 15.6415 | 15.568 | 15.502 | 15.4348 | 15.356 | 15.2286 | 15.1429 | 15.0322 | 14.9362 | 16.9936 | 16.8696 | 16.7298 | 16.5843 | 16.4385 | 16.2673 | 15.4967 | 14.6782 | 12.9595
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Consumer Transformation | Headroom (MW) | N/A | 23.6303 | 23.5604 | 23.3807 | 23.2164 | 23.0491 | 22.7966 | 22.4429 | 22.0452 | 21.6359 | 21.2065 | 20.7199 | 20.2591 | 19.8008 | 19.3653 | 18.9769 | 18.6362 | 17.2393 | 15.8437 | 14.4642
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Leading the Way | Headroom (MW) | N/A | 23.6649 | 23.6335 | 23.4841 | 23.3675 | 23.2358 | 23.0701 | 22.7967 | 22.4384 | 22.0677 | 21.6867 | 21.3044 | 21.0727 | 20.8593 | 20.6579 | 20.5084 | 20.4 | 19.583 | 18.7054 | 17.6743
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | Steady Progression | Headroom (MW) | N/A | 23.6284 | 23.6065 | 23.496 | 23.4451 | 23.3849 | 23.3182 | 23.2563 | 23.1865 | 23.1075 | 23.0404 | 22.9513 | 22.8644 | 22.778 | 22.6864 | 22.599 | 22.5042 | 22.4361 | 22.3119 | 21.8217
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | System Transformation | Headroom (MW) | N/A | 23.6389 | 23.6157 | 23.5125 | 23.4322 | 23.3275 | 23.2263 | 23.0751 | 22.9201 | 22.7521 | 22.5836 | 22.4096 | 22.2515 | 22.0808 | 21.9145 | 21.7643 | 21.6253 | 21.1933 | 20.685 | 19.9973
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | 52.0241 | -0.6881 | WPD Best View | Headroom (MW) | N/A | 23.6649 | 23.6335 | 23.4841 | 23.3675 | 23.2358 | 23.0701 | 22.7967 | 22.4384 | 22.0677 | 21.6867 | 21.3044 | 21.0727 | 20.8593 | 20.6579 | 20.5084 | 20.4 | 19.583 | 18.7054 | 17.6743
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Consumer Transformation | Headroom (MW) | Thermal | 39.9301 | 39.7286 | 39.5229 | 39.3686 | 39.2567 | 39.1674 | 38.8607 | 38.5628 | 37.2648 | 36.9611 | 34.3367 | 32.7101 | 29.2408 | 10.6172 | 8.2395 | 5.7651 | -14.1155 | -45.5009 | -72.9476
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Leading the Way | Headroom (MW) | Thermal | 40.0302 | 39.9055 | 39.9389 | 40.0802 | 40.2838 | 40.7489 | 41.0624 | 41.3336 | 24.547 | 24.8164 | 23.7315 | 23.5007 | 22.3375 | 17.6325 | 9.7577 | 0.69021 | -22.8826 | -51.5654 | -80.5029
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | Steady Progression | Headroom (MW) | N/A | 39.9664 | 39.8191 | 39.2753 | 39.2708 | 39.3037 | 39.5098 | 39.6602 | 39.78 | 39.8519 | 39.9247 | 39.8022 | 39.7218 | 39.6615 | 39.618 | 39.6057 | 39.5926 | 39.8236 | 37.5008 | 32.7928
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | System Transformation | Headroom (MW) | Thermal | 39.9671 | 39.8434 | 39.726 | 39.7386 | 39.7544 | 39.9336 | 39.9727 | 39.9751 | 39.8637 | 39.821 | 39.5122 | 39.2481 | 38.0967 | 20.9576 | 20.8264 | 20.6802 | 11.4147 | -4.1694 | -20.121
East Claydon 132kV | Brackley | Brackley | Bulk Supply Point | 33 | 52.0489 | -1.1461 | WPD Best View | Headroom (MW) | Thermal | 40.0302 | 39.9055 | 39.9389 | 40.0802 | 40.2838 | 40.7489 | 41.1203 | 41.3915 | 24.6189 | 24.8884 | 23.822 | 23.6345 | 22.521 | 17.8746 | 9.7577 | 0.69021 | -22.8826 | -51.5654 | -80.5029
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Consumer Transformation | Headroom (MW) | N/A | 14.5814 | 14.5058 | 14.3642 | 14.2358 | 14.1052 | 13.9335 | 13.7131 | 13.5003 | 13.312 | 13.1129 | 12.8987 | 12.7057 | 12.5195 | 11.4091 | 11.2474 | 11.0722 | 9.8361 | 3.7744 | 0.074103
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Leading the Way | Headroom (MW) | Thermal | 14.6009 | 14.5598 | 14.4538 | 14.3767 | 14.2917 | 14.2403 | 14.1448 | 14.0807 | 14.0224 | 13.9849 | 13.9511 | 13.9539 | 13.9656 | 13.9748 | 12.2896 | 10.5592 | 7.7846 | 4.3764 | -1.29
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | Steady Progression | Headroom (MW) | N/A | 14.602 | 14.5531 | 14.4622 | 14.4153 | 14.3591 | 14.3167 | 14.274 | 14.2237 | 14.166 | 14.1203 | 14.0555 | 14.0233 | 13.9887 | 13.9681 | 13.9558 | 13.9511 | 14.055 | 14.0881 | 13.6369
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | System Transformation | Headroom (MW) | N/A | 14.5928 | 14.5449 | 14.4326 | 14.3675 | 14.2815 | 14.2059 | 14.0613 | 13.9442 | 13.8049 | 13.6776 | 13.5471 | 13.4468 | 13.3632 | 13.2983 | 13.2512 | 13.2092 | 13.104 | 10.0813 | 8.2878
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | 52.0273 | -1.1377 | WPD Best View | Headroom (MW) | Thermal | 14.6009 | 14.5598 | 14.4538 | 14.3767 | 14.2917 | 14.2403 | 14.1448 | 14.0807 | 14.0224 | 13.9849 | 13.9511 | 13.9539 | 13.9656 | 13.9748 | 12.2896 | 10.5592 | 7.7846 | 4.3764 | -1.29
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Consumer Transformation | Headroom (MW) | Thermal | 6.688 | 6.6819 | 6.58 | 6.5001 | 6.4308 | 6.3439 | 6.2318 | 6.1292 | 6.0252 | 5.9203 | 5.8044 | 5.7071 | 4.6804 | 4.5727 | 4.4941 | 4.403 | 2.8374 | -0.12293 | -3.1253
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Leading the Way | Headroom (MW) | Thermal | 6.7145 | 6.6826 | 6.5958 | 6.5476 | 6.5054 | 6.4576 | 6.4134 | 6.3686 | 6.3506 | 6.3302 | 6.3087 | 6.2859 | 6.258 | 6.2463 | 4.5294 | 3.5657 | 1.9716 | -0.7783 | -3.6213
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | Steady Progression | Headroom (MW) | N/A | 6.6807 | 6.6726 | 6.5929 | 6.5496 | 6.5072 | 6.4665 | 6.4262 | 6.3881 | 6.3444 | 6.2935 | 6.2492 | 6.2123 | 6.1752 | 6.1381 | 6.1027 | 6.0755 | 6.02 | 5.9248 | 5.6517
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | System Transformation | Headroom (MW) | N/A | 6.6928 | 6.6959 | 6.6138 | 6.5597 | 6.502 | 6.4381 | 6.368 | 6.2907 | 6.2124 | 6.1306 | 6.058 | 5.9914 | 5.9297 | 5.8834 | 5.8372 | 5.7865 | 5.6374 | 4.0846 | 1.5047
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | 52.049 | -1.1455 | WPD Best View | Headroom (MW) | Thermal | 6.7145 | 6.6826 | 6.5958 | 6.5476 | 6.5054 | 6.4576 | 6.4134 | 6.3686 | 6.3506 | 6.3302 | 6.3087 | 6.2859 | 6.258 | 6.2463 | 4.5294 | 3.5657 | 1.9716 | -0.7783 | -3.6213
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Consumer Transformation | Headroom (MW) | N/A | 20.4359 | 20.4345 | 20.4881 | 20.5594 | 20.6716 | 20.8931 | 21.1511 | 21.3337 | 21.4537 | 21.6148 | 20.6943 | 20.7206 | 19.8226 | 19.8244 | 18.9559 | 19.0023 | 13.1035 | 8.0222 | 1.3988
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Leading the Way | Headroom (MW) | Thermal | 20.4504 | 20.4702 | 20.568 | 20.6941 | 20.8921 | 21.2362 | 21.6083 | 21.8144 | 21.9501 | 22.1191 | 22.1464 | 22.0933 | 21.133 | 21.0452 | 18.454 | 17.5193 | 11.5248 | 4.9752 | -1.8689
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | Steady Progression | Headroom (MW) | N/A | 20.4298 | 20.4284 | 20.461 | 20.5161 | 20.6069 | 20.7877 | 20.981 | 21.1269 | 21.2443 | 21.3569 | 21.3877 | 21.4115 | 21.4401 | 21.4597 | 21.4872 | 21.512 | 21.4858 | 21.5925 | 19.5938
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | System Transformation | Headroom (MW) | N/A | 20.4364 | 20.4415 | 20.4926 | 20.5704 | 20.6959 | 20.926 | 21.2149 | 21.409 | 21.5515 | 21.7157 | 21.7653 | 21.8078 | 21.8524 | 21.8865 | 21.9263 | 21.967 | 18.9396 | 16.4804 | 13.4233
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | 52.0748 | -1.0311 | WPD Best View | Headroom (MW) | Thermal | 20.4504 | 20.4702 | 20.568 | 20.6941 | 20.8921 | 21.2362 | 21.6662 | 21.8723 | 22.0221 | 22.191 | 22.2369 | 22.227 | 21.3165 | 21.2872 | 18.454 | 17.5193 | 11.5248 | 4.9752 | -1.8689
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Consumer Transformation | Headroom (MW) | Thermal | 4.8297 | 4.7911 | 4.7155 | 4.6577 | 4.6004 | 4.5092 | 4.3741 | 4.2576 | 3.1975 | 3.096 | 2.9263 | 1.8292 | 0.7456 | 0.59117 | -0.4135 | -1.4363 | -8.7858 | -18.5787 | -27.5032
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Leading the Way | Headroom (MW) | Thermal | 4.8408 | 4.822 | 4.773 | 4.7509 | 4.7325 | 4.7246 | 4.6905 | 4.693 | 4.6799 | 4.698 | 3.7412 | 3.7212 | 3.6955 | 1.4682 | -0.20384 | -2.8397 | -11.2021 | -19.9403 | -28.8286
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | Steady Progression | Headroom (MW) | N/A | 4.8449 | 4.8114 | 4.7623 | 4.7286 | 4.7047 | 4.683 | 4.6576 | 4.6394 | 4.6117 | 4.5879 | 4.5588 | 4.529 | 4.5176 | 4.5124 | 4.5133 | 4.5202 | 4.6102 | 3.3775 | 1.8417
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | System Transformation | Headroom (MW) | Thermal | 4.8353 | 4.8083 | 4.7453 | 4.7027 | 4.6574 | 4.6152 | 4.5273 | 4.4581 | 4.3672 | 4.2915 | 4.2162 | 4.1477 | 3.1655 | 3.1354 | 3.1122 | 3.0914 | -0.42659 | -4.4998 | -9.6801
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | 52.0774 | -1.2411 | WPD Best View | Headroom (MW) | Thermal | 4.8408 | 4.822 | 4.773 | 4.7509 | 4.7325 | 4.7246 | 4.6905 | 4.693 | 4.6799 | 4.698 | 3.7412 | 3.7212 | 3.6955 | 1.4682 | -0.20384 | -2.8397 | -11.2021 | -19.9403 | -28.8286
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Consumer Transformation | Headroom (MW) | N/A | 20.5367 | 20.4569 | 20.5167 | 20.5572 | 20.5905 | 20.6293 | 20.5324 | 20.4836 | 20.418 | 20.3587 | 19.1546 | 18.8891 | 18.6143 | 18.3352 | 18.0711 | 16.8393 | 13.0087 | 5.5197 | 0.32346
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Leading the Way | Headroom (MW) | Thermal | 20.5652 | 20.5125 | 20.6898 | 20.8526 | 21.0038 | 21.2317 | 21.347 | 21.5186 | 21.6594 | 21.7997 | 21.6996 | 21.5618 | 21.4009 | 19.0134 | 18.804 | 16.001 | 11.154 | 3.917 | -0.77871
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | Steady Progression | Headroom (MW) | N/A | 20.5506 | 20.4951 | 20.1385 | 20.2028 | 20.2673 | 20.3976 | 20.463 | 20.5436 | 20.6271 | 20.7077 | 20.6925 | 20.6873 | 20.6815 | 20.6813 | 20.6884 | 20.6754 | 20.7942 | 19.6596 | 19.2104
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | System Transformation | Headroom (MW) | N/A | 20.5513 | 20.4944 | 20.5833 | 20.68 | 20.7593 | 20.89 | 20.9427 | 21.0147 | 21.0694 | 21.1474 | 21.0672 | 20.996 | 20.9275 | 20.8694 | 20.8149 | 20.7416 | 18.2758 | 13.7996 | 10.4588
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | 52.1246 | -0.9797 | WPD Best View | Headroom (MW) | Thermal | 20.5652 | 20.5125 | 20.6898 | 20.8526 | 21.0038 | 21.2317 | 21.347 | 21.5186 | 21.6594 | 21.7997 | 21.6996 | 21.5618 | 21.4009 | 19.0134 | 18.804 | 16.001 | 11.154 | 3.917 | -0.77871
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Consumer Transformation | Headroom (MW) | Thermal | 41.1608 | 40.9977 | 40.4519 | 40.1715 | 39.7565 | 39.1025 | 38.5944 | 37.679 | 36.7809 | 35.8091 | 28.1964 | 27.2149 | 26.2833 | 24.4756 | 23.6299 | 22.6785 | 12.1719 | -1.5254 | -11.8568
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Leading the Way | Headroom (MW) | N/A | 41.2063 | 41.1514 | 40.7117 | 40.5561 | 40.3077 | 39.9985 | 39.8497 | 40.1199 | 40.0673 | 40.1038 | 34.7984 | 34.7409 | 34.6748 | 34.592 | 33.6883 | 33.7636 | 27.4931 | 15.0951 | 6.7681
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | Steady Progression | Headroom (MW) | N/A | 41.1909 | 41.0459 | 40.5727 | 40.3993 | 40.153 | 39.9317 | 39.9269 | 38.9539 | 37.9969 | 38.0705 | 37.661 | 37.3467 | 37.466 | 37.6241 | 37.8042 | 37.9848 | 33.3921 | 33.5968 | 31.8293
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | System Transformation | Headroom (MW) | N/A | 41.1779 | 41.0785 | 40.6012 | 40.4233 | 40.1235 | 39.8081 | 39.8262 | 39.8653 | 39.8367 | 39.7934 | 39.5301 | 39.3404 | 39.2313 | 39.1663 | 39.1765 | 35.4487 | 31.2923 | 24.3494 | 19.5619
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | 52.0493 | -0.7968 | WPD Best View | Headroom (MW) | N/A | 41.2063 | 41.1925 | 40.7528 | 40.6547 | 40.4063 | 40.0971 | 40.317 | 40.5205 | 40.564 | 40.6005 | 35.4074 | 35.5969 | 35.7993 | 36.0183 | 34.8778 | 34.8711 | 28.1899 | 15.0951 | 6.7681
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Consumer Transformation | Headroom (MW) | N/A | 16.9628 | 16.9287 | 16.8456 | 16.8016 | 16.7502 | 16.6995 | 16.6127 | 16.3365 | 16.0755 | 15.8035 | 15.5155 | 15.2495 | 14.9838 | 14.7244 | 14.4666 | 14.2047 | 12.7839 | 11.2264 | 9.7174
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Leading the Way | Headroom (MW) | N/A | 16.9665 | 16.9257 | 16.849 | 16.7887 | 16.7388 | 16.6896 | 16.5105 | 16.4649 | 16.3751 | 16.3294 | 16.2365 | 16.0878 | 15.9345 | 15.7705 | 15.7401 | 15.7093 | 21.4239 | 20.7943 | 19.7984
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | Steady Progression | Headroom (MW) | N/A | 16.9601 | 16.9211 | 16.8322 | 16.783 | 16.7309 | 16.6802 | 16.618 | 15.5437 | 14.4639 | 14.4145 | 13.8964 | 13.4235 | 13.3739 | 13.3275 | 13.2824 | 13.2386 | 13.0095 | 12.7503 | 12.3496
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | System Transformation | Headroom (MW) | N/A | 16.9628 | 16.9286 | 16.8454 | 16.8013 | 16.7496 | 16.6983 | 16.6442 | 16.5958 | 16.5444 | 16.4956 | 16.3641 | 16.2018 | 16.0577 | 15.9162 | 15.7945 | 15.6594 | 15.1604 | 14.5574 | 13.8583
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | 52.0336 | -0.7647 | WPD Best View | Headroom (MW) | N/A | 16.9665 | 16.9389 | 16.8622 | 16.8217 | 16.7718 | 16.7226 | 16.6759 | 16.6303 | 16.5831 | 16.5375 | 16.4948 | 16.4559 | 16.4209 | 16.3889 | 16.3025 | 16.1896 | 21.7022 | 20.7943 | 19.7984
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Consumer Transformation | Headroom (MW) | N/A | 8.7169 | 8.6915 | 8.6414 | 8.616 | 8.5874 | 8.5594 | 8.5217 | 8.4761 | 8.4436 | 8.4168 | 8.3834 | 8.3533 | 8.3121 | 7.3904 | 7.3797 | 7.3699 | 5.8412 | 3.0675 | 0.22495
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Leading the Way | Headroom (MW) | Thermal | 8.7173 | 8.6881 | 8.6396 | 8.6088 | 8.5802 | 8.5525 | 8.4854 | 8.4603 | 8.4159 | 8.3951 | 8.3544 | 8.3007 | 8.2389 | 8.1847 | 7.1034 | 7.1196 | 3.4696 | 0.40846 | -2.4504
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | Steady Progression | Headroom (MW) | N/A | 8.7165 | 8.6903 | 8.6386 | 8.6108 | 8.5814 | 8.5526 | 8.5197 | 8.4919 | 8.4628 | 8.4357 | 8.4078 | 8.382 | 8.3561 | 8.3318 | 8.3086 | 8.2866 | 8.1802 | 8.0746 | 7.1347
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | System Transformation | Headroom (MW) | N/A | 8.7168 | 8.6913 | 8.6409 | 8.6151 | 8.5859 | 8.5571 | 8.5272 | 8.4994 | 8.4717 | 8.4455 | 8.4193 | 8.3867 | 8.3632 | 8.3422 | 8.3235 | 8.3071 | 7.2524 | 5.8493 | 4.2397
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | 52.1067 | -0.8058 | WPD Best View | Headroom (MW) | Thermal | 8.7173 | 8.6928 | 8.6443 | 8.6202 | 8.5917 | 8.564 | 8.5375 | 8.5124 | 8.4803 | 8.4595 | 8.433 | 8.4102 | 8.382 | 8.3655 | 7.1034 | 7.1196 | 3.4696 | 0.40846 | -2.4504
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Consumer Transformation | Headroom (MW) | N/A | 16.2084 | 16.2129 | 16.1385 | 16.0928 | 16.0435 | 15.9991 | 15.9116 | 15.6261 | 15.3419 | 15.0478 | 14.7281 | 14.4221 | 14.1353 | 13.837 | 13.5427 | 13.2027 | 11.4081 | 9.4884 | 7.6655
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Leading the Way | Headroom (MW) | N/A | 16.2094 | 16.2147 | 16.1475 | 16.0798 | 16.0325 | 15.9873 | 15.8071 | 15.7627 | 15.6766 | 15.6343 | 15.5479 | 15.4074 | 15.2598 | 15.0991 | 15.0723 | 15.0449 | 14.615 | 12.7853 | 11.7192
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | Steady Progression | Headroom (MW) | N/A | 16.2077 | 16.1978 | 16.118 | 16.0678 | 16.0206 | 15.9743 | 15.9108 | 15.865 | 15.8134 | 15.7681 | 15.7178 | 15.6741 | 15.6283 | 15.5863 | 15.5445 | 15.5039 | 15.2917 | 15.039 | 14.6056
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | System Transformation | Headroom (MW) | N/A | 16.2084 | 16.2128 | 16.1383 | 16.0925 | 16.0429 | 15.998 | 15.9484 | 15.9035 | 15.8559 | 15.7948 | 15.5875 | 15.4072 | 15.2477 | 15.0887 | 14.9391 | 14.7768 | 14.1498 | 13.4807 | 12.7365
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | 52.0622 | -0.7589 | WPD Best View | Headroom (MW) | N/A | 16.2094 | 16.2331 | 16.1659 | 16.1222 | 16.0749 | 16.0296 | 15.9902 | 15.9458 | 15.9009 | 15.8586 | 15.8201 | 15.7858 | 15.7546 | 15.7262 | 15.6994 | 15.672 | 15.0335 | 12.7853 | 11.7192
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Consumer Transformation | Headroom (MW) | N/A | 13.4339 | 13.3754 | 13.1935 | 13.0443 | 12.882 | 12.6311 | 12.7094 | 12.788 | 12.8337 | 12.8129 | 12.7363 | 12.7505 | 12.7685 | 12.7944 | 12.8428 | 12.8816 | 9.4087 | 7.1847 | 5.9125
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Leading the Way | Headroom (MW) | N/A | 13.4557 | 13.4559 | 13.3221 | 13.2332 | 13.1363 | 12.9937 | 13.3775 | 13.7532 | 14.0709 | 14.3217 | 14.5263 | 14.8726 | 15.2145 | 15.5525 | 15.8505 | 16.1048 | 11.7923 | 9.0477 | 7.6591
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | Steady Progression | Headroom (MW) | N/A | 13.4544 | 13.4173 | 13.2851 | 13.2197 | 13.1539 | 13.0884 | 13.2843 | 13.5013 | 13.7326 | 13.9697 | 14.2135 | 14.4945 | 14.7778 | 15.0733 | 15.374 | 15.672 | 14.8489 | 16.0925 | 16.8339
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | System Transformation | Headroom (MW) | N/A | 13.4448 | 13.4173 | 13.2812 | 13.1822 | 13.0748 | 12.9555 | 13.2335 | 13.527 | 13.8204 | 14.1029 | 14.4146 | 14.7868 | 15.1742 | 15.5701 | 15.9806 | 16.4068 | 14.8716 | 13.9027 | 13.4765
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | 52.076 | -0.7259 | WPD Best View | Headroom (MW) | N/A | 13.4557 | 13.4559 | 13.3221 | 13.2332 | 13.1363 | 12.9937 | 13.3775 | 13.7532 | 14.0709 | 14.3217 | 14.5263 | 14.8726 | 15.2145 | 15.5525 | 15.8505 | 16.1048 | 11.7923 | 9.0477 | 7.6591
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Consumer Transformation | Headroom (MW) | N/A | 13.8747 | 13.9006 | 13.8326 | 13.896 | 13.8566 | 13.7139 | 13.5349 | 13.3156 | 13.0904 | 12.8717 | 12.659 | 12.4388 | 12.2274 | 12.0115 | 11.8208 | 11.6143 | 10.5193 | 9.3029 | 8.0962
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Leading the Way | Headroom (MW) | N/A | 13.8747 | 13.9178 | 13.8493 | 13.9424 | 13.9157 | 13.8906 | 13.8154 | 13.794 | 13.6203 | 13.449 | 13.3312 | 13.2432 | 13.1587 | 13.087 | 13.0046 | 12.8995 | 12.3394 | 11.619 | 10.8352
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | Steady Progression | Headroom (MW) | N/A | 13.8746 | 13.884 | 13.8161 | 13.8513 | 13.8229 | 13.7946 | 13.764 | 13.7426 | 13.72 | 13.6958 | 13.6687 | 13.6438 | 13.6184 | 13.5947 | 13.5706 | 13.5472 | 13.4026 | 13.2611 | 12.9284
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | System Transformation | Headroom (MW) | N/A | 13.8746 | 13.9005 | 13.8324 | 13.8957 | 13.8654 | 13.8408 | 13.8105 | 13.7471 | 13.6485 | 13.5359 | 13.4314 | 13.3342 | 13.2267 | 13.1379 | 13.0564 | 12.9608 | 12.5905 | 12.1273 | 11.5718
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | 52.0451 | -0.7618 | WPD Best View | Headroom (MW) | N/A | 13.8747 | 13.9227 | 13.8543 | 13.9541 | 13.9274 | 13.9023 | 13.8821 | 13.794 | 13.6203 | 13.449 | 13.3312 | 13.2432 | 13.1587 | 13.087 | 13.0046 | 12.8995 | 12.3394 | 11.619 | 10.8352
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Consumer Transformation | Headroom (MW) | Fault level | -12.563 | -12.6164 | -12.6889 | -12.7839 | -12.8896 | -13.0504 | -13.2611 | -13.4645 | -13.6597 | -13.8724 | -14.1128 | -14.3613 | -14.6004 | -14.8435 | -15.0935 | -15.3639 | -16.7522 | -20.077 | -21.3646
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Leading the Way | Headroom (MW) | Fault level | -12.47 | -12.4898 | -12.54 | -12.5821 | -12.632 | -12.7051 | -12.7882 | -12.8428 | -12.9201 | -12.9942 | -13.0811 | -13.1793 | -13.279 | -13.3944 | -13.5106 | -13.6525 | -16.4257 | -19.0622 | -19.7547
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | Steady Progression | Headroom (MW) | Fault level | -10.375 | -10.3864 | -10.4002 | -10.4129 | -10.4326 | -10.4412 | -10.4543 | -10.4753 | -10.4925 | -10.5243 | -10.555 | -10.5885 | -10.6212 | -10.6468 | -10.6714 | -10.7044 | -10.8811 | -11.1198 | -11.4031
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | System Transformation | Headroom (MW) | Fault level | -12.121 | -12.1387 | -12.1792 | -12.2155 | -12.2585 | -12.3218 | -12.422 | -12.5066 | -12.6243 | -12.7351 | -12.8514 | -12.9691 | -13.0781 | -13.1945 | -13.3058 | -13.4343 | -14.0104 | -16.4043 | -16.88
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | 52.0634 | -0.8221 | WPD Best View | Headroom (MW) | Fault level | -11.9319 | -11.9508 | -11.9989 | -12.0392 | -12.0869 | -12.1569 | -12.2363 | -12.2886 | -12.3625 | -12.4335 | -12.5166 | -12.6106 | -12.706 | -12.8164 | -12.9276 | -13.0634 | -15.7169 | -18.2396 | -18.9022
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Consumer Transformation | Headroom (MW) | Thermal | 27.7978 | 27.5619 | -3.8281 | -4.2247 | -4.9284 | -5.8913 | -7.2162 | -8.4065 | -9.6109 | -10.8243 | -13.1568 | -26.5264 | -44.6864 | -48.5913 | -49.6012 | -54.1212 | -70.735 | -101.5607 | -111.9209
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Leading the Way | Headroom (MW) | Thermal | 27.9455 | 27.7052 | -3.4845 | -3.4866 | -3.8272 | -33.091 | -33.7139 | -34.1964 | -34.7442 | -35.1604 | -35.7193 | -47.6143 | -51.3244 | -52.9322 | -61.7751 | -68.7225 | -95.6648 | -110.916 | -137.4693
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | Steady Progression | Headroom (MW) | Thermal | 27.8481 | 27.6995 | -3.4585 | -3.4964 | -3.6668 | -3.8798 | -4.097 | -4.283 | -4.5257 | -4.7541 | -5.0644 | -5.3073 | -5.4923 | -5.6583 | -5.8106 | -5.9041 | -7.0699 | -9.9216 | -16.6914
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | System Transformation | Headroom (MW) | Thermal | 27.861 | 27.7244 | -3.4894 | -3.5361 | -3.8906 | -4.3411 | -4.9968 | -5.6016 | -6.3106 | -6.9785 | -7.7158 | -20.4299 | -37.9177 | -38.374 | -38.7496 | -42.5204 | -50.7481 | -70.8638 | -72.5047
East Claydon 132kV | Stony Stratford | Stony Stratford | Bulk Supply Point | 33 | 52.0184 | -0.8669 | WPD Best View | Headroom (MW) | Thermal | 27.9455 | 27.7275 | 27.2968 | 27.3252 | 26.9363 | -2.3276 | -2.9133 | -3.3957 | -3.9272 | -4.3033 | -4.7704 | -16.575 | -20.1874 | -21.5746 | -30.6956 | -37.6982 | -64.5752 | -79.7544 | -106.5174
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Consumer Transformation | Headroom (MW) | Thermal | 13.8142 | 13.7472 | 13.6229 | 13.5278 | 13.408 | 13.1842 | 12.8962 | 12.637 | 12.3868 | 12.1451 | 11.8407 | 11.5688 | 11.2951 | 10.1136 | 9.8767 | 9.6099 | 4.6381 | -1.0283 | -7.6229
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Leading the Way | Headroom (MW) | Thermal | 13.8463 | 13.6924 | 13.6211 | 13.6142 | 13.5792 | 13.4945 | 13.3945 | 13.3273 | 13.2455 | 13.2496 | 13.2122 | 13.2008 | 13.192 | 11.9108 | 10.2086 | 7.5955 | 2.2222 | -6.1355 | -11.1739
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | Steady Progression | Headroom (MW) | N/A | 13.8389 | 13.8077 | 13.7539 | 13.7541 | 13.7483 | 13.7015 | 13.6678 | 13.6349 | 13.5909 | 13.5663 | 13.5077 | 13.4636 | 13.4338 | 13.4024 | 13.3844 | 13.3641 | 13.4732 | 12.2408 | 10.5547
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | System Transformation | Headroom (MW) | N/A | 13.8317 | 13.8016 | 13.7294 | 13.7183 | 13.6742 | 13.5775 | 13.4413 | 13.3171 | 13.1508 | 13.0291 | 12.8656 | 12.7346 | 12.6175 | 12.5177 | 12.4363 | 12.3446 | 9.5672 | 5.24 | 0.67349
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | 51.9963 | -0.9758 | WPD Best View | Headroom (MW) | Thermal | 13.8463 | 13.6924 | 13.6211 | 13.6142 | 13.5792 | 13.4945 | 13.3945 | 13.3273 | 13.2455 | 13.2496 | 13.2122 | 13.2008 | 13.192 | 11.9108 | 10.2086 | 7.5955 | 2.2222 | -6.1355 | -11.1739
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Consumer Transformation | Headroom (MW) | Thermal | 3.5668 | 3.5447 | 3.4819 | 3.4401 | 3.389 | 3.329 | 3.2347 | 3.1531 | 3.0843 | 3.0188 | 2.9374 | 2.87 | 2.8165 | 1.8401 | 1.8073 | 0.054854 | -2.6562 | -8.5324 | -11.0472
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Leading the Way | Headroom (MW) | Thermal | 3.5851 | 3.5651 | 3.5318 | 3.5092 | 3.486 | 3.4765 | 3.4577 | 3.4529 | 3.4532 | 3.4749 | 3.5058 | 3.5412 | 2.3007 | 2.3318 | 0.67989 | -1.8503 | -9.3399 | -14.1188 | -21.1831
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | Steady Progression | Headroom (MW) | N/A | 3.579 | 3.562 | 3.5161 | 3.499 | 3.4824 | 3.467 | 3.4437 | 3.4294 | 3.4103 | 3.3978 | 3.3793 | 3.3664 | 3.3676 | 3.3668 | 3.3748 | 3.3938 | 3.5419 | 2.3587 | 0.88437
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | System Transformation | Headroom (MW) | Thermal | 3.5786 | 3.553 | 3.5119 | 3.4799 | 3.4448 | 3.409 | 3.3584 | 3.3073 | 3.2545 | 3.205 | 3.1466 | 3.1121 | 3.0931 | 3.0745 | 3.0754 | 1.3819 | 0.19339 | -5.0536 | -7.091
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | 51.9284 | -0.9916 | WPD Best View | Headroom (MW) | Thermal | 3.5851 | 3.5651 | 3.5318 | 3.5092 | 3.486 | 3.4765 | 3.4577 | 3.4529 | 3.4532 | 3.4749 | 3.5058 | 3.5412 | 2.3007 | 2.3318 | 0.67989 | -1.8503 | -9.3399 | -14.1188 | -21.1831
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Consumer Transformation | Headroom (MW) | N/A | 15.8017 | 15.7798 | 15.7109 | 15.8625 | 15.8231 | 15.7852 | 15.7423 | 15.727 | 15.6997 | 15.6734 | 15.6387 | 15.6022 | 15.5654 | 15.5292 | 15.5016 | 15.4709 | 15.2316 | 14.7369 | 14.2054
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Leading the Way | Headroom (MW) | N/A | 15.8256 | 15.808 | 15.7446 | 15.9633 | 15.9271 | 15.8865 | 15.8167 | 15.7915 | 15.7663 | 15.7275 | 15.6662 | 15.5802 | 15.4933 | 15.4039 | 15.3669 | 15.3302 | 15.0351 | 14.7301 | 14.426
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | Steady Progression | Headroom (MW) | N/A | 15.7838 | 15.7565 | 15.682 | 15.7828 | 15.7451 | 15.7093 | 15.684 | 15.6586 | 15.6314 | 15.6026 | 15.5728 | 15.5438 | 15.5118 | 15.4809 | 15.4489 | 15.4176 | 15.2435 | 15.0829 | 14.8501
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | System Transformation | Headroom (MW) | N/A | 15.8016 | 15.7797 | 15.7108 | 15.8622 | 15.8225 | 15.7842 | 15.7464 | 15.7303 | 15.709 | 15.681 | 15.6551 | 15.6224 | 15.5891 | 15.557 | 15.5254 | 15.4915 | 15.329 | 15.1301 | 14.9141
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | 52.0409 | -0.7715 | WPD Best View | Headroom (MW) | N/A | 15.8256 | 15.8093 | 15.7458 | 15.9677 | 15.9316 | 15.891 | 15.8584 | 15.8332 | 15.8243 | 15.7855 | 15.7462 | 15.7084 | 15.6722 | 15.6374 | 15.6004 | 15.5637 | 15.3656 | 15.1327 | 14.6189
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Consumer Transformation | Headroom (MW) | N/A | 15.3763 | 15.3067 | 15.1488 | 14.9922 | 14.8081 | 14.5727 | 14.2517 | 13.9397 | 13.6224 | 13.2794 | 12.8974 | 12.5669 | 12.2521 | 11.9421 | 11.647 | 11.3343 | 9.8241 | 8.1662 | 6.5426
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Leading the Way | Headroom (MW) | N/A | 15.4135 | 15.3744 | 15.2588 | 15.1631 | 15.0335 | 14.923 | 14.7561 | 14.5877 | 14.3956 | 14.1984 | 14.0076 | 13.9248 | 13.8568 | 13.811 | 13.7521 | 13.6786 | 13.0575 | 10.8919 | 9.8733
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | Steady Progression | Headroom (MW) | N/A | 15.3972 | 15.3573 | 15.2653 | 15.221 | 15.1733 | 15.1217 | 15.0709 | 15.0165 | 14.95 | 14.8847 | 14.806 | 14.7412 | 14.6773 | 14.6201 | 14.5615 | 14.5051 | 14.4717 | 14.3911 | 13.9532
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | System Transformation | Headroom (MW) | N/A | 15.3943 | 15.3537 | 15.2447 | 15.174 | 15.083 | 14.9858 | 14.8396 | 14.6868 | 14.518 | 14.3468 | 14.1715 | 14.019 | 13.8705 | 13.7407 | 13.6119 | 13.4882 | 13.0739 | 12.5549 | 11.8745
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | 52.0494 | -0.8255 | WPD Best View | Headroom (MW) | N/A | 15.4135 | 15.3744 | 15.2588 | 15.1631 | 15.0335 | 14.923 | 14.7561 | 14.5877 | 14.3956 | 14.1984 | 14.0076 | 13.9248 | 13.8568 | 13.811 | 13.7521 | 13.6786 | 13.0575 | 10.8919 | 9.8733
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Consumer Transformation | Headroom (MW) | N/A | 15.1136 | 15.131 | 15.0329 | 14.8914 | 14.7119 | 14.4917 | 14.1822 | 13.8843 | 13.5827 | 13.2521 | 12.8853 | 12.577 | 12.2674 | 11.9821 | 11.7063 | 11.4149 | 10.0508 | 6.2735 | 4.7355
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Leading the Way | Headroom (MW) | N/A | 15.1202 | 15.1351 | 15.0801 | 15.0341 | 14.9736 | 14.8752 | 14.7091 | 14.5591 | 14.3841 | 14.218 | 14.0302 | 13.964 | 13.9201 | 13.7742 | 13.7627 | 13.7505 | 11.9554 | 11.0711 | 7.8571
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | Steady Progression | Headroom (MW) | N/A | 15.1086 | 15.1117 | 15.0503 | 15.0208 | 14.9958 | 14.9682 | 14.9194 | 14.8909 | 14.8399 | 14.779 | 14.7015 | 14.6328 | 14.5805 | 14.5247 | 14.472 | 14.4279 | 14.4469 | 14.3136 | 13.868
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | System Transformation | Headroom (MW) | N/A | 15.1136 | 15.1308 | 15.0724 | 15.0503 | 14.9829 | 14.8901 | 14.7313 | 14.5852 | 14.4175 | 14.2497 | 14.0769 | 13.9264 | 13.7866 | 13.6606 | 13.5462 | 13.427 | 13.113 | 11.3452 | 10.6918
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | 52.019 | -0.7948 | WPD Best View | Headroom (MW) | N/A | 15.1202 | 15.1561 | 15.1012 | 15.0824 | 14.9736 | 14.8752 | 14.7091 | 14.5591 | 14.3841 | 14.218 | 14.0302 | 13.964 | 13.9201 | 13.8863 | 13.8497 | 13.7823 | 11.9554 | 11.0711 | 7.8571
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Consumer Transformation | Headroom (MW) | Thermal | 7.0166 | 6.9824 | 6.9398 | 6.9062 | 6.8742 | 6.8179 | 6.7416 | 6.6937 | 6.6505 | 6.6099 | 6.5829 | 6.5633 | 6.5685 | 6.5672 | 6.5742 | 6.5512 | 4.8738 | 0.54865 | -3.8982
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Leading the Way | Headroom (MW) | Thermal | 7.0244 | 7.0166 | 6.9776 | 6.9792 | 6.982 | 6.9823 | 6.9815 | 7.0095 | 7.0558 | 7.0756 | 7.0473 | 7.0103 | 6.9742 | 6.9262 | 4.1034 | 4.1412 | 1.4578 | -3.0628 | -7.4457
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | Steady Progression | Headroom (MW) | N/A | 7.02 | 7.0042 | 6.9711 | 6.9485 | 6.9278 | 6.9178 | 6.9101 | 6.896 | 6.8955 | 6.8891 | 6.8816 | 6.8842 | 6.8977 | 6.926 | 6.9492 | 6.9973 | 7.0054 | 6.957 | 5.9596
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | System Transformation | Headroom (MW) | N/A | 7.0189 | 7.0024 | 6.9489 | 6.9297 | 6.901 | 6.8646 | 6.8168 | 6.781 | 6.7408 | 6.6984 | 6.6646 | 6.6515 | 6.6608 | 6.679 | 6.7141 | 6.7514 | 5.7494 | 3.062 | 0.052075
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | 52.048 | -0.9047 | WPD Best View | Headroom (MW) | Thermal | 7.0244 | 7.0166 | 6.9776 | 6.9792 | 6.982 | 6.9823 | 6.9815 | 7.0095 | 7.0558 | 7.1157 | 7.1571 | 7.1624 | 7.1733 | 7.1793 | 4.1034 | 4.1412 | 1.4578 | -3.0628 | -7.4457
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Consumer Transformation | Headroom (MW) | Thermal | 7.5123 | 7.4739 | 7.3974 | 7.318 | 7.2201 | 7.0908 | 6.898 | 6.7215 | 6.5255 | 6.3599 | 5.2237 | 5.0245 | 4.8216 | 3.7072 | 3.5586 | 1.7156 | -2.4243 | -11.4524 | -19.5634
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Leading the Way | Headroom (MW) | Thermal | 7.5342 | 7.5174 | 7.4642 | 7.4132 | 7.3542 | 7.2892 | 7.1886 | 7.0939 | 6.9736 | 6.9139 | 6.8297 | 6.8096 | 4.5838 | 4.5551 | 1.9967 | 0.2771 | -8.4076 | -17.6469 | -25.3514
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | Steady Progression | Headroom (MW) | N/A | 7.5244 | 7.5038 | 7.4655 | 7.4403 | 7.4233 | 7.3975 | 7.3699 | 7.3536 | 7.3191 | 7.2891 | 7.2496 | 7.2236 | 7.2016 | 7.1836 | 7.1615 | 7.1528 | 5.9105 | 5.897 | 4.4015
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | System Transformation | Headroom (MW) | Thermal | 7.526 | 7.5069 | 7.4554 | 7.4123 | 7.3638 | 7.3105 | 7.2322 | 7.1534 | 7.0615 | 6.9743 | 6.8668 | 6.8031 | 6.7376 | 6.6695 | 6.614 | 4.8678 | 2.4989 | -2.8696 | -8.347
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | 51.9518 | -0.8839 | WPD Best View | Headroom (MW) | Thermal | 7.5342 | 7.5174 | 7.4642 | 7.4132 | 7.3542 | 7.2892 | 7.1886 | 7.0939 | 6.9736 | 6.9139 | 6.8297 | 6.8096 | 4.5838 | 4.5551 | 1.9967 | 0.2771 | -8.4076 | -17.6469 | -25.3514
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Consumer Transformation | Headroom (MW) | Thermal | 28.7991 | 28.6015 | 27.8302 | 27.5081 | 26.7166 | 25.4868 | 23.7762 | 22.202 | 20.5686 | 18.0657 | 15.3013 | 11.3102 | 7.7257 | 4.1105 | 0.76568 | -6.4197 | -32.7025 | -66.489 | -96.6409
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Leading the Way | Headroom (MW) | Thermal | 28.8567 | 28.457 | 27.8546 | 27.8035 | 27.5269 | 27.1969 | 22.3493 | 21.9306 | 21.1911 | 20.7316 | 20.02 | 17.6195 | 15.9082 | 11.6658 | 2.4501 | -7.6089 | -39.8537 | -71.8845 | -100.6433
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | Steady Progression | Headroom (MW) | N/A | 28.8547 | 28.6798 | 28.0656 | 27.8679 | 27.573 | 27.2829 | 26.9442 | 26.6642 | 26.3674 | 26.1221 | 25.8451 | 25.5916 | 25.3119 | 25.0278 | 24.7908 | 24.5772 | 23.1317 | 19.3754 | 14.3577
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | System Transformation | Headroom (MW) | Thermal | 28.8304 | 28.7193 | 28.0376 | 27.84 | 27.4421 | 27.0279 | 26.2376 | 25.3446 | 24.3496 | 23.463 | 22.564 | 21.7739 | 21.0795 | 20.4306 | 18.9505 | 18.4184 | 8.0044 | -8.5173 | -25.476
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | 52.6883 | -1.3271 | WPD Best View | Headroom (MW) | Thermal | 39.4971 | 39.3905 | 38.7189 | 38.5325 | 38.144 | 37.7417 | 36.9803 | 36.1145 | 35.1623 | 34.3308 | 33.4836 | 32.7591 | 32.1246 | 31.5333 | 30.0828 | 29.5285 | 16.3215 | -0.87224 | -18.2861
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Consumer Transformation | Headroom (MW) | N/A | 15.3209 | 15.358 | 15.2946 | 15.2683 | 15.1697 | 14.9247 | 14.5859 | 14.2225 | 13.8165 | 13.3862 | 12.8997 | 11.9175 | 11.329 | 10.7211 | 10.1311 | 8.6805 | 6.6356 | 4.1807 | 1.463
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Leading the Way | Headroom (MW) | N/A | 15.3247 | 15.3721 | 15.3125 | 15.2664 | 15.249 | 15.2343 | 14.8796 | 14.7581 | 14.3938 | 14.0399 | 13.6499 | 12.3832 | 11.8758 | 11.3658 | 10.9222 | 10.7316 | 7.1435 | 6.3199 | 5.4245
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | Steady Progression | Headroom (MW) | N/A | 15.3182 | 15.3348 | 15.2683 | 15.2355 | 15.2103 | 15.1854 | 15.1422 | 15.1174 | 15.088 | 15.0651 | 15.0364 | 15.0229 | 14.936 | 14.8404 | 14.7297 | 14.6165 | 14.0557 | 13.7828 | 13.2558
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | System Transformation | Headroom (MW) | N/A | 15.3209 | 15.3579 | 15.2945 | 15.2682 | 15.2435 | 15.2259 | 15.1981 | 15.0524 | 14.881 | 14.7057 | 14.5232 | 14.2829 | 14.0844 | 13.8656 | 13.6482 | 13.4419 | 12.6965 | 12.1552 | 10.2572
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | 52.7138 | -1.3478 | WPD Best View | Headroom (MW) | N/A | 15.3209 | 15.3579 | 15.2945 | 15.2682 | 15.2435 | 15.2259 | 15.1981 | 15.0524 | 14.881 | 14.7057 | 14.5232 | 14.2829 | 14.0844 | 13.8656 | 13.6482 | 13.4419 | 12.6965 | 12.1552 | 10.2572
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Consumer Transformation | Headroom (MW) | Thermal | 11.3538 | 11.4467 | 11.336 | 11.2896 | 11.181 | 11.0598 | 10.9013 | 10.7634 | 10.6214 | 10.4958 | 10.3548 | 9.304 | 9.205 | 9.0942 | 9.043 | 7.0887 | 3.0812 | -2.803 | -7.5841
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Leading the Way | Headroom (MW) | Thermal | 11.3602 | 11.1653 | 11.0952 | 11.1167 | 11.0626 | 11.0203 | 7.5936 | 7.5554 | 7.514 | 7.5185 | 7.5045 | 7.5091 | 7.514 | 6.5991 | 4.9216 | 4.8999 | -2.0432 | -6.6815 | -11.9251
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | Steady Progression | Headroom (MW) | N/A | 11.3576 | 11.4231 | 11.3305 | 11.2931 | 11.2421 | 11.1974 | 11.1405 | 11.0928 | 11.0477 | 11.0054 | 10.9563 | 10.9201 | 10.8909 | 10.879 | 10.8819 | 10.8774 | 11.0654 | 11.1519 | 10.6881
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | System Transformation | Headroom (MW) | N/A | 11.356 | 11.468 | 11.366 | 11.338 | 11.2504 | 11.1755 | 11.0802 | 10.9763 | 10.8712 | 10.7663 | 10.6846 | 10.6086 | 10.5562 | 10.5257 | 10.5147 | 10.5074 | 9.4316 | 5.565 | 3.5397
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | 52.6882 | -1.3276 | WPD Best View | Headroom (MW) | N/A | 11.3574 | 11.4723 | 11.3753 | 11.3553 | 11.2768 | 11.214 | 11.135 | 11.0521 | 10.9699 | 10.8984 | 10.8447 | 10.8029 | 10.7799 | 10.7886 | 10.7917 | 10.7841 | 7.271 | 4.4227 | 0.91883
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Consumer Transformation | Headroom (MW) | Thermal | 7.115 | 7.0173 | 6.8498 | 6.7777 | 6.6317 | 6.434 | 6.1605 | 5.9138 | 5.6569 | 5.391 | 5.0823 | 4.8082 | 4.5418 | 3.3698 | 3.1909 | 2.0516 | -1.4793 | -4.1413 | -8.1703
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Leading the Way | Headroom (MW) | Thermal | 7.1328 | 7.0801 | 6.9532 | 6.9817 | 6.9179 | 6.828 | 6.7093 | 6.6094 | 6.4669 | 6.3699 | 6.2333 | 6.1359 | 6.037 | 5.9707 | 4.2903 | 2.5921 | 0.099928 | -4.9463 | -9.9401
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | Steady Progression | Headroom (MW) | N/A | 7.137 | 7.0699 | 6.9585 | 6.9384 | 6.8846 | 6.8353 | 6.7838 | 6.7397 | 6.6897 | 6.6331 | 6.5685 | 6.5196 | 6.4942 | 6.4688 | 6.4558 | 6.4593 | 6.6743 | 6.8197 | 5.0437
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | System Transformation | Headroom (MW) | N/A | 7.1244 | 7.0609 | 6.9202 | 6.8972 | 6.8166 | 6.7174 | 6.5679 | 6.4339 | 6.2801 | 6.1395 | 5.982 | 5.872 | 5.7687 | 5.6922 | 5.6505 | 5.62 | 4.3288 | 3.9304 | 1.8134
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | 52.6395 | -1.2715 | WPD Best View | Headroom (MW) | N/A | 7.1259 | 7.0635 | 6.926 | 6.9067 | 6.8311 | 6.7382 | 6.5971 | 6.4742 | 6.3343 | 6.2104 | 6.0725 | 5.9845 | 5.9031 | 5.8473 | 5.821 | 5.7894 | 4.3586 | 3.7745 | 1.5512
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Consumer Transformation | Headroom (MW) | N/A | 14.5523 | 14.5216 | 14.4611 | 14.4287 | 14.397 | 14.3659 | 14.3343 | 14.305 | 14.275 | 14.248 | 14.2187 | 14.1965 | 14.162 | 14.1371 | 14.1179 | 14.0986 | 13.9474 | 13.7254 | 13.4386
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Leading the Way | Headroom (MW) | N/A | 14.5526 | 14.5219 | 14.4618 | 14.4295 | 14.3983 | 14.3678 | 14.0577 | 14.0293 | 13.9975 | 13.9718 | 13.9389 | 13.8893 | 13.8291 | 13.7622 | 13.7444 | 13.7252 | 11.7163 | 11.4691 | 11.2251
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | Steady Progression | Headroom (MW) | N/A | 14.552 | 14.521 | 14.4601 | 14.4271 | 14.3946 | 14.3625 | 14.3307 | 14.2997 | 14.2691 | 14.2392 | 14.2096 | 14.184 | 14.1564 | 14.1297 | 14.1037 | 14.0781 | 13.9604 | 13.8463 | 13.6826
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | System Transformation | Headroom (MW) | N/A | 14.5522 | 14.5214 | 14.4608 | 14.4282 | 14.3962 | 14.3646 | 14.3335 | 14.3032 | 14.2736 | 14.2445 | 14.2162 | 14.1941 | 14.1684 | 14.1438 | 14.1203 | 14.0976 | 13.9953 | 13.8796 | 13.7383
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | 52.699 | -1.3464 | WPD Best View | Headroom (MW) | N/A | 14.5522 | 14.5214 | 14.4608 | 14.4282 | 14.3962 | 14.3646 | 14.3336 | 14.3033 | 14.2737 | 14.2447 | 14.2163 | 14.1943 | 14.1687 | 14.1442 | 14.1207 | 14.0979 | 13.996 | 13.8862 | 13.7619
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Consumer Transformation | Headroom (MW) | Thermal | 18.1691 | 18.1018 | 17.9702 | 18.0106 | 17.7598 | 17.3909 | 16.8789 | 16.4013 | 15.934 | 15.4418 | 13.9722 | 13.4785 | 12.9784 | 12.4822 | 11.0898 | 10.5723 | 4.5182 | -1.6748 | -6.7946
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Leading the Way | Headroom (MW) | Thermal | 18.1694 | 18.0811 | 17.9499 | 18.0069 | 17.9372 | 17.8388 | 17.3361 | 17.278 | 17.1772 | 17.0548 | 16.8571 | 16.6759 | 15.5675 | 15.3625 | 13.4711 | 13.2477 | 8.5025 | 2.5092 | -1.3002
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | Steady Progression | Headroom (MW) | N/A | 18.169 | 18.1016 | 17.97 | 17.9763 | 17.9063 | 17.8373 | 17.7549 | 17.6929 | 17.6252 | 17.5629 | 17.4951 | 17.3632 | 17.241 | 17.1272 | 17.0309 | 16.9249 | 15.8762 | 15.5494 | 14.1431
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | System Transformation | Headroom (MW) | N/A | 18.1691 | 18.1017 | 17.9701 | 18.0104 | 17.9402 | 17.8709 | 17.611 | 17.3403 | 17.0305 | 16.7211 | 16.4105 | 16.1316 | 15.8666 | 15.6186 | 15.386 | 15.1384 | 11.9074 | 9.5642 | 7.1702
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | 52.7266 | -1.3751 | WPD Best View | Headroom (MW) | N/A | 18.1691 | 18.1018 | 17.9702 | 18.0107 | 17.9406 | 17.8716 | 17.626 | 17.3615 | 17.0596 | 16.7601 | 16.4612 | 16.1955 | 15.9435 | 15.7079 | 15.4844 | 15.2352 | 11.9176 | 9.4614 | 6.9918
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Consumer Transformation | Headroom (MW) | Thermal | 3.8148 | 3.7774 | 3.6987 | 3.6466 | 3.5949 | 3.5078 | 3.3825 | 3.2836 | 3.1761 | 3.155 | 3.102 | 2.1648 | 1.2183 | 1.1554 | 1.1259 | 1.0729 | -1.5749 | -7.9852 | -12.2887
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Leading the Way | Headroom (MW) | Thermal | 3.8227 | 3.806 | 3.7614 | 3.7362 | 3.7176 | 3.7074 | 3.674 | 3.6632 | 3.6636 | 3.7841 | 3.8758 | 4.0024 | 4.1187 | 4.1642 | 1.5758 | -1.0384 | -3.6165 | -7.866 | -11.916
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | Steady Progression | Headroom (MW) | N/A | 3.8282 | 3.7996 | 3.7579 | 3.7279 | 3.7082 | 3.6824 | 3.6574 | 3.642 | 3.6192 | 3.6401 | 3.6618 | 3.698 | 3.7359 | 3.7451 | 3.7606 | 3.7888 | 3.9198 | 4.0729 | 3.8749
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | System Transformation | Headroom (MW) | Thermal | 3.8189 | 3.7962 | 3.741 | 3.6958 | 3.6571 | 3.6189 | 3.549 | 3.4841 | 3.4075 | 3.4161 | 3.4273 | 3.4663 | 3.5075 | 3.5099 | 3.5209 | 3.5427 | 3.5747 | -0.11284 | -2.7636
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | 52.6763 | -1.3617 | WPD Best View | Headroom (MW) | Thermal | 3.8189 | 3.7962 | 3.741 | 3.6958 | 3.6571 | 3.6189 | 3.549 | 3.4841 | 3.4075 | 3.4161 | 3.4273 | 3.4663 | 3.5075 | 3.5099 | 3.5209 | 3.5427 | 3.5747 | -0.11284 | -2.7636
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Consumer Transformation | Headroom (MW) | Thermal | 6.1658 | 6.1167 | 6.025 | 5.9427 | 5.8976 | 5.7961 | 5.6345 | 5.5037 | 5.3606 | 4.3104 | 4.1365 | 3.9919 | 2.9147 | 2.7761 | 1.7534 | -0.21906 | -5.2726 | -11.8575 | -16.2678
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Leading the Way | Headroom (MW) | Thermal | 6.1822 | 6.1464 | 6.0832 | 6.0493 | 6.0535 | 6.0324 | 5.9775 | 5.9457 | 5.9113 | 5.9237 | 5.8937 | 4.9522 | 4.8914 | 3.6405 | 2.7166 | -0.86032 | -5.7085 | -12.1748 | -17.5119
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | Steady Progression | Headroom (MW) | N/A | 6.1817 | 6.1422 | 6.0861 | 6.0574 | 6.0431 | 6.0166 | 5.9858 | 5.9557 | 5.9283 | 5.8982 | 5.8624 | 5.8407 | 5.8241 | 5.8065 | 5.7944 | 5.7953 | 5.4363 | 3.2127 | 2.941
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | System Transformation | Headroom (MW) | Thermal | 6.1794 | 6.1372 | 6.0662 | 6.019 | 5.9915 | 5.944 | 5.8513 | 5.768 | 5.6772 | 5.5971 | 5.5086 | 5.4425 | 5.3874 | 5.3517 | 4.394 | 4.36 | 1.6078 | -1.2263 | -3.887
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | 52.629 | -1.3777 | WPD Best View | Headroom (MW) | Thermal | 6.1794 | 6.1372 | 6.0662 | 6.019 | 5.9915 | 5.944 | 5.8513 | 5.768 | 5.6772 | 5.5971 | 5.5086 | 5.4425 | 5.3874 | 5.3517 | 4.394 | 4.36 | 1.6078 | -1.2263 | -3.887
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Consumer Transformation | Headroom (MW) | Thermal | 4.2366 | 4.1913 | 4.124 | 4.0731 | 4.0141 | 3.9369 | 3.8273 | 3.7379 | 3.6572 | 3.5668 | 3.4644 | 3.378 | 3.3057 | 2.3038 | 2.2429 | 2.1641 | -0.62882 | -4.004 | -8.5077
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Leading the Way | Headroom (MW) | Thermal | 4.2415 | 4.2133 | 4.1667 | 4.146 | 4.12 | 4.0972 | 4.0507 | 4.0207 | 3.9961 | 3.9982 | 3.9961 | 4.0006 | 4.004 | 2.7301 | 2.7374 | 1.0226 | -4.0184 | -8.5849 | -12.7703
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | Steady Progression | Headroom (MW) | N/A | 4.2403 | 4.2167 | 4.1634 | 4.1415 | 4.1131 | 4.0953 | 4.0782 | 4.0532 | 4.0294 | 4.0073 | 3.9843 | 3.9724 | 3.9627 | 3.9603 | 3.9631 | 3.9662 | 4.0728 | 2.8689 | 2.6578
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | System Transformation | Headroom (MW) | Thermal | 4.2386 | 4.2051 | 4.1482 | 4.1124 | 4.0759 | 4.0398 | 3.976 | 3.9158 | 3.8577 | 3.8019 | 3.741 | 3.7052 | 3.6695 | 3.6523 | 3.6451 | 3.6396 | 2.3916 | -0.34337 | -3.415
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | 52.7825 | -1.3794 | WPD Best View | Headroom (MW) | Thermal | 4.2393 | 4.2063 | 4.151 | 4.1147 | 4.0733 | 4.0304 | 3.9563 | 3.885 | 3.8253 | 3.7644 | 3.696 | 3.6564 | 3.6163 | 3.5843 | 3.5681 | 3.5433 | 2.1654 | -1.9669 | -3.8503
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Consumer Transformation | Headroom (MW) | Thermal | 1.8316 | 1.669 | 1.3795 | 1.1288 | 0.95738 | 0.68367 | 0.23688 | -0.22646 | -0.68054 | -1.0471 | -1.2345 | -1.5751 | -2.8455 | -3.1685 | -3.4498 | -3.8002 | -8.3308 | -16.0378 | -23.8665
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Leading the Way | Headroom (MW) | Thermal | 1.8836 | 1.8032 | 1.6211 | 1.5095 | 1.5157 | 1.5237 | 1.4412 | 1.3381 | 1.2157 | 1.2287 | 1.5274 | 1.5504 | 1.5914 | 1.6217 | 1.6557 | -1.0982 | -7.1961 | 12.0496 | 6.5596
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | Steady Progression | Headroom (MW) | Thermal | 1.8702 | 1.7815 | 1.6064 | 1.5088 | 1.4793 | 1.4466 | -5.7782 | -14.0622 | -21.3276 | -28.5681 | -34.9032 | -40.7926 | -44.9087 | -49.0077 | -52.6379 | -56.7206 | -72.6059 | -90.9222 | -101.8704
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | System Transformation | Headroom (MW) | Thermal | 1.8637 | 1.7625 | 1.5462 | 1.3876 | 1.312 | 1.2103 | 0.99963 | 0.73084 | 0.43135 | 0.21843 | 0.23543 | 0.09406 | -0.018915 | -0.12876 | -0.16126 | -0.23847 | -0.66499 | -5.0118 | -9.0079
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | 52.5289 | -1.396 | WPD Best View | Headroom (MW) | Thermal | 1.8638 | 1.7625 | 1.5483 | 1.3929 | 1.3211 | 1.2239 | -1.0205 | -3.3309 | -5.6709 | -7.9238 | -9.6521 | -11.3943 | -12.5368 | -13.6698 | -14.7144 | -15.8321 | -20.7579 | -28.0529 | -33.8527
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Consumer Transformation | Headroom (MW) | N/A | 118.2033 | 118.1655 | 117.423 | 117.2475 | 116.8876 | 116.5892 | 115.5146 | 114.573 | 113.0216 | 111.0344 | 108.4704 | 105.9502 | 103.3217 | 100.8327 | 98.4988 | 95.9827 | 83.7578 | 70.5981 | 57.633
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Leading the Way | Headroom (MW) | N/A | 118.2274 | 118.1391 | 117.4194 | 117.1159 | 116.7903 | 116.5154 | 113.1515 | 112.8339 | 111.6042 | 111.3027 | 109.8665 | 108.3411 | 106.6332 | 104.7025 | 104.3216 | 103.8941 | 90.4464 | 82.5965 | 75.3676
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | Steady Progression | Headroom (MW) | N/A | 118.185 | 118.0447 | 117.2837 | 117.0232 | 116.6589 | 116.318 | 115.4041 | 115.0479 | 114.3329 | 113.9847 | 113.5083 | 112.6771 | 111.8933 | 111.1586 | 110.8657 | 110.5614 | 103.488 | 99.7158 | 94.2542
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | System Transformation | Headroom (MW) | N/A | 118.2031 | 118.165 | 117.422 | 117.2459 | 116.8841 | 116.583 | 115.8083 | 115.4796 | 114.8068 | 114.4753 | 113.7677 | 112.8837 | 112.006 | 111.2145 | 110.7365 | 110.092 | 106.1314 | 100.8065 | 94.5973
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | 52.623 | -1.1416 | WPD Best View | Headroom (MW) | N/A | 118.2032 | 118.1651 | 117.4222 | 117.2461 | 116.8852 | 116.5853 | 116.2438 | 115.2494 | 113.9396 | 112.0604 | 109.9971 | 107.7527 | 105.4398 | 103.2004 | 101.1227 | 98.8687 | 88.2775 | 76.7203 | 64.9728
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Consumer Transformation | Headroom (MW) | N/A | 16.3083 | 16.5696 | 16.4815 | 16.585 | 16.5453 | 16.5379 | 16.4667 | 16.1547 | 15.8525 | 15.4872 | 15.0872 | 14.7314 | 14.3501 | 14.0335 | 13.7111 | 13.3624 | 11.4141 | 8.9958 | 6.4894
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Leading the Way | Headroom (MW) | N/A | 16.3103 | 16.6645 | 16.5772 | 16.7087 | 16.6806 | 16.6642 | 16.0375 | 16.0143 | 15.9348 | 15.9113 | 15.7898 | 15.5267 | 15.221 | 14.8671 | 14.8574 | 14.845 | 11.3018 | 10.3921 | 9.4371
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | Steady Progression | Headroom (MW) | N/A | 16.3066 | 16.4833 | 16.3944 | 16.4533 | 16.4277 | 16.4026 | 16.3646 | 16.3424 | 16.3142 | 16.2915 | 16.2626 | 16.2421 | 16.2194 | 16.1994 | 16.1752 | 16.1527 | 15.0633 | 14.8517 | 14.2375
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | System Transformation | Headroom (MW) | N/A | 16.3082 | 16.5693 | 16.4809 | 16.584 | 16.5435 | 16.535 | 16.5139 | 16.5057 | 16.4925 | 16.4695 | 16.4012 | 16.2493 | 16.1101 | 15.9924 | 15.896 | 15.7759 | 15.4216 | 14.6122 | 13.3725
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | 52.61 | -1.1626 | WPD Best View | Headroom (MW) | N/A | 16.3082 | 16.5694 | 16.4811 | 16.5843 | 16.5441 | 16.5359 | 16.5226 | 16.5153 | 16.4594 | 16.2298 | 16.0077 | 15.8161 | 15.6291 | 15.4576 | 15.2952 | 15.0973 | 14.1115 | 12.6279 | 10.8297
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Consumer Transformation | Headroom (MW) | N/A | 14.4614 | 14.3836 | 14.2291 | 14.1543 | 14.0729 | 14.0522 | 13.9751 | 13.9147 | 13.8063 | 13.6095 | 13.1862 | 12.7872 | 12.3847 | 12.0702 | 11.7819 | 11.4116 | 9.8389 | 7.9098 | 5.9409
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Leading the Way | Headroom (MW) | N/A | 14.4629 | 14.3639 | 14.2115 | 14.1123 | 14.0327 | 14.0356 | 13.5655 | 13.5169 | 13.4044 | 13.357 | 13.2136 | 12.912 | 12.5708 | 12.2552 | 12.2822 | 12.2426 | 9.5243 | 8.5779 | 7.634
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | Steady Progression | Headroom (MW) | N/A | 14.4602 | 14.3812 | 14.2249 | 14.1425 | 14.0593 | 14.0205 | 13.9501 | 13.881 | 13.811 | 13.7451 | 13.6734 | 13.611 | 13.5453 | 13.5126 | 13.4829 | 13.4274 | 13.0467 | 12.6523 | 12.0005
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | System Transformation | Headroom (MW) | N/A | 14.4614 | 14.3835 | 14.2287 | 14.1537 | 14.0718 | 14.0505 | 14.0174 | 13.9553 | 13.8937 | 13.8338 | 13.7781 | 13.726 | 13.6699 | 13.6622 | 13.6597 | 13.5579 | 13.117 | 12.33 | 11.2931
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | 52.6304 | -1.1877 | WPD Best View | Headroom (MW) | N/A | 14.4614 | 14.3835 | 14.2288 | 14.1539 | 14.0721 | 14.0509 | 14.0252 | 13.9636 | 13.9062 | 13.8472 | 13.7927 | 13.5558 | 13.2833 | 13.0799 | 12.8942 | 12.6359 | 11.6818 | 10.3477 | 8.8575
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Consumer Transformation | Headroom (MW) | N/A | 21.6927 | 21.6297 | 21.5114 | 21.4777 | 21.4389 | 21.3731 | 21.2845 | 21.2255 | 21.1458 | 21.0916 | 21.0043 | 20.8762 | 20.7022 | 20.5271 | 20.3495 | 20.1348 | 18.8737 | 17.3485 | 15.8273
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Leading the Way | Headroom (MW) | N/A | 21.6945 | 21.6222 | 21.5063 | 21.4734 | 21.4451 | 21.3793 | 20.9461 | 20.8876 | 20.8116 | 20.76 | 20.6794 | 20.5644 | 20.444 | 20.3134 | 20.2744 | 20.2347 | 17.9991 | 17.5119 | 16.9941
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | Steady Progression | Headroom (MW) | N/A | 21.6912 | 21.628 | 21.5076 | 21.4628 | 21.4161 | 21.3503 | 21.2778 | 21.2169 | 21.1535 | 21.094 | 21.0319 | 20.9737 | 20.9147 | 20.8584 | 20.8032 | 20.7494 | 19.5157 | 19.244 | 18.8246
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | System Transformation | Headroom (MW) | N/A | 21.6926 | 21.6296 | 21.511 | 21.4772 | 21.4379 | 21.3714 | 21.3032 | 21.2426 | 21.1834 | 21.126 | 21.0688 | 21.0114 | 20.9532 | 20.8998 | 20.8495 | 20.8015 | 20.5381 | 19.9336 | 19.1381
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | 52.6265 | -1.1645 | WPD Best View | Headroom (MW) | N/A | 21.6927 | 21.6297 | 21.5112 | 21.4775 | 21.4385 | 21.3724 | 21.3081 | 21.2485 | 21.1926 | 21.1374 | 21.0041 | 20.8255 | 20.6426 | 20.461 | 20.2771 | 20.0617 | 18.8531 | 17.4007 | 15.9102
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Consumer Transformation | Headroom (MW) | Fault level | 0.11639 | 0.032261 | -0.094907 | -0.25789 | -0.44566 | -0.74163 | -1.1675 | -1.5921 | -2.024 | -2.4548 | -2.9359 | -3.3861 | -3.8489 | -4.2997 | -4.7631 | -5.2506 | -7.7029 | -9.9964 | -12.0503
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Leading the Way | Headroom (MW) | Fault level | 0.14322 | 0.098837 | 0.043837 | -0.019224 | -0.11771 | -0.24723 | -0.44939 | -0.66104 | -0.91354 | -1.0968 | -1.3072 | -1.5225 | -1.7327 | -1.9516 | -2.1905 | -2.435 | -3.3908 | -4.326 | -4.3676
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | Steady Progression | Headroom (MW) | Fault level | 0.13014 | 0.10627 | 0.081794 | 0.05852 | 0.038158 | 0.010769 | -0.01981 | -0.060139 | -0.10543 | -0.1571 | -0.22695 | -0.28752 | -0.34256 | -0.40311 | -0.45824 | -0.52763 | -0.80992 | -1.1242 | -1.4839
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | System Transformation | Headroom (MW) | Fault level | 0.13932 | 0.096193 | 0.044618 | -0.025942 | -0.11017 | -0.21836 | -0.394 | -0.5758 | -0.78473 | -0.99084 | -1.2096 | -1.4175 | -1.626 | -1.8254 | -2.0329 | -2.2591 | -3.2467 | -4.0097 | -4.639
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | 52.6468 | -1.1435 | WPD Best View | Headroom (MW) | Fault level | 0.11064 | 0.030667 | -0.090219 | -0.24515 | -0.42365 | -0.70499 | -1.1099 | -1.5135 | -1.924 | -2.3335 | -2.7909 | -3.2188 | -3.6587 | -4.0873 | -4.5278 | -4.9912 | -7.3224 | -9.5025 | -11.455
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Consumer Transformation | Headroom (MW) | N/A | 24.3508 | 24.3239 | 24.2447 | 24.2181 | 24.1722 | 24.1244 | 23.8985 | 23.7501 | 23.4496 | 23.0798 | 22.6754 | 22.2414 | 21.7889 | 21.3114 | 20.9342 | 20.5602 | 19.0612 | 17.7183 | 16.3757
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Leading the Way | Headroom (MW) | N/A | 24.36 | 24.3386 | 24.2675 | 24.2399 | 24.1963 | 24.1507 | 23.6356 | 23.5928 | 23.3236 | 23.2873 | 22.9748 | 22.7418 | 22.3484 | 21.9317 | 21.6925 | 21.4785 | 20.3056 | 18.5532 | 16.8553
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | Steady Progression | Headroom (MW) | N/A | 24.3439 | 24.3103 | 24.2244 | 24.1895 | 24.1409 | 24.0914 | 23.8922 | 23.8455 | 23.6958 | 23.6518 | 23.6076 | 23.4186 | 23.2464 | 23.0772 | 23.0371 | 23.0051 | 21.6829 | 21.0238 | 20.0477
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | System Transformation | Headroom (MW) | N/A | 24.3508 | 24.3239 | 24.2448 | 24.2183 | 24.1724 | 24.1245 | 23.945 | 23.9001 | 23.7542 | 23.7156 | 23.577 | 23.41 | 23.2438 | 23.0804 | 23.0421 | 23.0153 | 22.6039 | 21.9955 | 21.3054
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | 52.6388 | -1.1334 | WPD Best View | Headroom (MW) | N/A | 24.3508 | 24.3239 | 24.2447 | 24.2181 | 24.1722 | 24.1244 | 24.0383 | 23.7501 | 23.4496 | 23.0798 | 22.6754 | 22.2414 | 21.7889 | 21.3114 | 20.9342 | 20.5602 | 19.0612 | 17.7183 | 16.3757
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Consumer Transformation | Headroom (MW) | N/A | 27.007 | 26.9479 | 26.8102 | 26.752 | 26.6831 | 26.6086 | 26.2946 | 26.2237 | 26.0152 | 25.5634 | 24.9075 | 24.2435 | 23.5692 | 22.8855 | 22.2525 | 21.6081 | 18.6299 | 15.7298 | 12.9525
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Leading the Way | Headroom (MW) | N/A | 27.0147 | 26.8494 | 26.7187 | 26.5491 | 26.4853 | 26.4144 | 25.7262 | 25.6591 | 25.2935 | 25.228 | 24.8108 | 24.444 | 24.156 | 23.7218 | 23.662 | 23.6011 | 21.6109 | 19.6573 | 17.7422
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | Steady Progression | Headroom (MW) | N/A | 27.0013 | 26.9366 | 26.7934 | 26.7268 | 26.6534 | 26.5767 | 26.2986 | 26.225 | 26.0144 | 25.9416 | 25.7601 | 25.4929 | 25.2474 | 25.0054 | 24.9384 | 24.8731 | 23.3303 | 21.9245 | 20.3474
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | System Transformation | Headroom (MW) | N/A | 27.007 | 26.948 | 26.8105 | 26.7524 | 26.6835 | 26.6091 | 26.3607 | 26.2895 | 26.0839 | 26.0146 | 25.812 | 25.571 | 25.3297 | 25.092 | 25.0276 | 24.9636 | 23.6437 | 22.287 | 21.0615
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | 52.634 | -1.1384 | WPD Best View | Headroom (MW) | N/A | 27.007 | 26.9479 | 26.8102 | 26.752 | 26.6831 | 26.6086 | 26.5386 | 26.4676 | 26.1795 | 25.5634 | 24.9075 | 24.2435 | 23.5692 | 22.8855 | 22.2525 | 21.6081 | 18.6299 | 15.7298 | 12.9525
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Consumer Transformation | Headroom (MW) | N/A | 97.93 | 97.512 | 96.6428 | 95.8362 | 94.9133 | 93.7073 | 91.6699 | 89.8844 | 87.984 | 85.1884 | 82.9918 | 81.021 | 78.0935 | 76.1138 | 74.4269 | 71.5142 | 55.5253 | 36.9568 | 18.6811
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Leading the Way | Headroom (MW) | N/A | 97.9873 | 97.4743 | 96.8117 | 96.294 | 95.865 | 95.4141 | 92.9881 | 92.498 | 91.4509 | 90.8832 | 89.6505 | 87.6384 | 86.6507 | 85.4995 | 83.1711 | 82.2573 | 69.532 | 56.8125 | 44.9688
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | Steady Progression | Headroom (MW) | N/A | 97.9712 | 97.6093 | 96.9465 | 96.5864 | 96.2388 | 95.9012 | 95.3332 | 94.9999 | 94.4699 | 94.0507 | 93.1919 | 92.3531 | 91.7852 | 91.2453 | 90.9175 | 90.5656 | 85.6313 | 83.4536 | 78.057
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | System Transformation | Headroom (MW) | N/A | 97.969 | 97.6026 | 96.8965 | 96.4849 | 95.9806 | 95.3437 | 94.3039 | 93.4735 | 92.2843 | 91.237 | 90.0082 | 88.9364 | 87.9051 | 86.9975 | 85.3868 | 84.6426 | 79.5841 | 73.1364 | 64.5342
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | 52.6297 | -1.1013 | WPD Best View | Headroom (MW) | N/A | 97.9485 | 97.5439 | 96.7208 | 95.965 | 95.0906 | 93.949 | 92.2387 | 90.5692 | 88.8521 | 87.0407 | 85.1088 | 83.3904 | 81.5477 | 79.7557 | 77.001 | 74.8501 | 61.8176 | 47.387 | 32.1928
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Consumer Transformation | Headroom (MW) | N/A | 16.7879 | 16.7342 | 16.6387 | 16.5995 | 16.5474 | 16.4966 | 16.4227 | 16.3734 | 16.3058 | 16.2447 | 16.1496 | 16.0712 | 15.9987 | 15.9309 | 15.8452 | 15.7475 | 15.068 | 14.2198 | 13.359
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Leading the Way | Headroom (MW) | N/A | 16.7883 | 16.7245 | 16.633 | 16.5876 | 16.5373 | 16.4887 | 16.0705 | 16.0224 | 15.9502 | 15.905 | 15.8292 | 15.7131 | 15.5913 | 15.4588 | 15.4281 | 15.3972 | 13.1873 | 12.7129 | 12.2229
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | Steady Progression | Headroom (MW) | N/A | 16.7873 | 16.7333 | 16.6346 | 16.5881 | 16.5341 | 16.4815 | 16.4175 | 16.3649 | 16.3099 | 16.2585 | 16.2048 | 16.1551 | 16.105 | 16.0575 | 16.0114 | 15.9667 | 14.9874 | 14.7473 | 14.3665
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | System Transformation | Headroom (MW) | N/A | 16.7878 | 16.734 | 16.6382 | 16.5987 | 16.5462 | 16.4946 | 16.4376 | 16.3866 | 16.3349 | 16.2852 | 16.2362 | 16.1879 | 16.1401 | 16.096 | 16.0544 | 16.0152 | 15.8561 | 15.5294 | 14.9744
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | 52.6589 | -1.0785 | WPD Best View | Headroom (MW) | N/A | 16.7882 | 16.7347 | 16.6395 | 16.6008 | 16.5491 | 16.4987 | 16.4462 | 16.3975 | 16.32 | 16.2218 | 16.1226 | 16.0433 | 15.9723 | 15.9061 | 15.8187 | 15.7165 | 14.9662 | 14.062 | 13.1553
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Consumer Transformation | Headroom (MW) | N/A | 13.2077 | 13.1649 | 13.0729 | 13.0262 | 12.9732 | 12.9205 | 12.6737 | 12.6246 | 12.4597 | 12.4118 | 12.2167 | 11.9282 | 11.6151 | 11.3125 | 11.2747 | 11.2376 | 9.7813 | 8.0566 | 6.2222
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Leading the Way | Headroom (MW) | N/A | 13.2106 | 13.066 | 12.9766 | 12.8253 | 12.7723 | 12.72 | 12.1931 | 12.1463 | 11.852 | 11.8063 | 11.488 | 11.2999 | 11.2073 | 11.0026 | 10.967 | 10.9314 | 12.7606 | 11.2853 | 9.7984
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | Steady Progression | Headroom (MW) | N/A | 13.2056 | 13.1607 | 13.0667 | 13.0175 | 12.9642 | 12.9114 | 12.6824 | 12.6325 | 12.4534 | 12.404 | 12.0045 | 11.5429 | 11.3285 | 11.1156 | 11.0702 | 11.0259 | 9.6417 | 8.44 | 7.1294
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | System Transformation | Headroom (MW) | N/A | 13.2077 | 13.1649 | 13.0729 | 13.0262 | 12.973 | 12.9201 | 12.7223 | 12.6725 | 12.4941 | 12.4447 | 12.2691 | 12.0573 | 11.8447 | 11.6339 | 11.5922 | 11.552 | 10.3877 | 9.2164 | 8.191
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | 52.6293 | -1.1214 | WPD Best View | Headroom (MW) | N/A | 13.2077 | 13.1649 | 13.0729 | 13.0262 | 12.9732 | 12.9205 | 12.8908 | 12.8416 | 12.7931 | 12.7452 | 12.6999 | 12.6012 | 12.3669 | 12.1404 | 11.8998 | 11.6435 | 10.2206 | 8.6197 | 7.0534
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Consumer Transformation | Headroom (MW) | N/A | 15.8403 | 15.7906 | 15.607 | 15.4058 | 15.1927 | 14.8922 | 14.4738 | 14.0654 | 13.6668 | 13.2402 | 12.7882 | 12.3589 | 11.9281 | 11.5035 | 11.0863 | 10.6081 | 8.16 | 5.6174 | 3.1847
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Leading the Way | Headroom (MW) | N/A | 15.8407 | 15.783 | 15.687 | 15.6246 | 15.5438 | 15.4289 | 15.1964 | 15.078 | 14.8853 | 14.7059 | 14.5001 | 14.2871 | 14.072 | 13.856 | 13.6373 | 13.3903 | 12.2948 | 11.0008 | 9.6498
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | Steady Progression | Headroom (MW) | N/A | 15.84 | 15.79 | 15.6922 | 15.6379 | 15.5853 | 15.5335 | 15.4732 | 15.3916 | 15.2993 | 15.2023 | 15.1033 | 15.0047 | 14.9131 | 14.8245 | 14.7499 | 14.6689 | 13.8312 | 13.5884 | 13.198
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | System Transformation | Headroom (MW) | N/A | 15.8403 | 15.7906 | 15.6934 | 15.6118 | 15.481 | 15.3472 | 15.1259 | 14.914 | 14.6676 | 14.4304 | 14.1798 | 13.9611 | 13.7469 | 13.5474 | 13.3467 | 13.1354 | 12.251 | 11.3506 | 10.3813
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | 52.6295 | -1.1017 | WPD Best View | Headroom (MW) | N/A | 15.8403 | 15.7906 | 15.607 | 15.4058 | 15.1927 | 14.8922 | 14.4738 | 14.0654 | 13.6668 | 13.2402 | 12.7882 | 12.3589 | 11.9281 | 11.5035 | 11.0863 | 10.6081 | 8.16 | 5.6174 | 3.1847
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Consumer Transformation | Headroom (MW) | N/A | 16.1912 | 16.1437 | 16.0492 | 15.8663 | 15.6136 | 15.2627 | 14.7617 | 14.2801 | 13.8197 | 13.328 | 12.8103 | 12.3431 | 11.8726 | 11.4055 | 10.9269 | 10.3887 | 7.5217 | 4.5746 | 1.8066
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Leading the Way | Headroom (MW) | N/A | 16.1919 | 16.1168 | 16.0231 | 15.9486 | 15.8973 | 15.848 | 15.4069 | 15.3606 | 15.2532 | 15.2108 | 14.9977 | 14.8033 | 14.5986 | 14.3746 | 14.2855 | 14.0383 | 12.8613 | 11.5403 | 10.1032
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | Steady Progression | Headroom (MW) | N/A | 16.1908 | 16.1429 | 16.0482 | 15.9977 | 15.946 | 15.8954 | 15.8187 | 15.7698 | 15.7124 | 15.6302 | 15.4951 | 15.3844 | 15.2765 | 15.1871 | 15.0983 | 15.0002 | 14.1577 | 13.86 | 13.3334
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | System Transformation | Headroom (MW) | N/A | 16.1912 | 16.1437 | 16.0492 | 16.0058 | 15.954 | 15.7922 | 15.5236 | 15.2689 | 14.9739 | 14.6809 | 14.3872 | 14.1213 | 13.8657 | 13.628 | 13.4041 | 13.1502 | 12.0896 | 11.0854 | 10.0485
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | 52.6465 | -1.099 | WPD Best View | Headroom (MW) | N/A | 16.1912 | 16.1437 | 16.0492 | 15.8663 | 15.6136 | 15.2627 | 14.7617 | 14.2801 | 13.8197 | 13.328 | 12.8103 | 12.3431 | 11.8726 | 11.4055 | 10.9269 | 10.3887 | 7.5217 | 4.5746 | 1.8066
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Consumer Transformation | Headroom (MW) | N/A | 13.6898 | 13.6515 | 13.5751 | 13.5342 | 13.4943 | 13.4565 | 13.2102 | 12.938 | 12.7222 | 12.4928 | 12.2687 | 12.1203 | 11.9931 | 11.8648 | 11.7512 | 11.5696 | 10.2296 | 8.2106 | 6.1123
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Leading the Way | Headroom (MW) | N/A | 13.6902 | 13.6343 | 13.5589 | 13.4963 | 13.4572 | 13.4208 | 12.8212 | 12.791 | 12.7191 | 12.7011 | 12.6371 | 12.5041 | 12.3746 | 12.2301 | 12.254 | 12.2753 | 9.2015 | 8.6558 | 8.0172
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | Steady Progression | Headroom (MW) | N/A | 13.6895 | 13.6502 | 13.5727 | 13.5274 | 13.4857 | 13.4451 | 13.3871 | 13.3482 | 13.3036 | 13.2662 | 13.224 | 13.1893 | 13.1533 | 13.1222 | 13.0935 | 13.0676 | 12.1846 | 12.0356 | 11.6002
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | System Transformation | Headroom (MW) | N/A | 13.6896 | 13.6509 | 13.5739 | 13.5321 | 13.4906 | 13.4506 | 13.4049 | 13.3669 | 13.2594 | 13.0967 | 12.9409 | 12.8496 | 12.7681 | 12.7259 | 12.7166 | 12.7 | 12.8359 | 12.3642 | 11.4195
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | 52.6161 | -1.1014 | WPD Best View | Headroom (MW) | N/A | 13.6897 | 13.651 | 13.5742 | 13.5326 | 13.4916 | 13.4523 | 13.1763 | 12.908 | 12.6604 | 12.4111 | 12.153 | 11.9656 | 11.7998 | 11.6425 | 11.5161 | 11.3384 | 10.3903 | 8.7757 | 6.9066
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Consumer Transformation | Headroom (MW) | N/A | 11.2966 | 11.2082 | 11.0627 | 10.9357 | 10.7956 | 10.6189 | 10.4575 | 10.3039 | 10.1032 | 9.8737 | 9.6243 | 9.4146 | 9.1835 | 8.942 | 8.6863 | 8.3996 | 6.6783 | 5.0268 | 3.5757
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Leading the Way | Headroom (MW) | N/A | 11.3151 | 11.2502 | 11.1394 | 11.0729 | 10.9868 | 10.8968 | 10.847 | 10.8223 | 10.7113 | 10.6075 | 10.4578 | 10.3264 | 10.1886 | 10.023 | 9.8286 | 9.5973 | 8.1704 | 6.8421 | 5.6994
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | Steady Progression | Headroom (MW) | N/A | 11.3111 | 11.2469 | 11.1454 | 11.0811 | 11.0261 | 10.9693 | 10.9396 | 10.922 | 10.8824 | 10.8236 | 10.7703 | 10.7262 | 10.6903 | 10.6475 | 10.6089 | 10.5778 | 10.3737 | 10.2495 | 9.8156
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | System Transformation | Headroom (MW) | N/A | 11.3115 | 11.2416 | 11.1189 | 11.0421 | 10.953 | 10.8552 | 10.784 | 10.7405 | 10.6225 | 10.5224 | 10.4027 | 10.3138 | 10.2297 | 10.1408 | 10.059 | 9.9748 | 9.5064 | 8.8713 | 8.1207
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | 52.6644 | -1.0941 | WPD Best View | Headroom (MW) | N/A | 11.3019 | 11.2191 | 11.0839 | 10.9744 | 10.8458 | 10.6863 | 10.5603 | 10.4442 | 10.2583 | 10.0455 | 9.8069 | 9.6044 | 9.3882 | 9.1531 | 8.9005 | 8.5936 | 6.7387 | 5.0522 | 3.5946
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Consumer Transformation | Headroom (MW) | Thermal | 10.7666 | 10.6691 | 10.4872 | 10.3185 | 10.1467 | 9.9099 | 9.5202 | 9.1491 | 8.7566 | 7.4473 | 6.984 | 6.6346 | 5.3523 | 5.0045 | 4.7062 | 3.413 | -2.0636 | -8.899 | -15.7295
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Leading the Way | Headroom (MW) | Thermal | 10.8005 | 10.7495 | 10.6438 | 10.5887 | 10.5203 | 10.4609 | 10.3029 | 10.1274 | 9.9298 | 9.7966 | 9.5906 | 8.5544 | 8.4683 | 8.4043 | 6.6207 | 6.4774 | 0.90612 | -5.3747 | -10.6722
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | Steady Progression | Headroom (MW) | N/A | 10.7969 | 10.7352 | 10.6368 | 10.5866 | 10.5475 | 10.515 | 10.4646 | 10.4209 | 10.3589 | 10.3159 | 10.2399 | 10.2005 | 10.1684 | 10.1409 | 10.1352 | 10.1084 | 10.2096 | 9.7486 | 8.3443
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | System Transformation | Headroom (MW) | N/A | 10.7909 | 10.7271 | 10.6 | 10.5182 | 10.4327 | 10.3337 | 10.1556 | 9.9741 | 9.782 | 9.6266 | 9.4424 | 9.2954 | 9.1601 | 9.0755 | 8.0638 | 7.965 | 6.5073 | 4.5691 | 1.2488
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | 52.6348 | -1.0525 | WPD Best View | Headroom (MW) | Thermal | 10.7795 | 10.69 | 10.5441 | 10.409 | 10.2746 | 10.0864 | 9.7795 | 9.4824 | 9.1838 | 8.8989 | 8.5781 | 8.324 | 8.0698 | 7.8546 | 6.7026 | 6.4112 | 3.6702 | 0.53537 | -3.6584
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Consumer Transformation | Headroom (MW) | N/A | 74.2087 | 73.791 | 73.0252 | 72.4413 | 71.8606 | 70.962 | 69.5813 | 68.0852 | 66.6361 | 65.1804 | 63.6422 | 62.3012 | 60.9276 | 59.6185 | 58.2609 | 56.7456 | 48.5514 | 39.2942 | 30.1455
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Leading the Way | Headroom (MW) | N/A | 74.3068 | 74.0311 | 73.5123 | 73.2481 | 72.9762 | 72.6256 | 71.6519 | 71.1232 | 70.3283 | 69.8911 | 69.2722 | 68.8213 | 68.2209 | 67.4824 | 66.98 | 66.4636 | 60.6941 | 54.7701 | 48.4513
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | Steady Progression | Headroom (MW) | N/A | 74.2867 | 74.0288 | 73.4878 | 73.2132 | 73 | 72.7616 | 72.4801 | 72.1729 | 71.8704 | 71.5736 | 70.7751 | 70.1165 | 69.8589 | 69.6354 | 69.4572 | 69.2321 | 65.7001 | 64.4547 | 61.5307
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | System Transformation | Headroom (MW) | N/A | 74.2753 | 73.9713 | 73.3768 | 73.0138 | 72.6583 | 72.2354 | 71.5948 | 70.9513 | 70.24 | 69.5483 | 68.7192 | 68.0333 | 67.364 | 66.8396 | 66.286 | 65.6831 | 63.5257 | 60.5734 | 56.4953
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | 52.6467 | -1.1433 | WPD Best View | Headroom (MW) | N/A | 74.2416 | 73.8642 | 73.1813 | 72.6866 | 72.1831 | 71.4563 | 70.2767 | 68.9359 | 67.6641 | 66.403 | 65.0867 | 63.9266 | 62.7107 | 61.5614 | 60.3488 | 59.0028 | 51.9907 | 43.7525 | 33.9874
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Consumer Transformation | Headroom (MW) | N/A | 23.4332 | 23.3127 | 23.0966 | 22.9686 | 22.8063 | 22.569 | 22.2599 | 21.9498 | 21.6354 | 21.3502 | 21.0428 | 20.7669 | 20.506 | 20.298 | 20.0578 | 19.7687 | 18.2659 | 16.5168 | 14.7633
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Leading the Way | Headroom (MW) | N/A | 23.4487 | 23.3594 | 23.1879 | 23.1246 | 23.0138 | 22.8682 | 22.5919 | 22.461 | 22.2166 | 22.0571 | 21.8864 | 21.7708 | 21.6058 | 21.3528 | 21.3093 | 21.2627 | 20.7859 | 19.9966 | 19.189
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | Steady Progression | Headroom (MW) | N/A | 23.4416 | 23.3503 | 23.1799 | 23.1013 | 23.0127 | 22.931 | 22.84 | 22.7327 | 22.6455 | 22.5508 | 22.131 | 21.7663 | 21.6777 | 21.6169 | 21.5505 | 21.4669 | 20.5742 | 20.1883 | 19.5675
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | System Transformation | Headroom (MW) | N/A | 23.4398 | 23.3494 | 23.1618 | 23.0677 | 22.9661 | 22.8394 | 22.677 | 22.5208 | 22.3575 | 22.1941 | 22.0188 | 21.8798 | 21.7347 | 21.6597 | 21.5429 | 21.418 | 20.9297 | 20.2878 | 19.4113
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | 52.6694 | -1.1544 | WPD Best View | Headroom (MW) | N/A | 23.4378 | 23.3218 | 23.1191 | 22.9911 | 22.8452 | 22.6244 | 22.3369 | 22.0477 | 21.7625 | 21.505 | 21.2145 | 20.9627 | 20.7046 | 20.5056 | 20.2635 | 19.9758 | 18.5164 | 16.7769 | 15.0028
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Consumer Transformation | Headroom (MW) | N/A | 14.8493 | 14.7453 | 14.5843 | 14.4275 | 14.2765 | 14.0374 | 13.7175 | 13.3888 | 13.0675 | 12.7122 | 12.3324 | 11.9997 | 11.6672 | 11.3504 | 11.0198 | 10.6505 | 8.7999 | 6.7966 | 4.8278
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Leading the Way | Headroom (MW) | N/A | 14.8783 | 14.8121 | 14.7174 | 14.6549 | 14.605 | 14.5179 | 14.3904 | 14.2563 | 14.0901 | 13.9388 | 13.7718 | 13.609 | 13.4394 | 13.3079 | 13.137 | 12.9547 | 10.9926 | 9.3802 | 7.9319
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | Steady Progression | Headroom (MW) | N/A | 14.8751 | 14.8255 | 14.7186 | 14.6728 | 14.6339 | 14.5821 | 14.5353 | 14.4789 | 14.4269 | 14.3604 | 14.2872 | 14.2354 | 14.1871 | 14.14 | 14.1039 | 14.0641 | 12.7541 | 12.5153 | 12.0061
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | System Transformation | Headroom (MW) | N/A | 14.8716 | 14.7968 | 14.6844 | 14.5982 | 14.5157 | 14.4028 | 14.2651 | 14.1033 | 13.9119 | 13.7273 | 13.5469 | 13.3972 | 13.2471 | 13.1321 | 13.0077 | 12.873 | 12.4647 | 11.8811 | 11.0377
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | 52.6697 | -1.1295 | WPD Best View | Headroom (MW) | N/A | 14.8714 | 14.7871 | 14.6669 | 14.5752 | 14.479 | 14.344 | 14.1464 | 13.9425 | 13.7263 | 13.5024 | 13.2653 | 13.0432 | 12.8074 | 12.6049 | 12.3684 | 12.1014 | 10.8458 | 9.3032 | 7.6543
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Consumer Transformation | Headroom (MW) | N/A | 13.9333 | 13.8306 | 13.6283 | 13.4879 | 13.3374 | 13.1086 | 12.7697 | 12.4607 | 12.2031 | 11.9317 | 11.6515 | 11.4446 | 11.2009 | 10.9379 | 10.6734 | 10.3778 | 8.5071 | 6.209 | 3.8673
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Leading the Way | Headroom (MW) | N/A | 13.9637 | 13.8947 | 13.7834 | 13.7371 | 13.6651 | 13.614 | 13.492 | 13.3926 | 13.3432 | 13.3397 | 13.3431 | 13.3538 | 13.2854 | 13.1423 | 12.9922 | 12.8537 | 9.8863 | 9.0339 | 7.4712
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | Steady Progression | Headroom (MW) | N/A | 13.962 | 13.8964 | 13.7651 | 13.6907 | 13.6321 | 13.5732 | 13.5163 | 13.4495 | 13.373 | 13.3177 | 13.23 | 13.1846 | 13.1464 | 13.1103 | 13.0967 | 13.07 | 13.1621 | 13.2389 | 12.5847
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | System Transformation | Headroom (MW) | N/A | 13.9562 | 13.8734 | 13.725 | 13.632 | 13.5154 | 13.414 | 13.2381 | 13.0656 | 12.8858 | 12.7135 | 12.5411 | 12.4091 | 12.2973 | 12.1983 | 12.1232 | 12.0319 | 11.7847 | 11.187 | 10.1307
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | 52.6508 | -1.1729 | WPD Best View | Headroom (MW) | N/A | 13.9395 | 13.8528 | 13.6793 | 13.5631 | 13.4184 | 13.2409 | 12.9524 | 12.6598 | 12.4451 | 12.2092 | 11.9915 | 11.8307 | 11.6452 | 11.4187 | 11.207 | 10.977 | 9.6502 | 7.9006 | 4.6431
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Consumer Transformation | Headroom (MW) | N/A | 60.8625 | 60.797 | 60.6786 | 60.5533 | 60.4314 | 60.2383 | 59.9722 | 59.7042 | 59.435 | 59.1732 | 58.8911 | 58.6405 | 58.3868 | 58.1401 | 57.8942 | 57.6279 | 56.2558 | 54.7686 | 53.3258
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Leading the Way | Headroom (MW) | N/A | 60.8851 | 60.8573 | 60.7814 | 60.7251 | 60.6635 | 60.5833 | 60.4404 | 60.3051 | 60.1297 | 60.0312 | 59.9268 | 59.8463 | 59.7587 | 59.6684 | 59.5563 | 59.4339 | 58.7255 | 57.3616 | 56.1715
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | Steady Progression | Headroom (MW) | N/A | 60.878 | 60.8552 | 60.793 | 60.7536 | 60.7331 | 60.6981 | 60.6508 | 60.6064 | 60.5509 | 60.5017 | 60.441 | 60.3896 | 60.3392 | 60.2903 | 60.2584 | 60.2131 | 59.9574 | 59.7851 | 59.4504
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | System Transformation | Headroom (MW) | N/A | 60.8772 | 60.8463 | 60.7681 | 60.712 | 60.6521 | 60.5706 | 60.4411 | 60.3206 | 60.1723 | 60.0362 | 59.8898 | 59.7687 | 59.6455 | 59.5377 | 59.4286 | 59.3129 | 58.8823 | 58.3861 | 57.7802
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | 52.6467 | -1.1433 | WPD Best View | Headroom (MW) | N/A | 60.8625 | 60.797 | 60.6786 | 60.5533 | 60.4314 | 60.2383 | 59.9722 | 59.7042 | 59.435 | 59.1732 | 58.8911 | 58.6405 | 58.3868 | 58.1401 | 57.8942 | 57.6279 | 56.2558 | 54.7686 | 53.3258
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Consumer Transformation | Headroom (MW) | N/A | 15.3304 | 15.3055 | 15.2375 | 15.2039 | 15.209 | 15.2087 | 15.062 | 14.7818 | 14.4952 | 14.2131 | 13.9243 | 13.6495 | 13.3667 | 13.092 | 12.8157 | 12.5207 | 10.9226 | 9.2033 | 7.5613
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Leading the Way | Headroom (MW) | N/A | 15.3311 | 15.3075 | 15.2422 | 15.2065 | 15.2289 | 15.2423 | 14.9372 | 14.9082 | 14.7487 | 14.7245 | 14.5442 | 14.4414 | 14.3315 | 14.2109 | 14.1851 | 14.1585 | 14.5038 | 13.1978 | 11.8877
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | Steady Progression | Headroom (MW) | N/A | 15.33 | 15.3013 | 15.2312 | 15.1949 | 15.1881 | 15.1771 | 15.1377 | 15.1054 | 15.0741 | 15.043 | 14.8858 | 14.7406 | 14.7086 | 14.6779 | 14.6477 | 14.618 | 13.4523 | 12.9271 | 12.122
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | System Transformation | Headroom (MW) | N/A | 15.3304 | 15.3055 | 15.2375 | 15.2039 | 15.209 | 15.2086 | 15.1735 | 15.141 | 15.1125 | 15.0772 | 14.9225 | 14.7786 | 14.6394 | 14.5118 | 14.3836 | 14.2473 | 13.6644 | 13.0314 | 12.3354
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | 52.6444 | -1.1276 | WPD Best View | Headroom (MW) | N/A | 15.3304 | 15.3055 | 15.2375 | 15.2039 | 15.209 | 15.2087 | 15.0689 | 14.7818 | 14.4952 | 14.2131 | 13.9243 | 13.6495 | 13.3667 | 13.092 | 12.8157 | 12.5207 | 10.9226 | 9.2033 | 7.5613
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Consumer Transformation | Headroom (MW) | N/A | 22.4517 | 22.3021 | 22.0519 | 21.8339 | 21.6145 | 21.2976 | 20.8433 | 20.4069 | 20.0271 | 19.6109 | 19.1807 | 18.8037 | 18.4487 | 18.0726 | 17.6999 | 17.2496 | 14.6894 | 11.7092 | 7.4757
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Leading the Way | Headroom (MW) | N/A | 22.4957 | 22.3656 | 22.2101 | 22.1207 | 22.0299 | 21.9174 | 21.7579 | 21.6227 | 21.5059 | 21.4295 | 21.3567 | 21.2361 | 21.11 | 20.9579 | 20.7933 | 20.5846 | 18.2271 | 16.4937 | 14.4911
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | Steady Progression | Headroom (MW) | N/A | 22.4853 | 22.3895 | 22.2491 | 22.1544 | 22.0755 | 21.9941 | 21.9154 | 21.821 | 21.7212 | 21.6165 | 21.5009 | 21.4165 | 21.3456 | 21.2754 | 21.2255 | 21.1721 | 21.0433 | 20.8627 | 20.0452
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | System Transformation | Headroom (MW) | N/A | 22.4816 | 22.3853 | 22.1968 | 22.0618 | 21.9245 | 21.7521 | 21.5135 | 21.2723 | 21.0004 | 20.7381 | 20.4913 | 20.2733 | 20.0788 | 19.9037 | 19.7437 | 19.5651 | 18.8914 | 17.9455 | 15.3991
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | 52.5775 | -1.1445 | WPD Best View | Headroom (MW) | N/A | 22.4793 | 22.3709 | 22.1731 | 22.0196 | 21.8675 | 21.6804 | 21.3962 | 21.1171 | 20.8357 | 20.5412 | 20.2641 | 20.0194 | 19.798 | 19.5753 | 19.3758 | 19.1348 | 18.0274 | 16.5787 | 13.6498
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Consumer Transformation | Headroom (MW) | N/A | 49.1521 | 49.2882 | 48.5987 | 41.8848 | 41.2512 | 40.616 | 39.6668 | 38.6885 | 37.8144 | 36.9423 | 35.9005 | 35.1286 | 34.2924 | 33.4727 | 32.6856 | 31.7797 | 21.3855 | 8.5667 | 0.60294
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Leading the Way | Headroom (MW) | N/A | 49.2473 | 49.7341 | 49.2696 | 42.8781 | 42.5764 | 42.4805 | 41.4037 | 41.3784 | 41.0455 | 41.14 | 40.6847 | 40.1247 | 39.5265 | 38.8608 | 38.7749 | 36.5011 | 25.7599 | 19 | 12.8784
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | Steady Progression | Headroom (MW) | N/A | 49.2503 | 49.3664 | 48.9439 | 42.5669 | 42.3629 | 42.2792 | 42.1696 | 40.9758 | 39.7963 | 39.6479 | 38.9371 | 38.3414 | 38.1852 | 38.0864 | 37.9833 | 37.9051 | 34.5596 | 33.5243 | 31.2073
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | System Transformation | Headroom (MW) | N/A | 49.217 | 49.4766 | 48.9569 | 42.4695 | 42.0781 | 41.8418 | 41.4101 | 40.914 | 40.3558 | 39.8577 | 39.2386 | 38.7928 | 38.3752 | 38.0231 | 37.6983 | 37.3934 | 36.2601 | 29.064 | 24.8289
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | 52.5775 | -1.1441 | WPD Best View | Headroom (MW) | N/A | 49.2085 | 49.4659 | 48.9414 | 42.4364 | 42.0389 | 41.793 | 41.3412 | 40.8222 | 40.2529 | 39.757 | 39.127 | 38.6892 | 38.2728 | 37.9205 | 37.5709 | 37.2228 | 35.6063 | 27.9038 | 23.3106
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Consumer Transformation | Headroom (MW) | Thermal | 10.4975 | 10.4109 | 10.2686 | 4.0124 | 3.892 | 3.8558 | 3.814 | 3.7212 | 3.6346 | 3.5568 | 3.4012 | 3.2815 | 3.151 | 3.0104 | 2.8848 | 2.7391 | -2.2036 | -3.8383 | -5.0453
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Leading the Way | Headroom (MW) | Thermal | 10.516 | 10.4542 | 10.3465 | 4.1394 | 4.0838 | 4.174 | 4.3124 | 4.388 | 4.4852 | 4.6107 | 4.6348 | 4.6173 | 4.5917 | 4.5536 | 4.4892 | 2.7092 | -1.5305 | -3.7602 | -3.4444
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | Steady Progression | Headroom (MW) | N/A | 10.5157 | 10.4507 | 10.347 | 4.1338 | 4.0781 | 4.0984 | 4.1436 | 3.1191 | 2.1069 | 2.115 | 1.6199 | 1.1588 | 1.1384 | 1.1203 | 1.1006 | 1.0858 | 0.96747 | 0.94039 | 0.61005
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | System Transformation | Headroom (MW) | N/A | 10.5133 | 10.4448 | 10.3248 | 4.0926 | 4.0121 | 4.0338 | 4.0726 | 4.0454 | 4.0149 | 3.9974 | 3.9072 | 3.8463 | 3.7845 | 3.73 | 3.6731 | 3.6233 | 3.2703 | 1.5385 | 0.98908
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | 52.5829 | -1.2071 | WPD Best View | Headroom (MW) | N/A | 10.5133 | 10.4448 | 10.3248 | 4.0926 | 4.0121 | 4.0338 | 4.0726 | 4.0454 | 4.0149 | 3.9974 | 3.9072 | 3.8463 | 3.7845 | 3.73 | 3.6731 | 3.6233 | 3.2703 | 1.5385 | 0.98908
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Consumer Transformation | Headroom (MW) | N/A | 15.2196 | 15.6607 | 15.488 | 15.3806 | 15.2343 | 15.1466 | 14.9684 | 14.7979 | 14.6355 | 14.4504 | 14.28 | 14.1747 | 14.0646 | 13.952 | 13.8383 | 13.6976 | 12.6571 | 7.5683 | 4.6127
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Leading the Way | Headroom (MW) | N/A | 15.2359 | 15.9129 | 15.7894 | 15.7496 | 15.6841 | 15.6914 | 15.1883 | 15.1432 | 15.0602 | 15.0249 | 14.9363 | 14.7976 | 14.6517 | 14.4965 | 14.484 | 14.0026 | 11.3207 | 9.8325 | 5.8782
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | Steady Progression | Headroom (MW) | N/A | 15.232 | 15.5531 | 15.445 | 15.399 | 15.372 | 15.3713 | 15.3416 | 15.3001 | 15.2683 | 15.242 | 15.198 | 15.1856 | 15.1597 | 15.1692 | 15.1679 | 15.1838 | 14.0426 | 13.861 | 13.4064
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | System Transformation | Headroom (MW) | N/A | 15.2245 | 15.6981 | 15.5582 | 15.4977 | 15.3998 | 15.3913 | 15.2982 | 15.2057 | 15.0814 | 14.9687 | 14.8479 | 14.7772 | 14.724 | 14.6881 | 14.658 | 14.6471 | 14.7047 | 11.6828 | 9.5536
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | 52.5677 | -1.1848 | WPD Best View | Headroom (MW) | N/A | 15.2271 | 15.6943 | 15.5526 | 15.4895 | 15.3942 | 15.3872 | 15.2957 | 15.2001 | 15.0769 | 14.9653 | 14.8479 | 14.7842 | 14.7394 | 14.7068 | 14.6753 | 14.6589 | 14.5904 | 11.4306 | 9.2238
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Consumer Transformation | Headroom (MW) | N/A | 23.435 | 23.2167 | 22.8421 | 22.4918 | 22.1249 | 21.6136 | 20.8844 | 20.1694 | 19.5443 | 18.9352 | 18.2192 | 17.6724 | 17.0768 | 16.5103 | 15.9625 | 15.3431 | 10.932 | 4.8367 | 1.0355
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Leading the Way | Headroom (MW) | N/A | 23.4954 | 23.367 | 23.1336 | 22.9891 | 22.8086 | 22.6151 | 21.9029 | 21.8471 | 21.5001 | 21.5044 | 21.1136 | 20.7098 | 20.2831 | 19.8107 | 19.8017 | 19.7892 | 15.9697 | 12.9277 | 10.4446
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | Steady Progression | Headroom (MW) | N/A | 23.5026 | 23.3625 | 23.1518 | 23.0341 | 22.9128 | 22.8095 | 22.6845 | 22.5567 | 22.4211 | 22.291 | 22.1192 | 21.997 | 21.8871 | 21.7969 | 21.7147 | 21.6356 | 19.5496 | 18.7229 | 17.1909
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | System Transformation | Headroom (MW) | N/A | 23.4792 | 23.3336 | 23.0739 | 22.8792 | 22.6662 | 22.4168 | 22.0393 | 21.6629 | 21.2595 | 20.8915 | 20.4835 | 20.1693 | 19.8666 | 19.605 | 19.3671 | 19.123 | 18.2851 | 15.8428 | 14.2862
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | 52.5848 | -1.1021 | WPD Best View | Headroom (MW) | N/A | 23.4681 | 23.3268 | 23.0639 | 22.8542 | 22.6327 | 22.372 | 21.9729 | 21.5767 | 21.161 | 20.7943 | 20.3719 | 20.0587 | 19.7488 | 19.4837 | 19.2224 | 18.9406 | 17.7456 | 14.9348 | 13.0978
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Consumer Transformation | Headroom (MW) | Thermal | 86.5227 | 86.0899 | 85.3448 | 69.2524 | 69.0405 | 68.5976 | 49.3402 | 48.6664 | 47.0126 | 46.2814 | 45.531 | 44.344 | 43.9769 | 42.6165 | 39.5274 | 37.6162 | 26.2574 | 1.075 | -4.1457
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Leading the Way | Headroom (MW) | Thermal | 86.7282 | 86.5308 | 86.1448 | 70.467 | 61.6659 | 62.3288 | 53.3216 | 50.4873 | 50.772 | 51.3195 | 51.0508 | 52.2186 | 52.9809 | 52.2914 | 45.6081 | 44.3337 | 39.9593 | 24.3488 | -4.7307
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | Steady Progression | Headroom (MW) | N/A | 86.5537 | 86.2837 | 85.7858 | 70.1091 | 45.6471 | 45.844 | 45.9948 | 43.1213 | 40.2117 | 40.4059 | 39.2928 | 38.5246 | 38.9262 | 39.3906 | 39.854 | 40.5268 | 42.7477 | 42.8839 | 41.8296
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | System Transformation | Headroom (MW) | N/A | 86.5996 | 86.3313 | 85.7901 | 70.0014 | 70.0991 | 70.22 | 70.1416 | 70.1572 | 70.046 | 70.0133 | 70.1591 | 70.7264 | 70.2322 | 70.6408 | 71.1138 | 71.977 | 70.3653 | 60.4174 | 65.5777
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | 52.4916 | -0.6685 | WPD Best View | Headroom (MW) | N/A | 86.6941 | 86.4503 | 86.0149 | 70.3143 | 61.4795 | 62.0986 | 53.1435 | 50.0878 | 50.3001 | 50.7075 | 51.2781 | 52.3787 | 52.3216 | 53.2254 | 50.5923 | 50.7253 | 55.9418 | 45.4951 | 22.779
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Consumer Transformation | Headroom (MW) | N/A | 17.4508 | 17.4697 | 17.4399 | 17.3812 | 17.3923 | 17.4505 | 17.5382 | 17.6118 | 17.5831 | 17.5624 | 17.537 | 17.5815 | 17.7596 | 17.9281 | 17.9934 | 17.9943 | 19.1007 | 18.8418 | 18.3338
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Leading the Way | Headroom (MW) | N/A | 17.4767 | 17.5208 | 17.5216 | 17.4603 | 17.5021 | 17.5949 | 17.7165 | 14.3075 | 14.2396 | 14.1757 | 14.0969 | 14.1367 | 14.3521 | 14.5903 | 14.6873 | 14.6801 | 16.2455 | 15.5289 | 14.7064
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | Steady Progression | Headroom (MW) | N/A | 17.4314 | 17.4296 | 17.3759 | 17.3206 | 17.319 | 17.3508 | 17.3861 | 17.4165 | 17.3916 | 17.3682 | 17.3435 | 17.3589 | 17.4482 | 17.5443 | 17.5768 | 17.5691 | 18.3646 | 18.3532 | 18.2079
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | System Transformation | Headroom (MW) | N/A | 17.4507 | 17.4696 | 17.4397 | 17.3808 | 17.3917 | 17.4496 | 17.5399 | 17.6127 | 17.5871 | 17.565 | 17.5454 | 17.601 | 17.7809 | 17.9517 | 18.0137 | 18.012 | 19.1693 | 19.0449 | 18.7064
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | 52.498 | -0.6724 | WPD Best View | Headroom (MW) | N/A | 17.4513 | 17.4711 | 17.4445 | 17.3866 | 17.4231 | 17.5202 | 17.663 | 14.2069 | 14.1424 | 14.077 | 13.9959 | 14.0064 | 14.1877 | 14.3856 | 14.4649 | 14.4557 | 16.1278 | 15.579 | 14.8351
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Consumer Transformation | Headroom (MW) | N/A | 22.5525 | 22.4318 | 22.2293 | 22.0043 | 22.0861 | 22.0424 | 22.102 | 22.1811 | 22.3108 | 22.4151 | 22.6943 | 23.2758 | 23.5296 | 23.7826 | 23.1796 | 22.9083 | 21.596 | 15.8036 | 9.6546
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Leading the Way | Headroom (MW) | N/A | 22.6607 | 22.5959 | 22.4925 | 22.3707 | 22.6911 | 23.1542 | 23.6802 | 24.3019 | 24.8949 | 25.581 | 26.5421 | 27.853 | 28.7123 | 29.416 | 27.0236 | 28.1898 | 23.572 | 19.4338 | 12.7292
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | Steady Progression | Headroom (MW) | N/A | 22.5359 | 22.4843 | 22.3727 | 22.3126 | 16.3394 | 16.5148 | 16.7909 | 14.0251 | 11.2807 | 11.639 | 10.734 | 10.0881 | 10.5172 | 10.9795 | 11.4634 | 12.1304 | 12.9253 | 14.3573 | 15.0289
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | System Transformation | Headroom (MW) | N/A | 22.5798 | 22.5133 | 22.3965 | 22.2811 | 22.4801 | 22.6456 | 22.9699 | 23.3271 | 23.71 | 24.1133 | 24.7656 | 25.6497 | 26.218 | 26.7826 | 27.4192 | 28.3854 | 29.0461 | 27.0847 | 23.673
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | 52.4918 | -0.6686 | WPD Best View | Headroom (MW) | N/A | 22.6585 | 22.5921 | 22.4892 | 22.3689 | 22.6912 | 23.1531 | 23.6869 | 24.3159 | 24.9441 | 25.6498 | 26.6473 | 27.9442 | 28.7783 | 29.623 | 28.7533 | 29.9064 | 27.7015 | 23.7848 | 18.2158
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Consumer Transformation | Headroom (MW) | N/A | 16.1886 | 16.1444 | 16.0548 | 16.0334 | 16.0159 | 15.9714 | 15.9196 | 15.9324 | 15.9614 | 16.003 | 16.0234 | 16.0437 | 16.087 | 16.0659 | 15.2138 | 15.217 | 16.4908 | 14.8478 | 14.2268
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Leading the Way | Headroom (MW) | N/A | 16.1895 | 16.1449 | 16.0568 | 16.0431 | 16.0373 | 15.9944 | 15.9142 | 15.95 | 15.9972 | 16.0792 | 16.126 | 16.1392 | 16.1588 | 16.0737 | 16.1206 | 15.2871 | 16.6086 | 14.7375 | 10.3685
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | Steady Progression | Headroom (MW) | N/A | 16.188 | 16.1425 | 16.0515 | 16.0212 | 15.9942 | 15.9479 | 15.9007 | 15.8894 | 15.8915 | 15.8981 | 15.9071 | 15.9191 | 15.9386 | 15.9197 | 15.9256 | 15.9101 | 16.7081 | 16.7472 | 16.6292
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | System Transformation | Headroom (MW) | N/A | 16.1885 | 16.1442 | 16.0544 | 16.0326 | 16.0146 | 15.9694 | 15.9233 | 15.9344 | 15.9697 | 16.008 | 16.0482 | 16.0809 | 16.136 | 16.1274 | 16.1594 | 16.1567 | 17.5691 | 17.5265 | 17.3085
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | 52.5109 | -0.6969 | WPD Best View | Headroom (MW) | N/A | 16.1891 | 16.1458 | 16.0572 | 16.039 | 16.0326 | 15.9891 | 15.9458 | 15.9601 | 16.0175 | 16.0959 | 16.1681 | 16.2469 | 16.3529 | 16.3491 | 16.3818 | 15.3051 | 16.7199 | 14.9814 | 11.9736
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Consumer Transformation | Headroom (MW) | Fault level | 4.7634 | 4.6454 | 4.4933 | 4.2948 | 4.0597 | 3.7092 | 3.1901 | 2.6964 | 2.2081 | 1.6675 | 1.0695 | 0.46801 | -0.1193 | -0.71057 | -2.2712 | -2.947 | -7.5283 | -12.8754 | -16.9446
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Leading the Way | Headroom (MW) | Fault level | 4.7623 | 4.7179 | 4.6718 | 4.6164 | 4.522 | 4.4188 | 4.222 | 4.0926 | 3.8753 | 3.6975 | 3.4518 | 3.2086 | 2.9557 | 2.7307 | 1.0246 | 0.75225 | -3.6516 | -7.1424 | -11.5369
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | Steady Progression | Headroom (MW) | N/A | 3.9781 | 3.9483 | 3.9272 | 3.901 | 3.8718 | 3.8439 | 3.8109 | 3.7672 | 3.7107 | 3.6475 | 3.5548 | 3.4855 | 3.412 | 3.3463 | 3.2761 | 3.1941 | 2.7588 | 2.3239 | 1.8118
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | System Transformation | Headroom (MW) | Fault level | 4.6278 | 4.5804 | 4.5122 | 4.4269 | 4.3161 | 4.1954 | 3.9682 | 3.7523 | 3.4846 | 3.2234 | 2.9177 | 2.6465 | 2.3773 | 2.1112 | 1.842 | 1.5279 | -0.93589 | -3.0902 | -4.9909
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | 52.4854 | -0.7131 | WPD Best View | Headroom (MW) | Fault level | 4.5568 | 4.5141 | 4.4697 | 4.4161 | 4.3252 | 4.2257 | 4.0365 | 3.911 | 3.7018 | 3.5317 | 3.2992 | 3.0725 | 2.8387 | 2.6321 | 1.0098 | 0.77218 | -2.3188 | -5.5247 | -9.6109
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Consumer Transformation | Headroom (MW) | N/A | 14.7194 | 14.6583 | 14.5982 | 14.5182 | 14.6355 | 14.7324 | 14.5716 | 14.4121 | 14.2811 | 14.147 | 13.96 | 13.8539 | 13.7451 | 13.6498 | 13.5454 | 13.4253 | 12.5794 | 10.0693 | 8.7135
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Leading the Way | Headroom (MW) | N/A | 14.7319 | 14.6989 | 14.6847 | 14.657 | 14.9094 | 15.1572 | 15.007 | 14.9969 | 14.9387 | 14.8917 | 14.8018 | 14.7607 | 14.5709 | 14.3745 | 14.3762 | 14.3744 | 13.1709 | 12.2441 | 8.5259
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | Steady Progression | Headroom (MW) | N/A | 14.727 | 14.6887 | 14.6475 | 14.6039 | 14.7287 | 14.8596 | 14.8348 | 14.8168 | 14.8176 | 14.8136 | 14.8055 | 14.7983 | 14.7925 | 14.7968 | 14.8178 | 14.8069 | 14.6914 | 14.5698 | 14.2062
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | System Transformation | Headroom (MW) | N/A | 14.7261 | 14.6848 | 14.6401 | 14.5927 | 14.7496 | 14.9036 | 14.8193 | 14.7348 | 14.6824 | 14.6498 | 14.5939 | 14.5628 | 14.5295 | 14.5049 | 14.5076 | 14.5025 | 14.5406 | 12.9262 | 12.2565
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | 52.4639 | -0.7307 | WPD Best View | Headroom (MW) | N/A | 14.7311 | 14.6976 | 14.6819 | 14.6522 | 14.902 | 15.1465 | 15.056 | 14.9893 | 14.9096 | 14.8528 | 14.7511 | 14.7237 | 14.7103 | 14.7457 | 14.77 | 14.7657 | 13.1608 | 12.3562 | 8.7136
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Consumer Transformation | Headroom (MW) | Thermal | 8.9681 | 8.9258 | 8.8091 | 8.7046 | 8.6011 | 8.4698 | 8.278 | 8.1089 | 6.9847 | 6.8273 | 6.5989 | 5.4537 | 5.2608 | 4.1352 | 4.0059 | 2.9244 | -3.7789 | -12.6923 | -21.0489
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Leading the Way | Headroom (MW) | Thermal | 8.9845 | 8.9755 | 8.8951 | 8.8527 | 8.8031 | 8.7664 | 8.7092 | 8.6884 | 8.6402 | 8.642 | 7.6912 | 7.6684 | 7.6489 | 6.3779 | 3.7781 | 2.0756 | -6.4172 | -14.4306 | -22.2954
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | Steady Progression | Headroom (MW) | N/A | 8.9833 | 8.9536 | 8.8827 | 8.8395 | 8.8081 | 8.7695 | 8.7391 | 8.7053 | 8.6708 | 8.6321 | 8.5942 | 8.5588 | 8.5254 | 8.5196 | 8.5118 | 8.5091 | 8.613 | 7.426 | 7.0737
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | System Transformation | Headroom (MW) | Thermal | 8.9805 | 8.9541 | 8.8586 | 8.8033 | 8.7361 | 8.6703 | 8.5572 | 8.4561 | 8.3392 | 8.2326 | 8.1147 | 8.0316 | 7.0323 | 6.9813 | 6.9458 | 6.9128 | 4.2881 | 0.43409 | -3.9726
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | 52.4954 | -0.4731 | WPD Best View | Headroom (MW) | Thermal | 8.9813 | 8.955 | 8.8611 | 8.8073 | 8.7424 | 8.6791 | 8.5696 | 8.4737 | 8.3627 | 8.2638 | 8.1548 | 8.0806 | 7.0891 | 7.0441 | 7.0101 | 6.9679 | 4.2297 | 0.31311 | -4.141
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Consumer Transformation | Headroom (MW) | Thermal | -89.9406 | -90.3326 | -96.2154 | -96.9408 | -97.796 | -99.0476 | -111.0701 | -112.5071 | -113.9013 | -115.5583 | -134.8899 | -136.7386 | -153.9924 | -185.8992 | -197.8714 | -202.5579 | -251.429 | -333.0078 | -385.4674
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Leading the Way | Headroom (MW) | Thermal | -89.6929 | -89.8397 | -90.2339 | -90.5983 | -90.9618 | -91.4985 | -102.5034 | -102.9104 | -119.488 | -123.0323 | -140.782 | -148.4122 | -156.5228 | -194.3033 | -219.6998 | -243.1118 | -311.5653 | -389.2844 | -408.9334
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | Steady Progression | Headroom (MW) | Thermal | -89.9252 | -90.1315 | -90.5775 | -90.7603 | -101.1684 | -101.3932 | -106.7224 | -110.9454 | -115.185 | -119.5012 | -123.1427 | -126.3324 | -130.8079 | -135.4377 | -137.5539 | -137.8551 | -153.0499 | -187.2455 | -193.4318
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | System Transformation | Headroom (MW) | Thermal | -89.8543 | -90.0779 | -90.5959 | -91.0135 | -91.4886 | -92.1395 | -92.902 | -93.6026 | -94.4138 | -95.3679 | -96.3542 | -101.9111 | -102.6941 | -110.6451 | -111.3635 | -118.228 | -147.0386 | -161.2616 | -176.1375
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | 52.3189 | -0.614 | WPD Best View | Headroom (MW) | Thermal | -89.8497 | -90.0633 | -90.5534 | -90.9398 | -91.377 | -91.8999 | -93.57 | -95.1449 | -111.2111 | -113.0282 | -126.6055 | -132.7747 | -134.5037 | -136.1996 | -142.8699 | -145.2397 | -173.0394 | -188.7706 | -202.6687
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Consumer Transformation | Headroom (MW) | N/A | 15.6098 | 15.5341 | 15.3498 | 15.2449 | 15.1463 | 14.9283 | 14.783 | 14.6664 | 14.5985 | 14.2961 | 13.9603 | 13.6446 | 13.3489 | 13.0171 | 11.7557 | 11.4062 | 8.0048 | 3.8671 | 0.36172
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Leading the Way | Headroom (MW) | N/A | 15.6402 | 15.6162 | 15.5157 | 15.5394 | 15.563 | 15.5228 | 15.4257 | 15.5695 | 15.6838 | 15.741 | 15.6993 | 15.5749 | 15.4113 | 15.1819 | 13.8574 | 13.7409 | 10.5691 | 5.5302 | 1.0044
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | Steady Progression | Headroom (MW) | N/A | 15.6387 | 15.6024 | 15.4946 | 15.4813 | 15.4774 | 15.4218 | 15.5006 | 15.5764 | 15.6447 | 15.6485 | 15.6281 | 15.614 | 15.6086 | 15.5966 | 15.5778 | 15.566 | 15.5298 | 15.4436 | 14.9963
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | System Transformation | Headroom (MW) | N/A | 15.6394 | 15.589 | 15.4657 | 15.4369 | 15.3901 | 15.2974 | 15.3091 | 15.364 | 15.4148 | 15.2784 | 15.1428 | 15.0319 | 14.9436 | 14.8415 | 14.7468 | 14.6545 | 12.8713 | 12.1644 | 10.0168
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | 52.3197 | -0.6141 | WPD Best View | Headroom (MW) | N/A | 15.6394 | 15.5903 | 15.4685 | 15.4416 | 15.3975 | 15.3081 | 15.3242 | 15.3853 | 15.4438 | 15.3173 | 15.1935 | 15.0957 | 15.0204 | 14.9308 | 14.8452 | 14.7513 | 12.8814 | 12.0524 | 9.8291
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Consumer Transformation | Headroom (MW) | N/A | 14.2713 | 14.1956 | 14.0789 | 13.9801 | 13.8829 | 13.75 | 13.5501 | 13.3608 | 13.1671 | 12.9721 | 12.7741 | 12.5945 | 12.4067 | 12.2389 | 12.0925 | 10.9878 | 8.8968 | 5.306 | 1.3421
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Leading the Way | Headroom (MW) | N/A | 14.2818 | 14.2433 | 14.1699 | 14.1245 | 14.0883 | 14.0449 | 13.9655 | 13.9186 | 13.8278 | 13.7832 | 13.7225 | 13.6875 | 13.6768 | 13.6274 | 13.6184 | 11.9477 | 9.2925 | 6.268 | 3.9929
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | Steady Progression | Headroom (MW) | N/A | 14.2894 | 14.2372 | 14.1557 | 14.1034 | 14.0629 | 14.0176 | 13.9847 | 13.9376 | 13.8903 | 13.844 | 13.7956 | 13.7455 | 13.7156 | 13.6894 | 13.6686 | 13.6551 | 13.6535 | 13.6478 | 13.3298
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | System Transformation | Headroom (MW) | N/A | 14.2781 | 14.2305 | 14.1324 | 14.0599 | 13.9936 | 13.9233 | 13.812 | 13.7052 | 13.5847 | 13.4761 | 13.3648 | 13.2639 | 13.1793 | 13.1091 | 13.0485 | 12.996 | 12.8072 | 11.1561 | 8.0422
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | 52.3747 | -0.7207 | WPD Best View | Headroom (MW) | N/A | 14.2804 | 14.2408 | 14.1643 | 14.1149 | 14.0735 | 14.0235 | 13.9354 | 13.8761 | 13.7697 | 13.7054 | 13.621 | 13.5691 | 13.5324 | 13.5111 | 13.4861 | 11.7727 | 10.5916 | 8.7394 | 5.3796
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Consumer Transformation | Headroom (MW) | N/A | 24.976 | 24.8517 | 24.5838 | 24.3071 | 23.9986 | 23.5662 | 22.9446 | 22.3308 | 21.7228 | 21.0585 | 20.3412 | 19.741 | 19.0956 | 18.4566 | 17.819 | 17.1396 | 13.7826 | 10.3835 | 7.1658
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Leading the Way | Headroom (MW) | N/A | 25.0704 | 25.0505 | 24.9067 | 24.7831 | 24.6488 | 24.4806 | 24.1776 | 23.9095 | 23.5644 | 23.2539 | 22.9146 | 22.788 | 22.571 | 22.4271 | 22.2178 | 22.0312 | 20.8045 | 17.9561 | 16.2486
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | Steady Progression | Headroom (MW) | N/A | 24.9793 | 24.93 | 24.7962 | 24.7214 | 24.6469 | 24.5864 | 24.5165 | 24.4251 | 24.32 | 24.2097 | 24.0802 | 24.0145 | 23.9049 | 23.8044 | 23.6982 | 23.5904 | 23.3777 | 23.2207 | 22.5123
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | System Transformation | Headroom (MW) | N/A | 25.0053 | 24.9582 | 24.7867 | 24.6438 | 24.4794 | 24.3094 | 24.0218 | 23.7262 | 23.3868 | 23.0439 | 22.6993 | 22.4734 | 22.1763 | 21.894 | 21.6164 | 21.3271 | 20.2614 | 19.1791 | 18.0317
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | 52.2952 | -0.597 | WPD Best View | Headroom (MW) | N/A | 25.006 | 24.9595 | 24.7895 | 24.6486 | 24.4868 | 24.3201 | 24.0368 | 23.7475 | 23.4158 | 23.0828 | 22.75 | 22.5372 | 22.2438 | 21.974 | 21.7056 | 21.4146 | 20.253 | 19.0484 | 17.8254
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Consumer Transformation | Headroom (MW) | Thermal | 8.6222 | 8.5734 | 8.5188 | 8.4683 | 8.3182 | 8.0974 | 7.8508 | 7.6276 | 7.3891 | 7.1555 | 6.9146 | 6.672 | 5.5128 | 5.2844 | 5.0621 | 4.8184 | 2.4495 | -1.1146 | -4.9711
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Leading the Way | Headroom (MW) | Thermal | 8.7141 | 8.6932 | 8.6955 | 8.6106 | 8.5301 | 8.3805 | 8.2291 | 8.1217 | 7.9956 | 7.9015 | 7.7906 | 7.5848 | 7.3767 | 7.1622 | 7.0541 | 4.6613 | 2.5105 | -0.84398 | -3.096
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | Steady Progression | Headroom (MW) | N/A | 8.5698 | 8.551 | 8.5072 | 8.516 | 8.5195 | 8.4997 | 8.4917 | 8.4714 | 8.4546 | 8.4327 | 8.4069 | 8.3056 | 8.1985 | 8.0917 | 7.9909 | 7.906 | 7.7384 | 7.6659 | 7.3485
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | System Transformation | Headroom (MW) | N/A | 8.6284 | 8.6025 | 8.5755 | 8.5621 | 8.5386 | 8.3872 | 8.2193 | 8.0612 | 7.8799 | 7.714 | 7.5393 | 7.3778 | 7.231 | 7.0747 | 6.9308 | 6.7952 | 6.2887 | 3.7289 | 1.9117
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | 52.345 | -0.5483 | WPD Best View | Headroom (MW) | N/A | 8.6292 | 8.6035 | 8.5779 | 8.4738 | 8.3603 | 8.2106 | 8.0371 | 7.876 | 7.6934 | 7.528 | 7.3621 | 7.2021 | 7.0639 | 6.9185 | 6.7685 | 6.634 | 5.987 | 3.0169 | 0.80277
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Consumer Transformation | Headroom (MW) | Thermal | 7.8876 | 7.8201 | 7.6873 | 7.4927 | 7.2919 | 7.0445 | 6.7465 | 6.4524 | 6.1664 | 5.9046 | 5.6041 | 5.3268 | 5.077 | 4.8157 | 3.6565 | 3.3979 | -1.711 | -8.3854 | -15.118
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Leading the Way | Headroom (MW) | Thermal | 7.908 | 7.8645 | 7.7858 | 7.6516 | 7.5154 | 7.3802 | 7.2211 | 7.0926 | 6.9276 | 6.8512 | 6.7434 | 6.6564 | 6.5865 | 5.2631 | 3.4892 | 0.8486 | -6.0559 | -15.97 | -24.8588
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | Steady Progression | Headroom (MW) | Thermal | 7.905 | 7.8555 | 7.7762 | 7.7251 | -2.5677 | -2.6112 | -6.7446 | -10.8844 | -15.0233 | -19.1647 | -22.402 | -25.3604 | -29.5841 | -33.792 | -35.6615 | -35.7449 | -42.369 | -52.0643 | -54.0756
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | System Transformation | Headroom (MW) | Thermal | 7.902 | 7.8492 | 7.7512 | 7.5913 | 7.4171 | 7.2507 | 7.0432 | 6.8482 | 6.6274 | 6.4273 | 6.207 | 6.0043 | 5.8383 | 5.6751 | 5.5336 | 5.3907 | 2.3545 | -2.2116 | -7.0524
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | 52.3921 | -0.5512 | WPD Best View | Headroom (MW) | Thermal | 7.9028 | 7.8502 | 7.7537 | 7.6888 | 7.6124 | 7.5453 | 6.4039 | 5.2777 | 4.1277 | 3 | 2.023 | 1.1313 | -0.054118 | -1.2238 | -1.7983 | -1.9352 | -6.6567 | -15.5321 | -20.41
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Consumer Transformation | Headroom (MW) | Thermal | 42.8387 | 42.3423 | 40.2895 | 39.4272 | 38.2406 | 36.3571 | 33.6047 | 31.0331 | 28.239 | 23.5475 | 17.7956 | 14.8392 | 8.2747 | -2.9364 | -8.1884 | -20.0274 | -49.368 | -89.5619 | -124.3308
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Leading the Way | Headroom (MW) | Thermal | 42.9547 | 42.089 | 41.3319 | 40.7801 | 40.2816 | 31.2474 | 29.7812 | 29.0628 | 25.0623 | 24.0352 | 21.7853 | 19.9418 | 19.2153 | 14.9103 | 8.4255 | -8.0786 | -39.7085 | -70.1742 | -100.5007
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | Steady Progression | Headroom (MW) | Thermal | 42.931 | 42.6142 | 41.923 | 41.5389 | 30.9699 | 30.6919 | 28.2804 | 25.9664 | 23.5284 | 21.0991 | 18.7735 | 17.1088 | 12.0248 | 10.5088 | 9.3233 | 8.9487 | 6.6527 | -3.6913 | -9.7146
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | System Transformation | Headroom (MW) | Thermal | 42.8987 | 42.5918 | 40.7745 | 40.2672 | 39.7766 | 39.2744 | 38.2114 | 37.0488 | 35.4993 | 34.0131 | 29.9698 | 28.608 | 27.3663 | 15.8509 | 14.8672 | 13.8813 | 1.0465 | -19.9045 | -39.4277
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | 52.4017 | -0.7381 | WPD Best View | Headroom (MW) | Thermal | 42.931 | 42.628 | 40.7889 | 40.2311 | 39.6719 | 30.5675 | 29.5414 | 28.4523 | 26.6137 | 25.0723 | 19.9953 | 18.8057 | 17.8326 | 13.6046 | 8.6009 | -2.8033 | -21.6842 | -50.9677 | -75.3542
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Consumer Transformation | Headroom (MW) | Thermal | 10.3734 | 10.265 | 10.0382 | 9.8498 | 9.6267 | 9.3413 | 8.9594 | 8.5584 | 8.1158 | 7.6341 | 7.0762 | 6.6145 | 5.2644 | 4.8633 | 4.507 | 3.2279 | -0.6636 | -6.9449 | -11.4054
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Leading the Way | Headroom (MW) | Thermal | 10.4084 | 10.3422 | 10.1552 | 10.0268 | 9.8746 | 9.693 | 9.4205 | 9.1326 | 8.7384 | 8.3292 | 7.8825 | 7.7039 | 7.5935 | 7.5378 | 4.105 | 3.1275 | -1.3806 | -7.3336 | -12.5825
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | Steady Progression | Headroom (MW) | N/A | 10.3885 | 10.3246 | 10.1832 | 10.1021 | 10.02 | 9.9477 | 9.8615 | 9.7805 | 9.6888 | 9.5958 | 9.4934 | 9.3931 | 9.309 | 9.2236 | 9.1383 | 9.0523 | 9.0095 | 8.9017 | 7.0476
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | System Transformation | Headroom (MW) | Thermal | 10.3914 | 10.3281 | 10.1587 | 10.0558 | 9.9414 | 9.8101 | 9.6318 | 9.4547 | 9.2509 | 9.0474 | 8.8548 | 8.6754 | 8.5041 | 8.3396 | 8.201 | 8.0733 | 7.5154 | 4.3435 | -0.0015513
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | 52.3639 | -0.6952 | WPD Best View | Headroom (MW) | Thermal | 10.4053 | 10.3362 | 10.1438 | 10.0089 | 9.8502 | 9.6609 | 9.3799 | 9.0724 | 8.6627 | 8.2204 | 7.7379 | 7.5116 | 7.3523 | 7.26 | 5.4942 | 4.5096 | 2.5012 | -3.1113 | -6.7951
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Consumer Transformation | Headroom (MW) | Thermal | 10.775 | 10.674 | 10.5044 | 10.3537 | 10.1849 | 9.9588 | 9.704 | 9.396 | 9.075 | 7.8468 | 4.9419 | 4.6071 | 3.3593 | 3.0677 | 1.9038 | 1.6622 | -4.1018 | -11.5039 | -17.4514
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Leading the Way | Headroom (MW) | Thermal | 10.7911 | 10.7352 | 10.6285 | 10.5509 | 10.4644 | 10.3671 | 10.2776 | 10.1407 | 7.369 | 7.2774 | 7.1798 | 6.1962 | 6.1781 | 4.9027 | 4.9174 | 2.2709 | -4.169 | -7.5528 | -13.4626
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | Steady Progression | Headroom (MW) | N/A | 10.7935 | 10.7331 | 10.6182 | 10.5557 | 10.5046 | 10.4484 | 10.4361 | 10.3834 | 10.3308 | 10.2689 | 9.7359 | 9.6811 | 7.0677 | 7.0206 | 7.0017 | 6.9716 | 7.0925 | 5.8951 | 5.4144
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | System Transformation | Headroom (MW) | Thermal | 10.7824 | 10.7182 | 10.5917 | 10.5016 | 10.4105 | 10.3089 | 10.1944 | 10.0485 | 9.8731 | 9.7155 | 6.9906 | 6.8468 | 6.7371 | 5.6988 | 5.6279 | 5.5543 | 4.0666 | 1.0104 | -1.6853
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | 52.2902 | -0.9273 | WPD Best View | Headroom (MW) | Thermal | 10.7845 | 10.7185 | 10.5857 | 10.4798 | 10.3603 | 10.2175 | 10.0349 | 9.7864 | 9.4827 | 9.2432 | 6.4735 | 6.337 | 6.2574 | 5.2554 | 5.2144 | 5.1461 | 3.4401 | 0.14868 | -2.7028
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Consumer Transformation | Headroom (MW) | Thermal | 12.4424 | 12.3449 | 11.1473 | 10.9733 | 10.8306 | 10.6301 | 10.222 | 9.9456 | 9.5204 | 8.2107 | 7.7054 | 7.2867 | 5.953 | 5.5778 | 4.3536 | 3.1222 | -5.1901 | -15.5985 | -27.9409
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Leading the Way | Headroom (MW) | Thermal | 12.4656 | 11.8688 | 11.7591 | 11.6845 | 11.6566 | 11.6333 | 11.3957 | 11.3543 | 11.0736 | 10.9179 | 9.8033 | 9.7253 | 9.6923 | 8.4561 | 5.8758 | 1.6406 | -8.4189 | -19.4455 | -30.4542
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | Steady Progression | Headroom (MW) | N/A | 12.4641 | 12.4246 | 12.3407 | 12.2992 | 12.3018 | 12.3418 | 12.3067 | 12.3379 | 12.308 | 12.2759 | 12.2238 | 12.1922 | 12.1735 | 12.1428 | 12.1414 | 12.1442 | 12.444 | 11.4091 | 9.6241
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | System Transformation | Headroom (MW) | Thermal | 12.4543 | 12.4115 | 11.2723 | 11.1973 | 11.1701 | 11.1658 | 10.9936 | 10.9507 | 10.762 | 10.6022 | 10.4394 | 10.3036 | 10.1891 | 9.164 | 9.0958 | 9.0415 | 6.4138 | -0.17763 | -6.2102
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | 52.4454 | -0.815 | WPD Best View | Headroom (MW) | Thermal | 12.4629 | 12.4233 | 11.2786 | 11.1861 | 11.1441 | 11.1002 | 10.8353 | 10.7521 | 10.4238 | 10.1987 | 9.0159 | 8.8808 | 8.786 | 7.4838 | 4.8679 | 2.3306 | -5.0945 | -15.6477 | -26.2783
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Consumer Transformation | Headroom (MW) | Thermal | 16.0405 | 15.9768 | 15.7615 | 15.5599 | 15.3521 | 15.069 | 14.6487 | 14.2951 | 13.901 | 13.4915 | 13.0532 | 12.6466 | 11.3205 | 10.9479 | 10.6544 | 10.36 | 7.4888 | 1.8911 | -1.1314
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Leading the Way | Headroom (MW) | N/A | 16.0714 | 16.0665 | 15.9301 | 15.8317 | 15.7165 | 15.5803 | 15.3678 | 15.2175 | 15.0003 | 14.8257 | 14.6589 | 14.5563 | 14.4721 | 14.4287 | 14.4303 | 13.4964 | 10.2088 | 6.8719 | 4.2798
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | Steady Progression | Headroom (MW) | Thermal | 16.0688 | 16.0378 | 15.9161 | 15.8496 | 5.5328 | 5.4692 | 3.3444 | 1.2487 | -0.87835 | -3.005 | -4.5086 | -5.8726 | -7.9977 | -9.0901 | -9.9245 | -9.9448 | -11.5371 | -13.6261 | -14.0728
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | System Transformation | Headroom (MW) | N/A | 16.0601 | 16.0361 | 15.8844 | 15.7852 | 15.6632 | 15.5308 | 15.3415 | 15.2017 | 14.9763 | 14.7638 | 14.5578 | 14.3671 | 14.1941 | 14.035 | 13.9457 | 13.8588 | 13.4281 | 10.2541 | 8.5247
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | 52.471 | -0.9335 | WPD Best View | Headroom (MW) | N/A | 16.0601 | 16.0361 | 15.8844 | 15.7852 | 15.6632 | 15.5308 | 15.3415 | 15.2017 | 14.9763 | 14.7638 | 14.5578 | 14.3671 | 14.1941 | 14.035 | 13.9457 | 13.8588 | 13.4281 | 10.2541 | 8.5247
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Consumer Transformation | Headroom (MW) | Thermal | 31.8088 | 31.7171 | 31.5256 | 31.4188 | 31.0221 | 30.1883 | 28.9878 | 27.8278 | 26.6925 | 25.5013 | 24.2409 | 22.9711 | 21.7283 | 20.5063 | 18.3558 | 17.0668 | 9.0574 | 0.42905 | -7.9584
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Leading the Way | Headroom (MW) | N/A | 31.8151 | 31.6899 | 31.5024 | 31.35 | 31.2514 | 31.1579 | 30.5215 | 30.4318 | 30.1138 | 29.9209 | 29.5008 | 29.0322 | 28.5878 | 26.9323 | 26.4487 | 24.3087 | 18.3863 | 13.2527 | 8.11
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | Steady Progression | Headroom (MW) | N/A | 31.8043 | 31.71 | 31.5163 | 31.4027 | 31.299 | 31.1982 | 31.0618 | 30.9629 | 30.8514 | 30.7526 | 30.6421 | 30.5457 | 30.3139 | 30.0673 | 29.8342 | 29.5921 | 28.6726 | 26.6803 | 25.4426
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | System Transformation | Headroom (MW) | N/A | 31.8088 | 31.7173 | 31.526 | 31.4192 | 31.3172 | 31.219 | 30.8567 | 30.2527 | 29.5506 | 28.8516 | 28.1432 | 27.4738 | 26.8384 | 26.2291 | 25.6298 | 25.0134 | 21.1147 | 17.6065 | 13.1494
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | 52.4029 | -0.7286 | WPD Best View | Headroom (MW) | N/A | 31.815 | 31.7274 | 31.5397 | 31.4349 | 31.3362 | 31.2423 | 31.152 | 30.8537 | 30.3011 | 29.8819 | 29.4501 | 28.9684 | 28.5109 | 26.843 | 26.3503 | 24.2119 | 18.3762 | 13.3555 | 8.2884
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Consumer Transformation | Headroom (MW) | N/A | 12.9879 | 12.9537 | 12.9018 | 12.861 | 12.8135 | 12.7587 | 12.6719 | 12.5994 | 12.5237 | 12.4523 | 12.3672 | 12.3025 | 12.2384 | 12.1768 | 12.1131 | 12.0321 | 11.54 | 9.6638 | 9.0553
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Leading the Way | Headroom (MW) | N/A | 12.9924 | 12.9756 | 12.9459 | 12.9256 | 12.9071 | 12.892 | 12.8741 | 12.8621 | 12.8432 | 12.8404 | 12.8361 | 12.804 | 12.7677 | 12.7287 | 12.7246 | 12.7204 | 11.3078 | 9.6761 | 9.2519
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | Steady Progression | Headroom (MW) | N/A | 13.0011 | 12.9731 | 12.9378 | 12.9188 | 12.9009 | 12.8759 | 12.859 | 12.8422 | 12.817 | 12.8002 | 12.7762 | 12.7585 | 12.7477 | 12.7338 | 12.7214 | 12.7225 | 12.7215 | 12.6826 | 12.5478
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | System Transformation | Headroom (MW) | N/A | 12.991 | 12.9698 | 12.9307 | 12.8973 | 12.8634 | 12.8289 | 12.7826 | 12.7298 | 12.6757 | 12.6219 | 12.5733 | 12.5305 | 12.4927 | 12.4606 | 12.4431 | 12.4161 | 12.3186 | 10.8693 | 10.6059
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | 52.425 | -0.7351 | WPD Best View | Headroom (MW) | N/A | 12.9924 | 12.9756 | 12.9459 | 12.9256 | 12.9071 | 12.892 | 12.8741 | 12.8621 | 12.8432 | 12.8404 | 12.8361 | 12.8168 | 12.808 | 12.8035 | 12.8046 | 12.7827 | 11.3078 | 9.6761 | 9.2519
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Consumer Transformation | Headroom (MW) | Thermal | 30.0269 | 29.7562 | 29.3591 | 28.9537 | 28.5226 | 27.9166 | 26.9844 | 26.1492 | 24.3421 | 22.6117 | 20.7371 | 17.9292 | 16.1046 | 13.361 | 10.0689 | 6.5242 | -21.9137 | -53.3053 | -98.9267
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Leading the Way | Headroom (MW) | Thermal | 30.0995 | 29.9394 | 29.7327 | 29.5942 | 29.4413 | 29.3324 | 29.0107 | 28.8392 | 28.55 | 28.4499 | 27.4528 | 25.1226 | 24.1229 | 19.6936 | 12.9176 | 3.4982 | -28.4499 | -71.8223 | -102.7739
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | Steady Progression | Headroom (MW) | N/A | 30.103 | 29.9674 | 29.786 | 29.6652 | 29.5491 | 29.4634 | 29.3589 | 29.2385 | 29.1082 | 28.9782 | 28.8259 | 28.7277 | 28.637 | 28.5689 | 28.5733 | 28.5911 | 27.7812 | 25.594 | 16.3356
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | System Transformation | Headroom (MW) | Thermal | 30.0742 | 29.9223 | 29.654 | 29.4445 | 29.1931 | 28.9553 | 28.4856 | 28.0516 | 27.5241 | 27.04 | 26.6011 | 25.2893 | 24.9761 | 24.6808 | 22.7874 | 21.6817 | 10.7293 | -7.7766 | -31.6234
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | 52.537 | -1.0237 | WPD Best View | Headroom (MW) | Thermal | 30.0768 | 29.9286 | 29.6681 | 29.469 | 29.2311 | 29.0107 | 28.5634 | 28.161 | 27.6648 | 27.2274 | 26.8366 | 25.5689 | 25.3003 | 25.0478 | 21.4847 | 20.3694 | 6.8728 | -13.3386 | -37.4948
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Consumer Transformation | Headroom (MW) | Thermal | 2.8248 | 2.769 | 2.704 | 2.6533 | 2.6036 | 2.5282 | 2.4028 | 2.2979 | 1.2434 | 1.1628 | 1.0131 | -0.066587 | -1.1428 | -1.2839 | -2.2681 | -3.2644 | -9.2698 | -15.6508 | -24.3264
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Leading the Way | Headroom (MW) | Thermal | 2.83 | 2.8046 | 2.7622 | 2.7504 | 2.7412 | 2.7333 | 2.7053 | 2.7045 | 2.6822 | 2.7071 | 1.7614 | 1.7518 | 1.7481 | 0.82929 | -0.82365 | -2.5078 | -7.0787 | -13.3528 | -20.7247
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | Steady Progression | Headroom (MW) | N/A | 2.8337 | 2.796 | 2.7618 | 2.7376 | 2.7193 | 2.7083 | 2.6903 | 2.6733 | 2.6613 | 2.6395 | 2.631 | 2.619 | 2.6132 | 2.6151 | 2.6258 | 2.6493 | 2.7963 | 2.9204 | 1.4034
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | System Transformation | Headroom (MW) | Thermal | 2.8263 | 2.7935 | 2.7418 | 2.7121 | 2.6787 | 2.6427 | 2.5685 | 2.5112 | 2.4355 | 2.3758 | 2.3213 | 1.3429 | 1.3245 | 1.3028 | 1.3009 | 1.3042 | -0.84211 | -2.3444 | -6.2828
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | 52.4887 | -1.1162 | WPD Best View | Headroom (MW) | Thermal | 2.8263 | 2.7935 | 2.7418 | 2.7121 | 2.6787 | 2.6427 | 2.5685 | 2.5112 | 2.4355 | 2.3758 | 2.3213 | 1.3429 | 1.3245 | 1.3028 | 1.3009 | 1.3042 | -0.84211 | -2.3444 | -6.2828
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Consumer Transformation | Headroom (MW) | Thermal | 12.6886 | 12.6083 | 12.4772 | 12.3243 | 12.1595 | 11.9329 | 11.6102 | 11.3209 | 11.0194 | 9.8091 | 9.5123 | 9.1841 | 8.8906 | 7.6636 | 5.7116 | 4.5038 | -1.8661 | -13.3703 | -23.9667
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Leading the Way | Headroom (MW) | Thermal | 12.7197 | 12.6455 | 12.5981 | 12.5333 | 12.4756 | 12.4266 | 12.3042 | 12.2492 | 12.167 | 12.1499 | 12.1641 | 9.9246 | 9.9102 | 8.6327 | 6.9253 | 2.6399 | -7.654 | -21.0798 | -33.3457
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | Steady Progression | Headroom (MW) | N/A | 12.7167 | 12.6808 | 12.6351 | 12.597 | 12.5509 | 12.5204 | 12.4872 | 12.4425 | 12.3936 | 12.3403 | 12.2937 | 12.2542 | 12.2204 | 12.1913 | 12.1857 | 12.1832 | 11.0391 | 9.8895 | 8.1494
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | System Transformation | Headroom (MW) | Thermal | 12.7078 | 12.6667 | 12.5995 | 12.5236 | 12.4387 | 12.3508 | 12.1775 | 12.0182 | 11.8342 | 11.6614 | 11.518 | 11.3771 | 11.2497 | 11.1505 | 9.3737 | 8.3714 | 5.5773 | -1.3699 | -9.5233
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | 52.5372 | -1.0234 | WPD Best View | Headroom (MW) | Thermal | 12.7085 | 12.6679 | 12.6023 | 12.5283 | 12.4461 | 12.3614 | 12.1925 | 12.0394 | 11.8632 | 11.7004 | 11.5687 | 11.4409 | 11.3265 | 11.2398 | 9.4721 | 8.4682 | 5.5874 | -1.4727 | -9.7017
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Consumer Transformation | Headroom (MW) | Thermal | 12.1145 | 11.9799 | 11.7788 | 11.577 | 11.3605 | 11.0566 | 10.5724 | 10.1313 | 9.6802 | 9.2408 | 7.8127 | 6.4126 | 5.9578 | 4.5823 | 4.2264 | 2.8858 | -7.4708 | -20.9771 | -34.1616
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Leading the Way | Headroom (MW) | Thermal | 12.1507 | 12.0902 | 11.9735 | 11.9114 | 11.8254 | 11.7735 | 11.6022 | 11.4865 | 11.3018 | 11.1938 | 11.1284 | 11.0472 | 10.0656 | 7.8326 | 4.417 | 0.96703 | -11.5514 | -24.2532 | -35.567
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | Steady Progression | Headroom (MW) | N/A | 12.1537 | 12.0916 | 11.9901 | 11.9316 | 11.8799 | 11.8357 | 11.7824 | 11.7237 | 11.6544 | 11.5994 | 11.5022 | 11.4556 | 11.4043 | 11.3635 | 11.3628 | 11.3597 | 11.5468 | 10.385 | 7.2367
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | System Transformation | Headroom (MW) | Thermal | 12.1411 | 12.0631 | 11.9136 | 11.8098 | 11.6767 | 11.5628 | 11.3406 | 11.1232 | 10.8554 | 10.6037 | 10.3628 | 10.1703 | 10.0029 | 9.8284 | 9.7138 | 9.607 | 3.5951 | -3.6084 | -9.878
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | 52.4794 | -0.9025 | WPD Best View | Headroom (MW) | Thermal | 12.143 | 12.0681 | 11.925 | 11.8295 | 11.7073 | 11.6075 | 11.4034 | 11.2114 | 10.9671 | 10.7521 | 10.5476 | 10.3861 | 10.2502 | 10.1062 | 8.3127 | 8.198 | -0.27159 | -9.0676 | -15.5711
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Consumer Transformation | Headroom (MW) | Thermal | 30.6834 | 30.404 | 29.9279 | 29.5039 | 29.052 | 28.4449 | 27.5706 | 25.7769 | 24.7178 | 23.6977 | 19.654 | 18.403 | 16.1967 | 14.0027 | 8.426 | 5.4008 | -13.9693 | -44.763 | -73.6216
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Leading the Way | Headroom (MW) | Thermal | 30.7409 | 30.5601 | 30.2432 | 30.0017 | 29.7501 | 29.4858 | 28.9689 | 28.6265 | 28.0848 | 27.7473 | 26.2642 | 24.4047 | 23.802 | 16.6042 | 10.2288 | 2.813 | -25.2281 | -56.2009 | -84.1655
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | Steady Progression | Headroom (MW) | N/A | 30.7374 | 30.5612 | 30.249 | 30.065 | 29.8766 | 29.7035 | 29.5239 | 29.3292 | 29.0974 | 28.9251 | 28.7004 | 28.4899 | 28.303 | 28.1145 | 27.9413 | 27.8017 | 26.1202 | 22.1104 | 19.3924
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | System Transformation | Headroom (MW) | Thermal | 30.7227 | 30.5291 | 30.169 | 29.8991 | 29.6035 | 29.3038 | 28.8537 | 28.4016 | 27.896 | 27.4374 | 26.0571 | 25.6234 | 25.1344 | 24.6515 | 22.5295 | 22.1006 | 11.4259 | -5.3125 | -21.4405
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | 52.7647 | -0.8698 | WPD Best View | Headroom (MW) | N/A | 30.739 | 30.5654 | 30.2576 | 30.0813 | 29.9 | 29.7376 | 29.5781 | 29.3913 | 29.1881 | 29.0466 | 28.8641 | 28.6943 | 28.5605 | 28.4336 | 28.3345 | 28.2362 | 25.2198 | 20.7526 | 16.5827
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Consumer Transformation | Headroom (MW) | Thermal | 4.3631 | 4.3044 | 4.1987 | 4.107 | 4.0134 | 3.8859 | 3.7196 | 3.5661 | 3.4125 | 3.3058 | 2.2415 | 2.1158 | 1.9548 | 1.7866 | 1.643 | 0.58744 | -2.573 | -7.9189 | -10.8028
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Leading the Way | Headroom (MW) | Thermal | 4.3731 | 4.3376 | 4.2527 | 4.1971 | 4.1378 | 4.0793 | 3.9936 | 3.9361 | 3.8642 | 3.8746 | 3.8807 | 3.8853 | 3.8471 | 1.5993 | 1.5339 | -0.19524 | -4.1144 | -9.1502 | -13.322
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | Steady Progression | Headroom (MW) | N/A | 4.3688 | 4.3315 | 4.2575 | 4.2182 | 4.1703 | 4.1322 | 4.0923 | 4.0425 | 3.9921 | 3.9745 | 3.9452 | 3.9181 | 3.879 | 3.8454 | 3.814 | 3.8097 | 3.7131 | 2.4358 | 2.2344
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | System Transformation | Headroom (MW) | Thermal | 4.3684 | 4.3295 | 4.2414 | 4.1839 | 4.1227 | 4.0589 | 3.9675 | 3.8782 | 3.7848 | 3.7245 | 3.6755 | 3.6298 | 3.5504 | 3.4778 | 3.4211 | 3.3889 | 0.94614 | -1.8513 | -3.1677
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | 52.7753 | -0.9198 | WPD Best View | Headroom (MW) | N/A | 4.3688 | 4.3315 | 4.2575 | 4.2182 | 4.1703 | 4.1322 | 4.0923 | 4.0425 | 3.9921 | 3.9745 | 3.9452 | 3.9181 | 3.879 | 3.8454 | 3.814 | 3.8097 | 3.7131 | 2.4358 | 2.2344
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Consumer Transformation | Headroom (MW) | Thermal | 13.5485 | 13.3969 | 13.154 | 12.8893 | 12.6073 | 12.1998 | 11.6295 | 10.1268 | 9.51 | 8.888 | 7.181 | 6.3829 | 4.6528 | 2.9277 | -1.3358 | -3.025 | -15.4364 | -33.3513 | -50.4609
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Leading the Way | Headroom (MW) | Thermal | 13.5912 | 13.5089 | 13.3828 | 13.2579 | 13.1156 | 12.945 | 12.6721 | 12.4151 | 12.0328 | 11.7203 | 10.3838 | 8.6806 | 8.255 | 5.6573 | 1.0452 | -2.8398 | -20.0295 | -38.6923 | -55.3315
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | Steady Progression | Headroom (MW) | N/A | 13.5877 | 13.5168 | 13.3944 | 13.3083 | 13.2214 | 13.1386 | 13.057 | 12.9598 | 12.8343 | 12.7218 | 12.5771 | 12.4459 | 12.3247 | 12.1999 | 12.079 | 11.9513 | 10.3898 | 9.0146 | 7.0632
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | System Transformation | Headroom (MW) | Thermal | 13.5819 | 13.4869 | 13.3317 | 13.1854 | 13.016 | 12.8333 | 12.546 | 12.254 | 11.9159 | 11.5841 | 10.312 | 9.9789 | 9.6655 | 9.362 | 7.3892 | 7.0863 | 1.3283 | -8.2479 | -17.1186
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | 52.7644 | -0.8697 | WPD Best View | Headroom (MW) | N/A | 13.5879 | 13.5179 | 13.3964 | 13.312 | 13.2267 | 13.1467 | 13.0659 | 12.9634 | 12.8458 | 12.7428 | 12.6116 | 12.4908 | 12.3884 | 12.2917 | 12.2142 | 12.1139 | 9.3226 | 7.6517 | 4.2538
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Consumer Transformation | Headroom (MW) | Thermal | 6.9549 | 6.9186 | 6.8524 | 6.8118 | 6.7623 | 6.7067 | 6.6224 | 6.5664 | 6.4964 | 6.433 | 5.4184 | 5.3497 | 5.2942 | 5.2421 | 4.3006 | 4.2699 | 1.5429 | -5.0038 | -11.6613
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Leading the Way | Headroom (MW) | Thermal | 6.9589 | 6.9367 | 6.8898 | 6.865 | 6.8382 | 6.8125 | 6.786 | 6.7788 | 6.7555 | 6.7403 | 6.7247 | 6.7365 | 6.7607 | 4.6027 | 2.9574 | 1.2806 | -5.0522 | -10.5152 | -17.0653
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | Steady Progression | Headroom (MW) | N/A | 6.9645 | 6.9298 | 6.877 | 6.8497 | 6.8255 | 6.7952 | 6.7761 | 6.7566 | 6.7308 | 6.716 | 6.6954 | 6.6695 | 6.6702 | 6.6654 | 6.6691 | 6.6851 | 6.8077 | 5.6389 | 5.3822
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | System Transformation | Headroom (MW) | Thermal | 6.9554 | 6.9286 | 6.8733 | 6.8344 | 6.7961 | 6.7595 | 6.7184 | 6.6734 | 6.6257 | 6.5837 | 6.548 | 6.5163 | 6.505 | 6.5043 | 6.5148 | 6.5304 | 4.4578 | 0.4631 | -3.788
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | 52.7981 | -0.9851 | WPD Best View | Headroom (MW) | N/A | 6.966 | 6.9329 | 6.8835 | 6.8608 | 6.8423 | 6.8198 | 6.8106 | 6.8043 | 6.796 | 6.8024 | 6.8072 | 6.8116 | 6.8447 | 6.8734 | 6.9078 | 6.9378 | 6.9261 | 5.5193 | 5.0814
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Consumer Transformation | Headroom (MW) | N/A | 14.817 | 14.7841 | 14.7228 | 14.6957 | 14.6691 | 14.6526 | 14.5991 | 14.5176 | 14.2989 | 14.071 | 13.8131 | 13.5546 | 13.2949 | 13.0464 | 12.8182 | 12.5685 | 11.4973 | 10.511 | 8.3034
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Leading the Way | Headroom (MW) | N/A | 14.8177 | 14.7769 | 14.7179 | 14.6818 | 14.6585 | 14.649 | 14.5173 | 14.4965 | 14.4324 | 14.412 | 14.2751 | 14.1023 | 13.9392 | 13.745 | 13.6924 | 13.5675 | 12.968 | 11.1569 | 10.5533
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | Steady Progression | Headroom (MW) | N/A | 14.8163 | 14.7831 | 14.7201 | 14.6888 | 14.6593 | 14.6375 | 14.5985 | 14.5703 | 14.5402 | 14.5128 | 14.4827 | 14.4564 | 14.4292 | 14.4039 | 14.3793 | 14.3555 | 14.2095 | 14.0211 | 13.7125
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | System Transformation | Headroom (MW) | N/A | 14.817 | 14.7841 | 14.7227 | 14.6955 | 14.6687 | 14.652 | 14.6218 | 14.596 | 14.5696 | 14.5451 | 14.5215 | 14.4985 | 14.4135 | 14.3073 | 14.2043 | 14.095 | 13.6936 | 13.3236 | 11.6338
Grendon 132kV | Melton Mowbray | REGENT STREET 33 11kV S STN | Primary | 11 | 52.7636 | -0.8797 | WPD Best View | Headroom (MW) | N/A | 14.8163 | 14.7831 | 14.7201 | 14.6903 | 14.6608 | 14.639 | 14.6094 | 14.5812 | 14.5543 | 14.5269 | 14.5001 | 14.4738 | 14.4484 | 14.4231 | 14.3985 | 14.3748 | 14.258 | 14.1458 | 14.013
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Consumer Transformation | Headroom (MW) | Thermal | 56.1796 | 55.8332 | 55.2198 | 54.7142 | 54.0762 | 52.9205 | 51.4266 | 49.9989 | 48.6973 | 47.2907 | 44.8017 | 43.318 | 41.8796 | 39.5515 | 33.5733 | 32.0727 | 17.5997 | 2.824 | -14.0506
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Leading the Way | Headroom (MW) | N/A | 56.2504 | 55.8171 | 55.437 | 55.2911 | 55.1333 | 54.7732 | 54.1706 | 53.9126 | 53.6285 | 53.38 | 53.0835 | 52.7348 | 51.4673 | 49.7817 | 45.1164 | 43.0604 | 33.8446 | 23.2487 | 9.4772
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | Steady Progression | Headroom (MW) | N/A | 56.2308 | 55.9811 | 55.5147 | 55.2871 | 55.0704 | 54.8059 | 54.5715 | 54.3366 | 54.0986 | 53.8707 | 53.0005 | 52.2288 | 52.0128 | 51.7974 | 51.6235 | 51.4589 | 50.9974 | 47.3418 | 44.0247
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | System Transformation | Headroom (MW) | N/A | 56.2296 | 55.9777 | 55.4873 | 55.2361 | 54.9343 | 54.5351 | 53.8364 | 53.1226 | 52.3131 | 51.5258 | 50.7145 | 49.9721 | 49.3454 | 48.7747 | 48.2716 | 47.7593 | 40.2176 | 34.4052 | 26.4342
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | 52.2301 | -0.8835 | WPD Best View | Headroom (MW) | N/A | 56.2504 | 55.8279 | 55.4452 | 55.3106 | 55.1528 | 54.7927 | 54.4418 | 54.0969 | 53.6655 | 53.4169 | 53.1283 | 52.7974 | 51.5499 | 50.0333 | 45.2219 | 43.1659 | 34.0069 | 23.2487 | 9.4772
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Consumer Transformation | Headroom (MW) | N/A | 17.0535 | 17.0569 | 17.0042 | 17.0023 | 16.9427 | 16.8903 | 16.8375 | 16.7955 | 16.7457 | 16.67 | 16.5549 | 16.4502 | 16.3648 | 16.2727 | 16.184 | 16.078 | 15.378 | 14.4461 | 13.4584
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Leading the Way | Headroom (MW) | N/A | 17.0535 | 17.0758 | 17.0444 | 17.0596 | 17.0014 | 16.9486 | 16.8833 | 16.8401 | 16.7881 | 16.7364 | 16.6801 | 16.6174 | 16.5552 | 16.4918 | 16.4517 | 16.4119 | 16.1169 | 15.6914 | 13.6202
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | Steady Progression | Headroom (MW) | N/A | 17.0534 | 17.0401 | 16.9712 | 16.9527 | 16.8963 | 16.8436 | 16.7915 | 16.7421 | 16.6913 | 16.6411 | 16.5906 | 16.5419 | 16.4937 | 16.4468 | 16.4 | 16.3536 | 16.1123 | 15.9165 | 15.6195
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | System Transformation | Headroom (MW) | N/A | 17.0534 | 17.0567 | 17.0038 | 17.0016 | 16.9415 | 16.8884 | 16.8402 | 16.7965 | 16.75 | 16.7007 | 16.6504 | 16.6004 | 16.5525 | 16.5069 | 16.4626 | 16.42 | 16.2099 | 15.843 | 15.2786
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | 52.2238 | -0.8666 | WPD Best View | Headroom (MW) | N/A | 17.0535 | 17.0791 | 17.0477 | 17.067 | 17.0088 | 16.956 | 16.9136 | 16.8704 | 16.8251 | 16.7733 | 16.7248 | 16.68 | 16.6377 | 16.5972 | 16.5572 | 16.5174 | 16.2792 | 15.6914 | 13.6202
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Consumer Transformation | Headroom (MW) | Fault level | 10.5639 | 10.4286 | 10.2596 | 10.0222 | 9.7811 | 9.4063 | 8.8483 | 8.3033 | 7.7634 | 7.1723 | 6.5463 | 5.9053 | 5.2609 | 4.604 | 3.9358 | 3.2397 | -0.3551 | -3.7115 | -6.712
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Leading the Way | Headroom (MW) | N/A | 10.5293 | 10.4676 | 10.4009 | 10.3005 | 10.2059 | 10.0939 | 9.8776 | 9.6997 | 9.4566 | 9.2332 | 8.9886 | 8.6974 | 8.3918 | 8.0979 | 7.7673 | 7.4569 | 6.0595 | 4.8251 | 3.7759
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | Steady Progression | Headroom (MW) | N/A | 8.7816 | 8.7453 | 8.7188 | 8.6826 | 8.6566 | 8.6253 | 8.5908 | 8.541 | 8.4817 | 8.4134 | 8.3262 | 8.2469 | 8.1692 | 8.0867 | 8.0114 | 7.9327 | 7.4932 | 7.0827 | 6.6539
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | System Transformation | Headroom (MW) | N/A | 10.2321 | 10.1742 | 10.0953 | 9.9956 | 9.883 | 9.7518 | 9.5066 | 9.2688 | 8.9787 | 8.6888 | 8.3884 | 8.0935 | 7.8015 | 7.5068 | 7.2091 | 6.8944 | 5.4324 | 4.2896 | 3.4584
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | 52.243 | -0.8967 | WPD Best View | Headroom (MW) | N/A | 10.0749 | 10.0159 | 9.9521 | 9.856 | 9.7655 | 9.6584 | 9.4514 | 9.2811 | 9.0486 | 8.8348 | 8.6007 | 8.322 | 8.0297 | 7.7484 | 7.4321 | 7.1351 | 5.798 | 4.6169 | 3.613
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Consumer Transformation | Headroom (MW) | N/A | 17.6546 | 17.5306 | 17.2991 | 17.1796 | 17.0462 | 16.726 | 16.3125 | 15.8728 | 15.5 | 15.1009 | 14.6826 | 14.2533 | 13.8371 | 13.4204 | 13.0138 | 12.5648 | 10.2776 | 7.9409 | 5.7746
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Leading the Way | Headroom (MW) | N/A | 17.6732 | 17.6187 | 17.4657 | 17.4751 | 17.4656 | 17.3122 | 17.1177 | 16.9092 | 16.7517 | 16.6208 | 16.4659 | 16.2973 | 16.1314 | 15.9814 | 15.8006 | 15.6192 | 16.6655 | 15.5517 | 13.121
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | Steady Progression | Headroom (MW) | N/A | 17.6643 | 17.6141 | 17.476 | 17.4416 | 17.4144 | 17.3319 | 17.2492 | 17.1568 | 17.0682 | 16.9664 | 16.6852 | 16.438 | 16.3417 | 16.2456 | 16.1474 | 16.0542 | 15.7077 | 15.3871 | 14.7955
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | System Transformation | Headroom (MW) | N/A | 17.6681 | 17.608 | 17.4446 | 17.405 | 17.3468 | 17.2011 | 16.9783 | 16.7655 | 16.5437 | 16.3126 | 16.0708 | 15.8055 | 15.5834 | 15.3727 | 15.1739 | 14.9573 | 14.0705 | 13.1807 | 12.318
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | 52.2457 | -0.9135 | WPD Best View | Headroom (MW) | N/A | 17.6732 | 17.6214 | 17.4657 | 17.4751 | 17.4656 | 17.3122 | 17.1177 | 16.9092 | 16.7517 | 16.6208 | 16.4659 | 16.2973 | 16.1314 | 15.9814 | 15.8006 | 15.6192 | 16.6655 | 15.5517 | 13.121
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Consumer Transformation | Headroom (MW) | N/A | 10.6048 | 10.5755 | 10.5163 | 10.4871 | 10.4602 | 10.4365 | 10.416 | 10.3994 | 10.3883 | 10.3817 | 10.3803 | 10.3859 | 10.3967 | 10.4115 | 10.4277 | 10.4357 | 10.3763 | 10.1166 | 9.7936
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Leading the Way | Headroom (MW) | N/A | 10.6061 | 10.5767 | 10.5171 | 10.4886 | 10.4621 | 10.4394 | 10.4206 | 10.4072 | 10.3998 | 10.3997 | 10.4067 | 10.4209 | 10.4406 | 10.4637 | 10.4856 | 10.4893 | 10.3625 | 13.0984 | 12.6856
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | Steady Progression | Headroom (MW) | N/A | 10.6026 | 10.5718 | 10.5095 | 10.4764 | 10.4444 | 10.4135 | 10.3844 | 10.3566 | 10.33 | 10.3055 | 9.8356 | 9.4062 | 9.3891 | 9.3744 | 9.3627 | 9.3544 | 9.3482 | 9.335 | 9.1483
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | System Transformation | Headroom (MW) | N/A | 10.6033 | 10.5731 | 10.5108 | 10.4786 | 10.4471 | 10.4178 | 10.3902 | 10.3644 | 10.3414 | 10.3214 | 10.3047 | 10.2926 | 10.2862 | 10.2844 | 10.288 | 10.2949 | 10.3415 | 10.2274 | 9.9658
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | 52.2176 | -0.9577 | WPD Best View | Headroom (MW) | N/A | 10.6061 | 10.5767 | 10.5171 | 10.4886 | 10.4621 | 10.4394 | 10.4206 | 10.4072 | 10.3998 | 10.3997 | 10.4067 | 10.4209 | 10.4406 | 10.4637 | 10.4856 | 10.4893 | 10.3625 | 13.0984 | 12.6856
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Consumer Transformation | Headroom (MW) | Thermal | 5.4838 | 5.4394 | 5.3614 | 5.2991 | 5.243 | 5.1635 | 5.0324 | 4.9247 | 4.8215 | 4.7252 | 3.6725 | 3.5559 | 3.4557 | 3.3633 | 2.3737 | 2.2821 | -1.7113 | -7.2928 | -12.9224
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Leading the Way | Headroom (MW) | Thermal | 5.5007 | 5.4711 | 5.4265 | 5.4084 | 5.3989 | 5.3926 | 5.3623 | 5.3619 | 5.3626 | 5.3959 | 5.4109 | 5.4248 | 4.5184 | 3.2747 | 3.3082 | 1.6267 | -4.1265 | -9.6365 | -14.0482
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | Steady Progression | Headroom (MW) | N/A | 5.5 | 5.4652 | 5.4164 | 5.3915 | 5.3605 | 5.3408 | 5.3215 | 5.2978 | 5.2733 | 5.256 | 5.2378 | 5.2105 | 5.2022 | 5.2031 | 5.212 | 5.2261 | 5.3514 | 4.2008 | 3.9428
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | System Transformation | Headroom (MW) | Thermal | 5.4972 | 5.4597 | 5.3959 | 5.353 | 5.3083 | 5.2689 | 5.1981 | 5.1251 | 5.053 | 4.9815 | 4.9092 | 4.8483 | 4.8223 | 4.7958 | 4.7868 | 4.7748 | 2.6009 | -0.18028 | -3.1989
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | 52.1522 | -0.8911 | WPD Best View | Headroom (MW) | Thermal | 5.5007 | 5.4711 | 5.4265 | 5.4084 | 5.3989 | 5.3926 | 5.3623 | 5.3619 | 5.3626 | 5.3959 | 5.4109 | 5.4248 | 4.5184 | 3.2747 | 3.3082 | 1.6267 | -4.1265 | -9.6365 | -14.0482
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Consumer Transformation | Headroom (MW) | N/A | 15.3674 | 15.2647 | 15.0927 | 14.9433 | 14.7804 | 14.566 | 14.3407 | 14.1474 | 13.9885 | 13.8138 | 13.6119 | 13.4647 | 13.3088 | 12.2596 | 12.1721 | 12.0537 | 8.6891 | 7.1127 | 3.122
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Leading the Way | Headroom (MW) | N/A | 15.4 | 15.1093 | 15.0045 | 14.9395 | 14.8755 | 14.8041 | 14.7903 | 14.8385 | 14.8841 | 14.9992 | 15.1397 | 15.2689 | 15.3974 | 15.4082 | 14.0033 | 14.1535 | 11.6817 | 7.129 | 4.3553
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | Steady Progression | Headroom (MW) | N/A | 15.3959 | 15.3266 | 15.2233 | 15.1628 | 15.1149 | 15.0884 | 15.0949 | 15.1025 | 15.1075 | 15.1234 | 15.1256 | 15.1559 | 15.2048 | 15.2619 | 15.3325 | 15.403 | 15.8829 | 16.0489 | 14.8281
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | System Transformation | Headroom (MW) | N/A | 15.3921 | 15.3141 | 15.186 | 15.1057 | 15.0071 | 14.9329 | 14.8585 | 14.8063 | 14.7237 | 14.661 | 14.6042 | 14.6024 | 14.6106 | 14.6472 | 14.7072 | 14.7839 | 13.7322 | 13.4927 | 11.5088
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | 52.2054 | -0.8743 | WPD Best View | Headroom (MW) | N/A | 15.4 | 15.1093 | 15.0045 | 14.9395 | 14.8755 | 14.8041 | 14.7903 | 14.8385 | 14.8841 | 14.9992 | 15.1397 | 15.2689 | 15.3974 | 15.5543 | 14.0033 | 14.1535 | 11.6817 | 7.129 | 4.3553
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Consumer Transformation | Headroom (MW) | Thermal | 46.5207 | 46.0949 | 45.2834 | 44.5973 | 43.858 | 42.7855 | 41.2124 | 39.7234 | 38.3009 | 35.9658 | 34.3773 | 31.9909 | 29.6882 | 28.2809 | 25.3354 | 21.9331 | 0.77759 | -25.2804 | -56.3435
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Leading the Way | Headroom (MW) | Thermal | 46.6177 | 46.4076 | 46.0101 | 45.8164 | 45.5911 | 45.3666 | 44.7484 | 44.5324 | 44.0927 | 44.0251 | 43.6592 | 40.8362 | 40.1731 | 38.2736 | 32.1602 | 26.0591 | -0.92395 | -24.5673 | -48.6442
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | Steady Progression | Headroom (MW) | N/A | 46.5989 | 46.3831 | 45.9709 | 45.773 | 45.5318 | 45.3313 | 45.1012 | 44.8624 | 44.6174 | 44.3515 | 44.0285 | 43.7928 | 43.6091 | 43.5109 | 43.4563 | 43.3996 | 42.5472 | 40.5674 | 36.8853
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | System Transformation | Headroom (MW) | Thermal | 46.5743 | 46.3335 | 45.7981 | 45.4343 | 44.9657 | 44.4772 | 43.6387 | 42.8808 | 41.9478 | 41.1268 | 40.2664 | 39.5738 | 38.9771 | 38.4548 | 35.4352 | 34.9986 | 28.9312 | 16.2579 | -1.7384
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | 52.2431 | -0.8368 | WPD Best View | Headroom (MW) | Thermal | 46.5999 | 46.4043 | 45.9956 | 45.8367 | 45.6113 | 45.3992 | 44.9333 | 44.7429 | 44.3832 | 44.3049 | 44.1108 | 41.6656 | 41.4159 | 39.9403 | 34.7663 | 30.2881 | 9.2011 | -11.8697 | -33.842
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Consumer Transformation | Headroom (MW) | N/A | 21.0209 | 20.9049 | 20.7387 | 20.5074 | 20.2519 | 19.8728 | 19.3355 | 18.7922 | 18.2351 | 17.6468 | 16.9846 | 16.3074 | 15.6171 | 14.9129 | 14.251 | 12.5706 | 9.4032 | 5.75 | 2.3764
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Leading the Way | Headroom (MW) | N/A | 20.9092 | 20.8495 | 20.7627 | 20.643 | 20.4855 | 20.2974 | 19.9796 | 19.6802 | 19.2771 | 18.9455 | 18.5844 | 18.2157 | 17.84 | 17.487 | 17.1069 | 16.7433 | 14.36 | 13.2682 | 11.1354
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | Steady Progression | Headroom (MW) | N/A | 17.4214 | 17.3886 | 17.3606 | 17.3283 | 17.289 | 17.2485 | 17.2076 | 17.149 | 17.0828 | 17.0131 | 16.92 | 16.8332 | 16.7424 | 16.6475 | 16.5559 | 16.4408 | 15.9991 | 15.6444 | 15.224
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | System Transformation | Headroom (MW) | N/A | 20.3207 | 20.2684 | 20.1886 | 20.0959 | 19.9754 | 19.8411 | 19.609 | 19.3799 | 19.1131 | 18.8453 | 18.5637 | 18.2821 | 17.9998 | 17.6986 | 17.4064 | 17.0934 | 15.7913 | 14.8891 | 14.1861
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | 52.2715 | -0.8579 | WPD Best View | Headroom (MW) | N/A | 20.0096 | 19.9656 | 19.9078 | 19.845 | 19.7628 | 19.6722 | 19.4959 | 19.3588 | 19.1743 | 19.0099 | 18.8177 | 18.566 | 18.2971 | 18.0276 | 17.7306 | 17.4514 | 16.348 | 15.4286 | 14.5585
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Consumer Transformation | Headroom (MW) | Thermal | 3.4983 | 3.4799 | 3.4516 | 3.4162 | 3.4082 | 3.3779 | 3.3213 | 3.2928 | 3.2647 | 3.2717 | 3.2607 | 2.3523 | 2.3944 | 2.4322 | 2.4973 | 2.532 | 0.016168 | -4.0386 | -8.6126
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Leading the Way | Headroom (MW) | Thermal | 3.5045 | 3.5038 | 3.4918 | 3.4997 | 3.5272 | 3.5552 | 3.5711 | 3.6388 | 3.6991 | 3.8077 | 3.8967 | 3.9162 | 3.8826 | 3.8479 | 1.8123 | 0.20406 | -3.3441 | -6.6776 | -9.9624
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | Steady Progression | Headroom (MW) | N/A | 3.5005 | 3.4914 | 3.4733 | 3.459 | 3.4562 | 3.4574 | 3.4658 | 3.4633 | 3.4757 | 3.4843 | 3.4966 | 3.5168 | 3.5447 | 3.5947 | 3.65 | 3.7169 | 3.9466 | 3.249 | 3.0426
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | System Transformation | Headroom (MW) | Thermal | 3.4992 | 3.4888 | 3.4579 | 3.4386 | 3.4286 | 3.4183 | 3.374 | 3.3603 | 3.3187 | 3.3065 | 3.2977 | 3.3186 | 3.359 | 3.4197 | 3.5015 | 3.5845 | 2.8096 | 0.55454 | -2.4818
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | 52.2176 | -0.7764 | WPD Best View | Headroom (MW) | Thermal | 3.5037 | 3.5026 | 3.489 | 3.495 | 3.5198 | 3.5445 | 3.5561 | 3.6176 | 3.67 | 3.7687 | 3.8459 | 3.9564 | 4.0343 | 4.0434 | 1.7139 | 0.10728 | -3.3525 | -6.5729 | -9.7822
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Consumer Transformation | Headroom (MW) | Thermal | 5.9202 | 5.8861 | 5.8225 | 5.7684 | 5.7177 | 5.633 | 5.5109 | 5.3994 | 5.2951 | 5.1967 | 5.0946 | 5.0117 | 4.9444 | 4.8609 | 4.8012 | 4.7105 | 0.46985 | 0.030008 | -2.9319
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Leading the Way | Headroom (MW) | Thermal | 5.9302 | 5.9167 | 5.8957 | 5.89 | 5.8808 | 5.8794 | 5.8637 | 5.8765 | 5.8671 | 5.9033 | 5.89 | 5.8454 | 5.7997 | 5.7594 | 4.4325 | 4.4471 | 0.26472 | -2.7094 | -5.0062
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | Steady Progression | Headroom (MW) | N/A | 5.9241 | 5.9144 | 5.8827 | 5.8713 | 5.8533 | 5.8522 | 5.8372 | 5.8227 | 5.8127 | 5.8015 | 5.784 | 5.7877 | 5.7855 | 5.8016 | 5.8257 | 5.8482 | 5.8791 | 5.8601 | 5.6803
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | System Transformation | Headroom (MW) | N/A | 5.9237 | 5.9047 | 5.8673 | 5.8454 | 5.8068 | 5.7686 | 5.6997 | 5.6405 | 5.5639 | 5.5063 | 5.4524 | 5.4056 | 5.3839 | 5.3634 | 5.3624 | 5.3702 | 4.1928 | 3.9474 | 2.1281
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | 52.2627 | -0.7605 | WPD Best View | Headroom (MW) | N/A | 5.925 | 5.9072 | 5.8726 | 5.8546 | 5.8212 | 5.7894 | 5.7326 | 5.6853 | 5.6233 | 5.5825 | 5.5441 | 5.5174 | 5.5137 | 5.5038 | 5.5091 | 5.5035 | 4.1357 | 2.3716 | 0.38283
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Consumer Transformation | Headroom (MW) | N/A | 14.5043 | 14.4121 | 14.2667 | 14.163 | 14.0466 | 13.8974 | 13.6878 | 13.4876 | 13.3172 | 13.1414 | 12.9435 | 12.7856 | 12.6475 | 12.4931 | 12.3457 | 12.14 | 10.8297 | 9.1904 | 7.5308
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Leading the Way | Headroom (MW) | N/A | 14.5219 | 14.4756 | 14.3869 | 14.3393 | 14.3102 | 14.2869 | 14.2392 | 14.2377 | 14.2187 | 14.2508 | 14.1579 | 13.976 | 13.7864 | 13.5829 | 13.5853 | 13.5869 | 13.1395 | 12.6153 | 11.5868
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | Steady Progression | Headroom (MW) | N/A | 14.5188 | 14.4665 | 14.3707 | 14.3109 | 14.263 | 14.2108 | 14.1558 | 14.1162 | 14.0629 | 14.0075 | 13.9501 | 13.9048 | 13.8739 | 13.8531 | 13.8396 | 13.8225 | 13.8686 | 13.9125 | 13.4612
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | System Transformation | Headroom (MW) | N/A | 14.5158 | 14.4582 | 14.3424 | 14.2548 | 14.1719 | 14.0874 | 13.9619 | 13.8384 | 13.6917 | 13.5679 | 13.425 | 13.3305 | 13.2399 | 13.1754 | 13.1203 | 13.0568 | 12.8599 | 12.4031 | 11.6934
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | 52.243 | -0.8372 | WPD Best View | Headroom (MW) | N/A | 14.5205 | 14.4719 | 14.3788 | 14.3248 | 14.2881 | 14.2547 | 14.1932 | 14.1739 | 14.1285 | 14.1305 | 14.1118 | 14.0896 | 14.0641 | 14.0739 | 14.0427 | 14.0188 | 13.7366 | 12.9519 | 11.8899
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Consumer Transformation | Headroom (MW) | Thermal | 6.1135 | 6.0459 | 5.9354 | 5.8356 | 5.7266 | 5.582 | 5.3444 | 5.1263 | 4.909 | 3.794 | 3.5528 | 3.3427 | 2.2115 | 2.0172 | 0.19978 | -0.90615 | -8.7739 | -22.3212 | -38.1469
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Leading the Way | Headroom (MW) | Thermal | 6.1352 | 6.1163 | 6.0799 | 6.0644 | 6.0514 | 6.0517 | 6.0013 | 6.0308 | 6.0227 | 6.1075 | 6.1541 | 3.9925 | 4.0422 | 2.8543 | 0.40739 | -3.7977 | -19.8936 | -34.2091 | -47.5993
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | Steady Progression | Headroom (MW) | N/A | 6.1318 | 6.1045 | 6.0545 | 6.0338 | 6.0075 | 5.9874 | 5.9669 | 5.9447 | 5.9269 | 5.9031 | 5.8667 | 5.8562 | 5.8575 | 5.8818 | 5.9163 | 5.9573 | 5.0338 | 4.0511 | 2.4
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | System Transformation | Headroom (MW) | Thermal | 6.1228 | 6.0912 | 6.0305 | 5.9729 | 5.9025 | 5.8376 | 5.6944 | 5.585 | 5.4422 | 5.3274 | 5.2068 | 5.1271 | 5.0609 | 5.0116 | 2.3882 | 2.3796 | -0.045775 | -8.0528 | -18.6577
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | 52.154 | -0.7113 | WPD Best View | Headroom (MW) | Thermal | 6.1338 | 6.1119 | 6.0696 | 6.0452 | 6.0219 | 6.009 | 5.9412 | 5.9462 | 5.9064 | 5.9575 | 5.9714 | 3.7842 | 3.8069 | 2.6023 | 0.14064 | -2.3674 | -17.0115 | -30.1765 | -43.3809
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Consumer Transformation | Headroom (MW) | N/A | 16.3211 | 16.2687 | 16.0917 | 15.935 | 15.778 | 15.5466 | 15.2057 | 14.8726 | 14.5667 | 14.2411 | 13.8972 | 13.5544 | 13.2248 | 12.8995 | 12.5548 | 12.1575 | 9.9954 | 7.8454 | 5.8656
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Leading the Way | Headroom (MW) | N/A | 16.322 | 16.2775 | 16.2193 | 16.1585 | 16.1256 | 16.0935 | 15.8992 | 15.869 | 15.7917 | 15.7659 | 15.6879 | 15.5415 | 15.383 | 15.2089 | 15.1995 | 15.1893 | 14.634 | 13.7679 | 12.7746
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | Steady Progression | Headroom (MW) | N/A | 16.3206 | 16.294 | 16.2336 | 16.1947 | 16.1393 | 16.0926 | 16.03 | 15.9707 | 15.9022 | 15.8335 | 15.7499 | 15.6668 | 15.6063 | 15.5508 | 15.4942 | 15.4428 | 15.2446 | 15.1031 | 14.6705
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | System Transformation | Headroom (MW) | N/A | 16.3211 | 16.2965 | 16.208 | 16.1231 | 16.0159 | 15.9028 | 15.727 | 15.5501 | 15.3434 | 15.1443 | 14.9298 | 14.7402 | 14.5653 | 14.4028 | 14.2449 | 14.0687 | 13.3314 | 12.6836 | 12.0436
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | 52.2519 | -0.8514 | WPD Best View | Headroom (MW) | N/A | 16.322 | 16.3001 | 16.2419 | 16.2091 | 16.1609 | 16.1166 | 16.0213 | 15.9796 | 15.9026 | 15.8699 | 15.8158 | 15.7131 | 15.6084 | 15.5326 | 15.4088 | 15.2954 | 14.634 | 13.7679 | 12.7746
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Consumer Transformation | Headroom (MW) | N/A | 79.6978 | 79.6169 | 79.2705 | 79.2001 | 78.7725 | 77.7329 | 76.1687 | 74.7147 | 73.0734 | 71.1331 | 69.0145 | 66.8998 | 64.8629 | 62.8249 | 60.9088 | 58.8265 | 46.252 | 34.1554 | 18.6425
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Leading the Way | Headroom (MW) | N/A | 79.7766 | 79.8456 | 79.752 | 79.9213 | 79.8766 | 79.6635 | 78.954 | 78.8893 | 78.2345 | 77.6632 | 77.0151 | 76.2823 | 75.4401 | 74.2843 | 72.4472 | 72.1393 | 64.516 | 57.164 | 47.3967
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | Steady Progression | Headroom (MW) | N/A | 79.7158 | 79.6388 | 79.3269 | 79.3171 | 79.1841 | 78.9681 | 78.7361 | 78.5929 | 78.4075 | 78.2392 | 77.9994 | 77.8203 | 77.6591 | 77.5277 | 77.3591 | 77.1615 | 76.5802 | 75.9923 | 73.298
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | System Transformation | Headroom (MW) | N/A | 79.726 | 79.7204 | 79.4546 | 79.4853 | 79.2993 | 78.9938 | 78.5686 | 78.0467 | 77.242 | 76.4551 | 75.614 | 74.8261 | 73.927 | 73.0489 | 72.2821 | 71.4812 | 67.0329 | 63.0986 | 54.5957
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | 52.245 | -0.9134 | WPD Best View | Headroom (MW) | N/A | 79.7717 | 79.8865 | 79.7933 | 80.0307 | 79.9902 | 79.783 | 79.4474 | 78.9616 | 78.2195 | 77.5951 | 76.9123 | 76.1652 | 75.4653 | 74.8867 | 72.7074 | 72.2834 | 64.7266 | 57.7188 | 48.3504
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Consumer Transformation | Headroom (MW) | N/A | 17.8057 | 17.7405 | 17.6132 | 17.5431 | 17.4741 | 17.406 | 17.3054 | 17.2398 | 16.954 | 16.4719 | 15.9743 | 15.4752 | 15.0002 | 14.5162 | 14.0152 | 13.4928 | 10.6034 | 7.7209 | 5.0262
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Leading the Way | Headroom (MW) | N/A | 17.8059 | 17.7332 | 17.6061 | 17.527 | 17.4585 | 17.3912 | 17.2646 | 17.2006 | 17.1196 | 17.0617 | 16.9846 | 16.8747 | 16.7546 | 16.6224 | 16.5851 | 16.5473 | 16.0933 | 14.9809 | 13.5692
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | Steady Progression | Headroom (MW) | N/A | 17.8057 | 17.7406 | 17.6132 | 17.5417 | 17.4723 | 17.404 | 17.3281 | 17.2615 | 17.1928 | 17.1281 | 17.0611 | 16.9984 | 16.9352 | 16.875 | 16.8161 | 16.7588 | 16.4746 | 16.1731 | 15.7173
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | System Transformation | Headroom (MW) | N/A | 17.8057 | 17.7405 | 17.6131 | 17.5429 | 17.4736 | 17.4051 | 17.3336 | 17.2667 | 17.1986 | 17.1339 | 17.0706 | 17.0088 | 16.7781 | 16.517 | 16.2665 | 16.0125 | 14.9082 | 13.8508 | 12.8353
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | 52.2478 | -0.8765 | WPD Best View | Headroom (MW) | N/A | 17.8059 | 17.7409 | 17.6139 | 17.5443 | 17.4757 | 17.4084 | 17.3424 | 17.2783 | 17.2166 | 17.1588 | 17.1059 | 17.0582 | 17.0151 | 16.9759 | 16.9386 | 16.9007 | 16.3092 | 14.9809 | 13.5692
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Consumer Transformation | Headroom (MW) | N/A | 12.2184 | 12.22 | 12.0936 | 12.0473 | 12.0062 | 11.8904 | 11.7569 | 11.6019 | 11.4612 | 11.3095 | 11.1574 | 11.002 | 10.862 | 10.7165 | 10.5886 | 10.4423 | 9.5448 | 8.3956 | 5.9465
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Leading the Way | Headroom (MW) | N/A | 12.2331 | 12.2981 | 12.2134 | 12.2371 | 12.2756 | 12.2463 | 12.2446 | 12.2257 | 12.1817 | 12.1685 | 12.1462 | 12.0944 | 12.055 | 12.0336 | 12.0232 | 12.0042 | 10.3445 | 9.605 | 7.3926
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | Steady Progression | Headroom (MW) | N/A | 12.23 | 12.2363 | 12.1384 | 12.1244 | 12.1188 | 12.0701 | 12.0553 | 12.0204 | 11.9814 | 11.9423 | 11.8918 | 11.8594 | 11.8348 | 11.8175 | 11.8036 | 11.7956 | 11.8853 | 11.9313 | 11.5825
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | System Transformation | Headroom (MW) | N/A | 12.2284 | 12.2528 | 12.1448 | 12.121 | 12.1076 | 12.0409 | 11.9708 | 11.8745 | 11.7691 | 11.6694 | 11.579 | 11.4894 | 11.4208 | 11.3616 | 11.3223 | 11.2809 | 11.1882 | 10.8353 | 9.0026
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | 52.2152 | -0.9457 | WPD Best View | Headroom (MW) | N/A | 12.2331 | 12.2981 | 12.2134 | 12.2371 | 12.2756 | 12.2463 | 12.2446 | 12.2257 | 12.1817 | 12.1685 | 12.1462 | 12.0944 | 12.055 | 12.0336 | 12.0232 | 12.0042 | 10.3445 | 9.605 | 7.3926
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Consumer Transformation | Headroom (MW) | N/A | 5.9252 | 5.8982 | 5.8728 | 5.8689 | 5.8309 | 5.7755 | 5.7067 | 5.6426 | 5.6008 | 5.5544 | 5.5068 | 5.4768 | 5.4596 | 5.4481 | 5.4327 | 5.3969 | 3.6948 | 2.9307 | 0.81938
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Leading the Way | Headroom (MW) | Thermal | 5.9319 | 5.9161 | 5.9306 | 5.9673 | 5.9646 | 5.9622 | 5.9602 | 5.9875 | 6.0141 | 6.0545 | 6.1052 | 6.1507 | 6.1555 | 6.1022 | 4.6384 | 4.6697 | 3.2379 | 1.3853 | -0.63397
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | Steady Progression | Headroom (MW) | N/A | 5.93 | 5.9097 | 5.8924 | 5.9 | 5.8819 | 5.8681 | 5.849 | 5.8425 | 5.832 | 5.8175 | 5.8092 | 5.8002 | 5.8072 | 5.8207 | 5.8366 | 5.8596 | 6.0368 | 6.1036 | 5.8957
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | System Transformation | Headroom (MW) | N/A | 5.9283 | 5.9064 | 5.8931 | 5.8956 | 5.8675 | 5.8366 | 5.7889 | 5.7521 | 5.7106 | 5.6659 | 5.6296 | 5.6122 | 5.5974 | 5.6031 | 5.62 | 5.6391 | 4.4989 | 4.3426 | 2.6619
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | 52.2147 | -0.9988 | WPD Best View | Headroom (MW) | Thermal | 5.9312 | 5.9149 | 5.9278 | 5.9625 | 5.9572 | 5.9515 | 5.9452 | 5.9662 | 5.9851 | 6.0156 | 6.0545 | 6.0869 | 6.126 | 6.1872 | 4.5399 | 4.5729 | 3.2278 | 1.4881 | -0.45558
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Consumer Transformation | Headroom (MW) | N/A | 15.9178 | 16.062 | 16.1611 | 16.3037 | 16.2275 | 15.9007 | 15.4623 | 15.0825 | 14.7164 | 14.3472 | 13.8874 | 13.4424 | 13.0224 | 12.6195 | 12.2287 | 11.8136 | 9.5017 | 6.9574 | 3.2098
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Leading the Way | Headroom (MW) | N/A | 15.9491 | 16.138 | 16.3036 | 16.4802 | 16.574 | 16.5717 | 16.3383 | 16.4252 | 16.2606 | 16.1886 | 16.0847 | 15.9923 | 15.8371 | 15.5089 | 15.4955 | 15.4772 | 13.4853 | 12.105 | 10.5085
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | Steady Progression | Headroom (MW) | N/A | 15.8943 | 15.9875 | 16.0348 | 16.1281 | 16.1678 | 16.1648 | 16.1469 | 16.1831 | 16.2092 | 16.2474 | 16.244 | 16.2449 | 16.2391 | 16.2381 | 16.2331 | 16.2258 | 16.0487 | 15.9112 | 15.3225
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | System Transformation | Headroom (MW) | N/A | 15.9177 | 16.0617 | 16.1606 | 16.3029 | 16.3548 | 16.3513 | 16.311 | 16.1894 | 16.0222 | 15.8719 | 15.667 | 15.4738 | 15.3004 | 15.1382 | 15.0011 | 14.856 | 14.2769 | 13.4452 | 11.1616
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | 52.2418 | -0.9315 | WPD Best View | Headroom (MW) | N/A | 15.949 | 16.159 | 16.3245 | 16.5316 | 16.6253 | 16.6226 | 16.5172 | 16.4039 | 16.2316 | 16.1497 | 16.0339 | 15.9284 | 15.8514 | 15.8124 | 15.7167 | 15.6215 | 13.4752 | 12.2078 | 10.6869
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Consumer Transformation | Headroom (MW) | N/A | 10.167 | 10.084 | 9.9861 | 9.8556 | 9.711 | 9.4911 | 9.1915 | 8.9121 | 8.643 | 8.3557 | 8.0366 | 7.7117 | 7.3915 | 7.0696 | 6.7403 | 6.38 | 4.5674 | 2.9276 | 1.4468
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Leading the Way | Headroom (MW) | N/A | 10.1146 | 10.0705 | 10.0274 | 9.9637 | 9.8946 | 9.8034 | 9.6712 | 9.5697 | 9.4625 | 9.382 | 9.287 | 9.1586 | 9.0121 | 8.8894 | 8.7269 | 8.576 | 7.8673 | 7.1771 | 6.4813
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | Steady Progression | Headroom (MW) | N/A | 8.4333 | 8.4089 | 8.3933 | 8.3711 | 8.3546 | 8.3319 | 8.3063 | 8.2842 | 8.2533 | 8.218 | 8.1666 | 8.1272 | 8.0888 | 8.045 | 8.0012 | 7.9565 | 7.7233 | 7.4909 | 7.2
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | System Transformation | Headroom (MW) | N/A | 9.8304 | 9.7966 | 9.7522 | 9.6912 | 9.6276 | 9.5484 | 9.4191 | 9.28 | 9.1311 | 8.9826 | 8.8236 | 8.6744 | 8.5203 | 8.3735 | 8.2247 | 8.0582 | 7.2994 | 6.7235 | 6.2715
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | 52.2645 | -0.9006 | WPD Best View | Headroom (MW) | N/A | 9.6792 | 9.6411 | 9.6072 | 9.5573 | 9.5055 | 9.4366 | 9.3155 | 9.2225 | 9.1248 | 9.052 | 8.9655 | 8.8461 | 8.7099 | 8.5959 | 8.4455 | 8.3093 | 7.6904 | 7.0869 | 6.4753
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Consumer Transformation | Headroom (MW) | N/A | 59.3072 | 59.2338 | 59.1001 | 58.9432 | 58.7519 | 58.4596 | 58.039 | 57.6026 | 57.1261 | 56.576 | 55.9745 | 55.3274 | 54.6569 | 53.962 | 53.3908 | 52.7833 | 50.1406 | 47.9103 | 45.9181
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Leading the Way | Headroom (MW) | N/A | 58.9467 | 58.9103 | 58.8412 | 58.7537 | 58.6428 | 58.4964 | 58.2548 | 57.9847 | 57.6136 | 57.1969 | 56.7421 | 56.257 | 55.7646 | 55.2691 | 54.9675 | 54.7161 | 53.487 | 52.6531 | 51.8719
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | Steady Progression | Headroom (MW) | N/A | 49.0745 | 49.0599 | 49.0334 | 49.0077 | 48.9858 | 48.9557 | 48.9218 | 48.8826 | 48.8244 | 48.7655 | 48.6809 | 48.6018 | 48.515 | 48.4202 | 48.3296 | 48.231 | 47.8598 | 47.583 | 47.2628
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | System Transformation | Headroom (MW) | N/A | 57.2832 | 57.2461 | 57.1916 | 57.1182 | 57.0345 | 56.9331 | 56.7683 | 56.5935 | 56.3875 | 56.1679 | 55.9253 | 55.6771 | 55.4197 | 55.1426 | 54.9009 | 54.6444 | 53.5681 | 52.8379 | 52.2716
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | 52.245 | -0.9134 | WPD Best View | Headroom (MW) | N/A | 56.403 | 56.3682 | 56.302 | 56.2183 | 56.1122 | 55.9721 | 55.741 | 55.4825 | 55.1274 | 54.7287 | 54.2936 | 53.8294 | 53.3582 | 52.8841 | 52.5955 | 52.3598 | 51.2074 | 50.4475 | 49.7329
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Consumer Transformation | Headroom (MW) | Thermal | 42.1956 | 42.0226 | 41.6805 | 41.2956 | 41.0235 | 40.595 | 39.8889 | 39.2457 | 38.5401 | 37.9456 | 34.3166 | 30.7089 | 28.3942 | 25.8256 | 24.439 | -1.624 | -22.9909 | -55.1462 | -84.198
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Leading the Way | Headroom (MW) | Thermal | 42.2568 | 42.2064 | 42.0556 | 41.9129 | 41.8557 | 41.8315 | 41.6791 | 41.6053 | 41.3758 | 41.3625 | 15.6557 | 15.3241 | 12.593 | 9.8473 | 0.80869 | -7.0211 | -29.6172 | -59.1431 | -85.5626
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | Steady Progression | Headroom (MW) | N/A | 42.2575 | 42.1502 | 41.9097 | 41.7629 | 41.6683 | 41.5877 | 41.5074 | 41.426 | 41.2971 | 41.1993 | 41.0226 | 40.964 | 41.0448 | 41.0355 | 41.0947 | 41.1642 | 41.5515 | 39.2856 | 35.9642
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | System Transformation | Headroom (MW) | Thermal | 42.2391 | 42.1242 | 41.8675 | 41.6296 | 41.4192 | 41.2442 | 40.9139 | 40.5841 | 40.1511 | 39.8013 | 39.4036 | 39.1397 | 39.1902 | 39.0479 | 39.0123 | 13.4647 | 5.5499 | -11.3192 | -25.8691
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | 52.6682 | -0.7096 | WPD Best View | Headroom (MW) | Thermal | 42.2382 | 42.1135 | 41.8641 | 41.6155 | 41.4074 | 41.2492 | 40.9007 | 40.571 | 40.1394 | 39.7812 | 39.3494 | 39.0676 | 38.1577 | 37.9708 | 37.8963 | 37.7808 | 28.531 | 12.7819 | -0.62038
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Consumer Transformation | Headroom (MW) | N/A | 12.2526 | 12.268 | 12.2595 | 12.1932 | 12.1902 | 12.1578 | 12.0448 | 11.9367 | 11.8181 | 11.7023 | 11.5425 | 10.4516 | 10.2726 | 10.0958 | 9.9707 | 9.7886 | 7.9719 | 6.2614 | 2.3337
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Leading the Way | Headroom (MW) | N/A | 12.257 | 12.3125 | 12.3422 | 12.3024 | 12.3369 | 12.3609 | 12.2966 | 12.2334 | 12.1317 | 12.0366 | 11.9005 | 11.7628 | 11.619 | 11.4758 | 10.4675 | 10.3062 | 8.496 | 6.9787 | 5.4146
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | Steady Progression | Headroom (MW) | N/A | 12.2566 | 12.2661 | 12.244 | 12.2049 | 12.212 | 12.2184 | 12.197 | 12.1724 | 12.1442 | 12.1246 | 12.0944 | 12.074 | 12.0414 | 12.0214 | 12.0209 | 11.9995 | 11.9209 | 11.9179 | 11.6883
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | System Transformation | Headroom (MW) | N/A | 12.2554 | 12.2815 | 12.2749 | 12.2217 | 12.224 | 12.2457 | 12.189 | 12.1379 | 12.0685 | 12.022 | 11.9646 | 11.9146 | 11.8671 | 11.8199 | 11.812 | 11.7543 | 11.556 | 10.3706 | 8.7238
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | 52.6622 | -0.5957 | WPD Best View | Headroom (MW) | N/A | 12.2554 | 12.2815 | 12.2749 | 12.2217 | 12.224 | 12.2457 | 12.189 | 12.1379 | 12.0685 | 12.022 | 11.9646 | 11.9146 | 11.8671 | 11.8199 | 11.812 | 11.7543 | 11.556 | 10.3706 | 8.7238
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Consumer Transformation | Headroom (MW) | Thermal | 3.8229 | 3.8091 | 3.7767 | 3.7428 | 3.7205 | 3.6746 | 3.6114 | 3.5534 | 3.5028 | 3.4564 | 2.4559 | 2.3808 | 2.3212 | 2.2523 | 1.2937 | 1.2493 | -1.1122 | -2.6865 | -5.2324
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Leading the Way | Headroom (MW) | Thermal | 3.8344 | 3.8172 | 3.8019 | 3.7898 | 3.784 | 3.7861 | 3.762 | 3.7593 | 3.7553 | 3.7738 | 3.7635 | 3.7536 | 2.8096 | 2.8086 | 2.8196 | 2.8169 | 1.6564 | -0.96306 | -3.3239
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | Steady Progression | Headroom (MW) | N/A | 3.8344 | 3.823 | 3.7937 | 3.783 | 3.7737 | 3.7657 | 3.7489 | 3.7451 | 3.7321 | 3.7282 | 3.7163 | 3.7072 | 3.6998 | 3.6956 | 3.7064 | 3.713 | 3.761 | 3.7949 | 3.6826
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | System Transformation | Headroom (MW) | N/A | 3.8332 | 3.8122 | 3.789 | 3.7657 | 3.7427 | 3.7327 | 3.6952 | 3.6595 | 3.6334 | 3.5992 | 3.5673 | 3.533 | 3.5158 | 3.5045 | 3.4999 | 3.4953 | 2.5719 | 2.4435 | 2.2155
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | 52.686 | -0.6525 | WPD Best View | Headroom (MW) | N/A | 3.8332 | 3.8122 | 3.789 | 3.7657 | 3.7427 | 3.7327 | 3.6952 | 3.6595 | 3.6334 | 3.5992 | 3.5673 | 3.533 | 3.5158 | 3.5045 | 3.4999 | 3.4953 | 2.5719 | 2.4435 | 2.2155
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Consumer Transformation | Headroom (MW) | Thermal | 4.7135 | 4.6911 | 4.6524 | 4.6208 | 4.6149 | 4.5938 | 4.538 | 4.5048 | 4.4567 | 4.4606 | 4.4208 | 3.4749 | 2.548 | 2.5499 | 2.6068 | 2.6428 | -3.1472 | -9.4458 | -15.9034
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Leading the Way | Headroom (MW) | Thermal | 4.7177 | 4.71 | 4.6812 | 4.684 | 4.6856 | 4.6932 | 4.7199 | 4.7389 | 4.7664 | 4.8399 | 4.8746 | 4.7957 | 4.7168 | 4.6435 | 0.8837 | 0.93932 | -4.7785 | -12.563 | -18.0492
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | Steady Progression | Headroom (MW) | N/A | 4.7142 | 4.6998 | 4.6689 | 4.6561 | 4.6365 | 4.6288 | 4.6233 | 4.6242 | 4.6198 | 4.6235 | 4.6159 | 4.6353 | 4.6511 | 4.6697 | 4.7095 | 4.7632 | 4.8337 | 4.7934 | 2.5118
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | System Transformation | Headroom (MW) | Thermal | 4.7141 | 4.6981 | 4.6567 | 4.6405 | 4.6167 | 4.591 | 4.5744 | 4.5427 | 4.5103 | 4.5041 | 4.4932 | 4.5065 | 4.5332 | 4.5766 | 4.6371 | 4.7029 | 2.5198 | -1.0598 | -4.9916
Grendon 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | 52.7588 | -0.6665 | WPD Best View | Headroom (MW) | Thermal | 4.7128 | 4.6871 | 4.6526 | 4.6253 | 4.6024 | 4.5837 | 4.5464 | 4.5129 | 4.4739 | 4.4586 | 4.4162 | 4.4149 | 3.4913 | 3.4977 | 3.5325 | 3.5723 | 0.096057 | -4.6547 | -8.8019
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Consumer Transformation | Headroom (MW) | Thermal | 14.5134 | 14.4006 | 14.2058 | 14.0174 | 13.833 | 13.5957 | 13.2315 | 12.8839 | 12.517 | 12.1701 | 10.8015 | 9.4412 | 9.3261 | 8.0139 | 7.7004 | 7.35 | 0.99813 | -11.2995 | -20.5075
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Leading the Way | Headroom (MW) | Thermal | 14.5379 | 14.4712 | 14.3618 | 14.281 | 14.2108 | 14.1458 | 14.0354 | 13.9407 | 13.7943 | 13.7166 | 13.5525 | 13.3873 | 12.7054 | 11.3891 | 8.7245 | 5.271 | -2.5714 | -12.245 | -20.1564
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | Steady Progression | Headroom (MW) | N/A | 14.5429 | 14.4779 | 14.3534 | 14.2875 | 14.2247 | 14.1681 | 14.1188 | 14.047 | 13.9784 | 13.9 | 13.7941 | 13.7341 | 13.8265 | 13.8011 | 13.7729 | 13.7526 | 13.7764 | 12.5477 | 12.1013
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | System Transformation | Headroom (MW) | Thermal | 14.5309 | 14.4519 | 14.3144 | 14.2094 | 14.0928 | 13.9685 | 13.7849 | 13.6002 | 13.3724 | 13.1637 | 12.9377 | 12.7621 | 12.8651 | 12.7382 | 12.6255 | 12.498 | 9.8866 | 3.2302 | -1.4971
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | 52.6682 | -0.7096 | WPD Best View | Headroom (MW) | N/A | 14.5313 | 14.4522 | 14.3152 | 14.2106 | 14.0952 | 13.9809 | 13.7998 | 13.6168 | 13.3971 | 13.189 | 12.9605 | 12.7816 | 12.8746 | 12.74 | 12.6141 | 12.4841 | 9.8308 | 5.4656 | 2.1011
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Consumer Transformation | Headroom (MW) | Thermal | 3.8933 | 3.8538 | 3.786 | 3.7215 | 3.6649 | 3.573 | 3.4632 | 3.367 | 3.2455 | 3.1563 | 2.096 | 1.9603 | 0.92633 | -0.086299 | -0.13259 | -0.1939 | -5.2408 | -15.5151 | -22.4277
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Leading the Way | Headroom (MW) | Thermal | 3.9098 | 3.8954 | 3.8685 | 3.8556 | 3.8385 | 3.8455 | 3.8652 | 3.933 | 3.9282 | 3.9956 | 4.0253 | 4.0854 | 3.203 | 1.9911 | 0.37404 | -3.8937 | -9.9589 | -17.89 | -26.9869
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | Steady Progression | Headroom (MW) | N/A | 3.9094 | 3.8834 | 3.8498 | 3.8314 | 3.8214 | 3.8068 | 3.8194 | 3.8373 | 3.8226 | 3.823 | 3.8019 | 3.8134 | 3.8259 | 3.8477 | 3.885 | 3.9358 | 4.2596 | 3.2317 | 2.9802
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | System Transformation | Headroom (MW) | Thermal | 3.9054 | 3.8806 | 3.8325 | 3.7922 | 3.7431 | 3.7062 | 3.6704 | 3.6438 | 3.5665 | 3.5123 | 3.4409 | 3.4235 | 3.4088 | 3.4086 | 3.4378 | 3.4748 | 1.4763 | -3.8431 | -7.8589
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | 52.5955 | -0.719 | WPD Best View | Headroom (MW) | Thermal | 3.9054 | 3.8806 | 3.8325 | 3.7922 | 3.7431 | 3.7062 | 3.6704 | 3.6438 | 3.5665 | 3.5123 | 3.4409 | 3.4235 | 3.4088 | 3.4086 | 3.4378 | 3.4748 | 1.4763 | -3.8431 | -7.8589
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Consumer Transformation | Headroom (MW) | Thermal | -11.488 | -11.7711 | -17.432 | -17.841 | -18.4812 | -19.4683 | -20.8701 | -22.2768 | -23.6868 | -25.16 | -44.0492 | -45.5652 | -62.234 | -65.56 | -66.9165 | -68.38 | -82.5347 | -99.8981 | -114.1327
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Leading the Way | Headroom (MW) | Thermal | -11.4151 | -11.5518 | -11.8751 | -12.0807 | -12.3376 | -12.6839 | -13.6503 | -14.1895 | -29.3964 | -30.191 | -42.9331 | -43.6613 | -44.4153 | -45.0063 | -46.6981 | -48.6912 | -64.8917 | -75.5122 | -88.2316
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | Steady Progression | Headroom (MW) | Thermal | -11.4263 | -11.5763 | -11.8987 | -12.0117 | -12.1274 | -12.2768 | -12.4429 | -12.5945 | -12.7814 | -12.9577 | -13.1874 | -13.4433 | -13.6694 | -13.8658 | -14.0716 | -14.3141 | -14.1627 | -14.5927 | -19.085
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | System Transformation | Headroom (MW) | Thermal | -11.4428 | -11.6091 | -11.9933 | -12.1735 | -12.422 | -12.7278 | -13.3824 | -14.0109 | -14.7802 | -15.499 | -16.2612 | -16.9505 | -17.5466 | -25.231 | -25.6659 | -32.3117 | -34.8297 | -43.6983 | -50.1504
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | 52.2921 | -0.6847 | WPD Best View | Headroom (MW) | Thermal | -11.436 | -11.5904 | -11.9498 | -12.1964 | -12.5112 | -12.8852 | -13.5146 | -14.111 | -29.2115 | -29.8902 | -42.4714 | -43.191 | -43.8276 | -44.3602 | -46.2836 | -46.7343 | -57.6208 | -66.6588 | -75.4742
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Consumer Transformation | Headroom (MW) | Thermal | 16.5572 | 16.4249 | 16.1744 | 15.9217 | 15.6544 | 15.2697 | 14.676 | 14.1324 | 13.5982 | 13.0203 | 12.4065 | 11.82 | 11.2575 | 10.663 | 10.0766 | 9.3721 | 6.0563 | 2.826 | -0.44478
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Leading the Way | Headroom (MW) | N/A | 16.6012 | 16.5611 | 16.4382 | 16.3532 | 16.2676 | 16.1771 | 15.9508 | 15.8403 | 15.6523 | 15.514 | 15.3731 | 15.1174 | 14.7793 | 14.4814 | 14.1269 | 13.8847 | 13.8004 | 12.3604 | 9.5081
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | Steady Progression | Headroom (MW) | N/A | 13.8983 | 13.8749 | 13.8471 | 13.82 | 13.7948 | 13.7711 | 13.7382 | 13.695 | 13.6403 | 13.5736 | 13.4887 | 13.4155 | 13.3504 | 13.2812 | 13.2134 | 13.1331 | 12.7537 | 12.397 | 11.9846
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | System Transformation | Headroom (MW) | N/A | 16.2155 | 16.1618 | 16.0926 | 16.0061 | 15.9046 | 15.7875 | 15.5567 | 15.3374 | 15.0406 | 14.718 | 14.3834 | 14.0843 | 13.8191 | 13.6149 | 13.4234 | 13.1541 | 11.823 | 11.4909 | 10.4435
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | 52.3051 | -0.6892 | WPD Best View | Headroom (MW) | N/A | 15.9661 | 15.9133 | 15.8451 | 15.7599 | 15.66 | 15.5447 | 15.3175 | 15.1015 | 14.837 | 14.5724 | 14.2864 | 13.9245 | 13.5661 | 13.2168 | 12.8594 | 12.5618 | 11.2274 | 11.101 | 9.978
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Consumer Transformation | Headroom (MW) | Thermal | 4.4846 | 4.4732 | 4.4559 | 4.4446 | 4.4362 | 4.4203 | 4.3945 | 4.3781 | 4.3718 | 4.3753 | 4.3677 | 4.367 | 4.3889 | 3.4794 | 3.5188 | 3.5487 | 2.0844 | -1.6576 | -5.8506
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Leading the Way | Headroom (MW) | Thermal | 4.4877 | 4.4886 | 4.4796 | 4.4883 | 4.4913 | 4.5022 | 4.5205 | 4.5511 | 4.5748 | 4.5787 | 4.5693 | 4.5523 | 4.5361 | 4.5102 | 3.2973 | 3.3666 | -1.4752 | -4.5664 | -8.4217
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | Steady Progression | Headroom (MW) | N/A | 4.4848 | 4.4809 | 4.4712 | 4.461 | 4.4614 | 4.4633 | 4.4677 | 4.465 | 4.473 | 4.4844 | 4.4921 | 4.5115 | 4.5311 | 4.5569 | 4.569 | 4.5685 | 4.5861 | 4.5892 | 3.7405
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | System Transformation | Headroom (MW) | Thermal | 4.4843 | 4.4799 | 4.4601 | 4.4565 | 4.4448 | 4.4354 | 4.4218 | 4.4147 | 4.3991 | 4.3927 | 4.3888 | 4.4001 | 4.4317 | 4.4695 | 4.5194 | 4.5825 | 3.6216 | 2.3205 | -0.53987
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | 52.2063 | -0.6048 | WPD Best View | Headroom (MW) | Thermal | 4.487 | 4.4874 | 4.4768 | 4.4835 | 4.4839 | 4.4915 | 4.5055 | 4.5298 | 4.5458 | 4.5841 | 4.6017 | 4.6026 | 4.6074 | 4.6147 | 3.2082 | 3.2791 | -0.20125 | -3.1608 | -7.2673
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Consumer Transformation | Headroom (MW) | N/A | 13.3177 | 13.2506 | 13.1336 | 13.0985 | 12.8992 | 12.645 | 12.3276 | 12.0135 | 11.6741 | 11.3085 | 10.8947 | 10.5675 | 10.2304 | 9.918 | 9.6302 | 9.3261 | 7.8895 | 4.3739 | 2.893
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Leading the Way | Headroom (MW) | N/A | 13.3322 | 13.2938 | 13.2139 | 13.1699 | 13.0065 | 12.8314 | 12.599 | 12.3658 | 12.0809 | 11.7764 | 11.4332 | 11.2584 | 11.1202 | 11.0339 | 10.9279 | 9.1258 | 8.2333 | 5.8248 | 3.8408
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | Steady Progression | Headroom (MW) | N/A | 13.3236 | 13.2918 | 13.2109 | 13.236 | 13.2112 | 13.1692 | 13.1381 | 13.1008 | 13.058 | 13.016 | 12.9675 | 12.843 | 12.7207 | 12.6019 | 12.4833 | 12.3747 | 12.2738 | 12.222 | 11.8502
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | System Transformation | Headroom (MW) | N/A | 13.3236 | 13.283 | 13.2034 | 13.2294 | 13.17 | 13.1068 | 12.9106 | 12.7359 | 12.5406 | 12.3483 | 12.1423 | 11.9429 | 11.758 | 11.5802 | 11.4213 | 11.261 | 10.7596 | 9.1023 | 8.5166
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | 52.2875 | -0.6796 | WPD Best View | Headroom (MW) | N/A | 13.3244 | 13.2842 | 13.2062 | 13.1419 | 12.9929 | 12.8407 | 12.6388 | 12.4612 | 12.2658 | 12.0754 | 11.8802 | 11.6957 | 11.5238 | 11.3625 | 11.2042 | 11.0516 | 10.3777 | 8.2691 | 7.2489
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Consumer Transformation | Headroom (MW) | N/A | 14.3632 | 14.3462 | 14.3019 | 14.2828 | 14.169 | 13.9851 | 13.7223 | 13.4682 | 13.2412 | 13.0123 | 12.7255 | 12.4601 | 12.1993 | 11.028 | 10.8088 | 10.5751 | 9.3361 | 5.9307 | 3.8476
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Leading the Way | Headroom (MW) | N/A | 14.3648 | 14.3369 | 14.297 | 14.26 | 14.2455 | 14.2319 | 13.9151 | 13.9007 | 13.7738 | 13.6779 | 13.5668 | 13.488 | 13.2965 | 13.0738 | 13.0581 | 13.0419 | 10.5679 | 8.7049 | 7.092
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | Steady Progression | Headroom (MW) | N/A | 14.362 | 14.3415 | 14.2935 | 14.2684 | 14.2463 | 14.2252 | 14.1878 | 14.1657 | 14.1361 | 14.1215 | 14.0934 | 14.0702 | 14.0447 | 14.003 | 13.9543 | 13.8971 | 13.8049 | 13.648 | 13.3064
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | System Transformation | Headroom (MW) | N/A | 14.3632 | 14.3461 | 14.3019 | 14.2827 | 14.264 | 14.2457 | 14.1854 | 14.0778 | 13.9438 | 13.8323 | 13.7091 | 13.5783 | 13.4637 | 13.3579 | 13.2659 | 13.1581 | 12.7716 | 11.1351 | 10.7161
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | 52.2994 | -0.7389 | WPD Best View | Headroom (MW) | N/A | 14.3632 | 14.3461 | 14.3019 | 14.2827 | 14.264 | 14.2457 | 14.1854 | 14.0778 | 13.9438 | 13.8323 | 13.7091 | 13.5783 | 13.4637 | 13.3579 | 13.2659 | 13.1581 | 12.7716 | 11.1351 | 10.7161
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Consumer Transformation | Headroom (MW) | Thermal | 3.1096 | 3.0542 | 2.9488 | 2.8581 | 2.8068 | 2.6582 | 2.4562 | 2.1778 | 1.8746 | 1.5703 | 1.2283 | 0.89203 | -0.36621 | -0.70443 | -1.0069 | -1.258 | -3.9907 | -7.4608 | -10.6676
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Leading the Way | Headroom (MW) | Thermal | 3.1192 | 3.0881 | 3.0165 | 2.9681 | 2.9717 | 2.8937 | 2.6846 | 2.4729 | 2.1962 | 1.9364 | 1.6924 | 1.4673 | 1.2652 | 1.105 | 0.91525 | 0.8267 | -3.277 | -5.095 | -7.5098
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | Steady Progression | Headroom (MW) | N/A | 3.1255 | 3.0783 | 3.0097 | 2.9796 | 2.9796 | 2.9558 | 2.9211 | 2.9013 | 2.8729 | 2.8451 | 2.8098 | 2.7862 | 2.7631 | 2.7524 | 2.7425 | 2.7362 | 3.1581 | 2.9944 | 2.6198
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | System Transformation | Headroom (MW) | Thermal | 3.1141 | 3.0726 | 2.9892 | 2.9401 | 2.936 | 2.8847 | 2.7904 | 2.7079 | 2.6159 | 2.5299 | 2.4355 | 2.3641 | 2.3012 | 2.2439 | 2.2014 | 2.1778 | 2.4458 | 0.88515 | -0.65427
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | 52.2283 | -0.5653 | WPD Best View | Headroom (MW) | Thermal | 3.1167 | 3.0814 | 3.0105 | 2.973 | 2.9775 | 2.9266 | 2.8312 | 2.7462 | 2.6379 | 2.5355 | 2.4713 | 2.4238 | 2.3931 | 2.3839 | 2.3713 | 2.3772 | 0.22832 | -1.2622 | -3.4088
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Consumer Transformation | Headroom (MW) | N/A | 21.0134 | 20.9071 | 20.7227 | 20.5712 | 20.4204 | 20.2126 | 19.9307 | 19.6652 | 19.4015 | 19.1298 | 18.8415 | 18.5606 | 18.2875 | 18.0107 | 17.7319 | 17.4275 | 15.7789 | 14.057 | 12.4075
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Leading the Way | Headroom (MW) | N/A | 21.0295 | 20.9508 | 20.8122 | 20.7258 | 20.6377 | 20.549 | 20.4232 | 20.3091 | 20.1814 | 20.0692 | 19.9537 | 19.8174 | 19.6849 | 19.5634 | 19.4219 | 19.278 | 18.499 | 17.5958 | 16.6798
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | Steady Progression | Headroom (MW) | N/A | 21.036 | 20.9552 | 20.8243 | 20.7486 | 20.679 | 20.5991 | 20.5306 | 20.447 | 20.3676 | 20.2862 | 20.1954 | 20.1076 | 20.027 | 19.9485 | 19.8826 | 19.817 | 19.5061 | 19.2231 | 18.755
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | System Transformation | Headroom (MW) | N/A | 21.0265 | 20.9434 | 20.7907 | 20.6966 | 20.5868 | 20.4715 | 20.3176 | 20.1533 | 19.9815 | 19.8131 | 19.6411 | 19.4743 | 19.3215 | 19.1781 | 19.0363 | 18.8943 | 18.2367 | 17.5592 | 16.8648
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | 52.2923 | -0.6846 | WPD Best View | Headroom (MW) | N/A | 21.0265 | 20.9434 | 20.7907 | 20.6966 | 20.5868 | 20.4715 | 20.3176 | 20.1533 | 19.9815 | 19.8131 | 19.6411 | 19.4743 | 19.3215 | 19.1781 | 19.0363 | 18.8943 | 18.2367 | 17.5592 | 16.8648
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Consumer Transformation | Headroom (MW) | Thermal | 53.7242 | 42.0383 | 41.7393 | 41.3548 | 41.0971 | 40.361 | 39.5231 | 38.6728 | 37.7913 | 36.9621 | 36.0287 | 34.2698 | 33.5431 | 32.852 | 32.2758 | 31.1598 | 19.4848 | 7.6039 | -7.9488
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Leading the Way | Headroom (MW) | Thermal | 53.8037 | 42.2954 | 42.2593 | 42.141 | 42.168 | 41.6976 | 36.7349 | 36.2745 | 35.4043 | 34.8832 | 34.0047 | 33.4704 | 32.9259 | 31.635 | 28.3741 | 26.3022 | 17.0598 | -1.9342 | -15.8303
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | Steady Progression | Headroom (MW) | N/A | 53.7027 | 42.0484 | 41.8515 | 41.818 | 41.8832 | 41.7498 | 41.608 | 41.5273 | 41.3079 | 41.1245 | 40.9106 | 40.5849 | 40.3098 | 40.0214 | 39.9185 | 39.8524 | 40.2252 | 40.1428 | 37.0009
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | System Transformation | Headroom (MW) | N/A | 53.7383 | 42.1466 | 41.9762 | 41.834 | 41.7679 | 41.4065 | 40.9993 | 40.6052 | 40.1365 | 39.69 | 39.255 | 38.9198 | 38.6149 | 38.3846 | 38.2303 | 39.5277 | 36.0525 | 31.459 | 22.7411
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | 52.608 | -1.6558 | WPD Best View | Headroom (MW) | N/A | 53.7034 | 42.0514 | 41.7936 | 41.5181 | 41.3566 | 40.7614 | 40.1367 | 39.4749 | 38.7501 | 38.0539 | 37.2369 | 35.5982 | 34.9646 | 34.4089 | 33.9658 | 31.7116 | 25.1429 | 16.422 | 5.8262
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Consumer Transformation | Headroom (MW) | N/A | 11.2078 | 11.2024 | 11.1764 | 11.1033 | 10.9385 | 10.7333 | 10.4849 | 10.2262 | 9.9558 | 9.6662 | 9.3474 | 9.0571 | 8.7763 | 8.5516 | 8.3409 | 8.1197 | 6.0665 | 3.7163 | 0.92564
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Leading the Way | Headroom (MW) | N/A | 11.2321 | 11.2728 | 11.314 | 11.3042 | 11.1689 | 11.0256 | 10.8521 | 10.6474 | 10.3867 | 10.126 | 9.8571 | 9.7225 | 9.6187 | 9.5987 | 9.5712 | 9.5249 | 7.5408 | 4.2633 | 1.7067
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | Steady Progression | Headroom (MW) | N/A | 11.2151 | 11.2175 | 11.2275 | 11.2298 | 11.1943 | 11.172 | 11.1403 | 11.1104 | 11.0761 | 11.0427 | 10.9946 | 10.9583 | 10.9245 | 10.8933 | 10.875 | 10.8479 | 10.9587 | 11.014 | 10.5405
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | System Transformation | Headroom (MW) | N/A | 11.2206 | 11.2426 | 11.2609 | 11.2685 | 11.1932 | 11.1251 | 11.0266 | 10.9477 | 10.8366 | 10.7357 | 10.6191 | 10.5335 | 10.4442 | 10.3833 | 10.3234 | 10.2707 | 10.1749 | 9.7422 | 7.6778
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | 52.585 | -1.5492 | WPD Best View | Headroom (MW) | N/A | 11.2077 | 11.2018 | 11.1729 | 11.0986 | 10.9384 | 10.7291 | 10.4762 | 10.2192 | 9.943 | 9.6495 | 9.3147 | 9.0251 | 8.7343 | 8.5089 | 8.2933 | 8.0813 | 7.1459 | 4.9795 | 2.2947
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Consumer Transformation | Headroom (MW) | N/A | 20.9483 | 20.9433 | 20.9499 | 20.9781 | 21.0161 | 20.9813 | 21.012 | 21.0102 | 21.002 | 20.9905 | 20.9796 | 20.9672 | 20.9649 | 20.948 | 20.9318 | 20.9677 | 20.7662 | 20.503 | 20.1568
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Leading the Way | Headroom (MW) | N/A | 20.9487 | 20.954 | 20.9868 | 21.0503 | 21.1067 | 21.0832 | 17.0108 | 17.0414 | 17.0476 | 17.0408 | 17.0247 | 17.0139 | 16.996 | 16.9715 | 16.9521 | 16.9827 | 16.7858 | 16.4652 | 16.0535
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | Steady Progression | Headroom (MW) | N/A | 20.9482 | 20.9347 | 20.9208 | 20.9374 | 20.9564 | 20.9302 | 20.9422 | 20.9404 | 20.9179 | 20.9036 | 20.8889 | 20.8765 | 20.8672 | 20.8484 | 20.8395 | 20.8609 | 20.7806 | 20.794 | 20.641
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | System Transformation | Headroom (MW) | N/A | 20.9481 | 20.9422 | 20.9475 | 20.9827 | 21.0099 | 20.9808 | 21.0152 | 21.0173 | 21.0107 | 20.9912 | 20.9734 | 20.9673 | 20.953 | 20.9382 | 20.9358 | 20.9766 | 20.901 | 20.7963 | 20.5497
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | 52.5925 | -1.6266 | WPD Best View | Headroom (MW) | N/A | 20.9483 | 20.9433 | 20.9499 | 20.9781 | 21.0161 | 20.9813 | 21.012 | 21.0102 | 21.002 | 20.9905 | 20.9796 | 20.9672 | 20.9649 | 20.948 | 20.9318 | 20.9677 | 20.7662 | 20.503 | 20.1568
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Consumer Transformation | Headroom (MW) | Thermal | 4.9533 | 4.9373 | 4.8685 | 4.6951 | 4.7306 | 4.5076 | 4.2596 | 4.001 | 3.7204 | 3.4612 | 3.1803 | 2.9133 | 2.6804 | 2.4839 | 2.3407 | 1.2599 | -1.8778 | -5.2941 | -8.9521
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Leading the Way | Headroom (MW) | Thermal | 4.9698 | 4.9775 | 4.9226 | 4.7669 | 4.886 | 4.686 | 4.4913 | 4.241 | 3.9203 | 3.6943 | 3.4304 | 3.2822 | 3.1761 | 3.193 | 1.4998 | -0.20999 | -3.3085 | -8.3394 | -12.8303
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | Steady Progression | Headroom (MW) | N/A | 4.9473 | 4.9522 | 4.9299 | 4.9323 | 5.0858 | 5.0869 | 5.095 | 5.1132 | 5.1243 | 5.0597 | 4.9837 | 4.9227 | 4.8613 | 4.8055 | 4.7638 | 4.7355 | 5.1934 | 5.4747 | 5.0676
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | System Transformation | Headroom (MW) | Thermal | 4.9533 | 4.9629 | 4.9296 | 4.8268 | 4.9266 | 4.8027 | 4.6806 | 4.5572 | 4.4449 | 4.3314 | 4.2356 | 4.147 | 4.0511 | 3.9992 | 3.9576 | 3.9494 | 2.8697 | 1.443 | -0.65415
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | 52.6164 | -1.6131 | WPD Best View | Headroom (MW) | Thermal | 4.9461 | 4.9304 | 4.8668 | 4.7083 | 4.7608 | 4.5451 | 4.3115 | 4.0534 | 3.783 | 3.516 | 3.2312 | 2.9551 | 2.7051 | 2.4887 | 2.323 | 1.2485 | -0.47306 | -2.0096 | -4.4068
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Consumer Transformation | Headroom (MW) | N/A | 22.0121 | 22.0729 | 21.9462 | 21.833 | 21.7222 | 21.5088 | 21.2244 | 20.9676 | 20.7229 | 20.5003 | 20.2593 | 20.0485 | 19.8786 | 19.6782 | 19.4908 | 20.6111 | 18.0765 | 16.6592 | 13.0067
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Leading the Way | Headroom (MW) | N/A | 22.0456 | 22.1881 | 22.2063 | 22.217 | 22.2315 | 22.1527 | 21.6455 | 21.624 | 21.3369 | 21.2971 | 20.967 | 20.7294 | 20.4924 | 20.2127 | 20.2177 | 21.5771 | 21.4617 | 17.5873 | 14.3139
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | Steady Progression | Headroom (MW) | N/A | 21.9868 | 22.047 | 21.9479 | 21.9311 | 21.9032 | 21.8498 | 21.7514 | 21.7189 | 21.5704 | 21.5295 | 21.4791 | 21.2946 | 21.131 | 20.9613 | 20.9292 | 20.8857 | 20.7157 | 20.4182 | 19.7413
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | System Transformation | Headroom (MW) | N/A | 22.012 | 22.1037 | 22.0261 | 21.986 | 21.9184 | 21.826 | 21.6586 | 21.5206 | 21.3494 | 21.1885 | 21.0237 | 20.8997 | 20.816 | 20.7333 | 20.6807 | 21.9978 | 21.9228 | 22.0723 | 19.547
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | 52.6322 | -1.6878 | WPD Best View | Headroom (MW) | N/A | 21.9993 | 22.0952 | 22.0103 | 21.9943 | 21.9607 | 21.8885 | 21.8121 | 21.7464 | 21.651 | 21.5794 | 21.4741 | 21.3984 | 21.3496 | 21.3069 | 21.2911 | 21.2683 | 20.3477 | 18.6337 | 17.5831
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Consumer Transformation | Headroom (MW) | Thermal | 10.7844 | 10.7361 | 10.6519 | 10.599 | 10.5434 | 10.4837 | 10.3958 | 10.3214 | 10.2439 | 10.1975 | 10.1156 | 9.1374 | 9.0966 | 9.044 | 9.0254 | 8.0551 | 4.3071 | -0.1268 | -5.2321
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Leading the Way | Headroom (MW) | Thermal | 10.7892 | 10.7567 | 10.6832 | 10.6562 | 10.6287 | 10.6037 | 10.5889 | 10.5744 | 10.5666 | 10.5787 | 10.5791 | 10.5761 | 10.4964 | 9.5128 | 7.9868 | 6.2812 | 2.4337 | -4.057 | -7.2204
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | Steady Progression | Headroom (MW) | N/A | 10.787 | 10.7507 | 10.6792 | 10.6412 | 10.5973 | 10.5645 | 10.5327 | 10.4981 | 10.473 | 10.4425 | 10.4179 | 10.3865 | 10.3794 | 10.3666 | 10.3647 | 10.3761 | 10.4305 | 10.2956 | 8.8642
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | System Transformation | Headroom (MW) | N/A | 10.786 | 10.7488 | 10.6657 | 10.6236 | 10.5735 | 10.5255 | 10.472 | 10.4161 | 10.3486 | 10.297 | 10.257 | 10.2261 | 10.2044 | 10.1842 | 10.1865 | 10.1869 | 8.0378 | 5.2589 | 3.4744
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | 52.5822 | -1.6299 | WPD Best View | Headroom (MW) | Thermal | 10.7837 | 10.7344 | 10.6472 | 10.5925 | 10.5342 | 10.471 | 10.3786 | 10.2993 | 10.2248 | 10.1722 | 10.091 | 9.106 | 9.0643 | 9.0101 | 8.9803 | 7.9995 | 5.2099 | 2.1691 | -1.9479
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Consumer Transformation | Headroom (MW) | N/A | 26.7971 | 26.745 | 26.609 | 26.4622 | 26.2465 | 25.9732 | 25.5836 | 25.2207 | 24.9307 | 24.6382 | 24.3238 | 24.0719 | 23.8384 | 23.592 | 23.3256 | 23.006 | 20.9251 | 17.0344 | 13.1158
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Leading the Way | Headroom (MW) | N/A | 26.8007 | 26.726 | 26.593 | 26.4854 | 26.4268 | 26.356 | 25.6933 | 25.629 | 25.3152 | 25.2596 | 24.9245 | 24.6851 | 24.4335 | 24.1588 | 24.0816 | 23.9417 | 21.6663 | 18.5894 | 15.1879
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | Steady Progression | Headroom (MW) | N/A | 26.7944 | 26.7361 | 26.5971 | 26.5182 | 26.4501 | 26.3755 | 26.1294 | 26.0579 | 25.8789 | 25.8086 | 25.7301 | 25.5186 | 25.3206 | 25.1286 | 25.0667 | 25.0073 | 24.7027 | 24.3469 | 23.652
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | System Transformation | Headroom (MW) | N/A | 26.797 | 26.7447 | 26.6082 | 26.5364 | 26.4715 | 26.3549 | 26.1325 | 25.916 | 25.6884 | 25.4698 | 25.2498 | 25.0844 | 24.9389 | 24.8209 | 24.7164 | 24.6149 | 24.2803 | 22.2088 | 19.5948
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | 52.6324 | -1.6873 | WPD Best View | Headroom (MW) | N/A | 26.7944 | 26.7362 | 26.5973 | 26.5236 | 26.4557 | 26.3814 | 26.3091 | 26.2383 | 26.1683 | 26.0993 | 26.0319 | 25.967 | 25.9045 | 25.8443 | 25.7868 | 25.7323 | 25.5043 | 25.3058 | 24.7645
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Consumer Transformation | Headroom (MW) | N/A | 32.5802 | 32.5416 | 32.4614 | 32.4655 | 32.5221 | 32.4885 | 32.398 | 32.2679 | 32.122 | 32.0185 | 31.9083 | 32.8699 | 32.7625 | 32.6721 | 32.5927 | 32.5089 | 30.9337 | 28.7215 | 27.7006
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Leading the Way | Headroom (MW) | N/A | 32.5844 | 32.5403 | 32.4623 | 32.4739 | 32.5926 | 32.6535 | 32.6175 | 32.5926 | 32.4679 | 32.4192 | 32.3698 | 33.4079 | 33.2543 | 33.0965 | 33.0753 | 31.6375 | 31.1736 | 28.1892 | 27.2443
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | Steady Progression | Headroom (MW) | N/A | 32.577 | 32.5368 | 32.4544 | 32.4434 | 32.4851 | 32.4973 | 32.4926 | 32.4665 | 32.4427 | 32.4187 | 32.3904 | 32.379 | 32.3529 | 32.3283 | 32.3043 | 32.2814 | 32.1229 | 31.9658 | 31.6522
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | System Transformation | Headroom (MW) | N/A | 32.5801 | 32.5414 | 32.4609 | 32.4648 | 32.5392 | 32.5721 | 32.5974 | 32.5655 | 32.5016 | 32.4593 | 32.4077 | 33.4327 | 33.3977 | 33.3714 | 33.3513 | 33.3443 | 33.3009 | 31.7068 | 31.1198
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | 52.6323 | -1.6877 | WPD Best View | Headroom (MW) | N/A | 32.577 | 32.5368 | 32.4544 | 32.4446 | 32.4863 | 32.4985 | 32.5015 | 32.4754 | 32.4543 | 32.4303 | 32.4046 | 32.3932 | 32.3684 | 32.3438 | 32.3198 | 32.2969 | 32.1592 | 32.0609 | 31.9006
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Consumer Transformation | Headroom (MW) | N/A | 15.8555 | 15.8169 | 15.7367 | 15.7408 | 15.7974 | 15.7638 | 15.6733 | 15.5432 | 15.3973 | 15.2938 | 15.1836 | 15.1199 | 15.0125 | 14.9221 | 14.8427 | 14.7589 | 13.1837 | 10.9715 | 9.9506
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Leading the Way | Headroom (MW) | N/A | 15.8597 | 15.8156 | 15.7376 | 15.7492 | 15.8679 | 15.9288 | 15.8928 | 15.8679 | 15.7432 | 15.6945 | 15.6451 | 15.6579 | 15.5043 | 15.3465 | 15.3253 | 13.8875 | 13.4236 | 10.4392 | 9.4943
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | Steady Progression | Headroom (MW) | N/A | 15.8523 | 15.8121 | 15.7297 | 15.7187 | 15.7604 | 15.7726 | 15.7679 | 15.7418 | 15.718 | 15.694 | 15.6657 | 15.6543 | 15.6282 | 15.6036 | 15.5796 | 15.5567 | 15.3982 | 15.2411 | 14.9275
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | System Transformation | Headroom (MW) | N/A | 15.8554 | 15.8167 | 15.7362 | 15.7401 | 15.8145 | 15.8474 | 15.8727 | 15.8408 | 15.7769 | 15.7346 | 15.683 | 15.6827 | 15.6477 | 15.6214 | 15.6013 | 15.5943 | 15.5509 | 13.9568 | 13.3698
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | 52.6382 | -1.7101 | WPD Best View | Headroom (MW) | N/A | 15.8523 | 15.8121 | 15.7297 | 15.7199 | 15.7616 | 15.7738 | 15.7768 | 15.7507 | 15.7296 | 15.7056 | 15.6799 | 15.6685 | 15.6437 | 15.6191 | 15.5951 | 15.5722 | 15.4345 | 15.3362 | 15.1759
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Consumer Transformation | Headroom (MW) | N/A | 25.935 | 25.7833 | 25.5283 | 25.3285 | 25.121 | 24.8705 | 24.5287 | 24.1886 | 23.8702 | 23.5205 | 23.1476 | 22.7261 | 22.3957 | 21.9883 | 21.5776 | 21.1538 | 19.0798 | 16.6589 | 10.787
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Leading the Way | Headroom (MW) | N/A | 25.9619 | 25.8781 | 25.6929 | 25.584 | 25.4682 | 25.389 | 25.2831 | 25.1617 | 25.0355 | 24.9069 | 24.7533 | 24.5496 | 24.3452 | 24.1364 | 23.9182 | 23.7885 | 20.264 | 18.8277 | 17.1878
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | Steady Progression | Headroom (MW) | N/A | 25.9681 | 25.8653 | 25.6747 | 25.5714 | 25.4734 | 25.3893 | 25.3039 | 25.2103 | 25.134 | 25.0434 | 24.9324 | 24.8431 | 24.7691 | 24.7172 | 24.6658 | 24.6157 | 24.6298 | 24.6403 | 24.0055
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | System Transformation | Headroom (MW) | N/A | 25.9511 | 25.8435 | 25.6253 | 25.4818 | 25.3407 | 25.2009 | 25.0115 | 24.8243 | 24.6162 | 24.408 | 24.1921 | 24.0047 | 23.8504 | 23.714 | 23.5872 | 23.4699 | 23.0658 | 22.3526 | 18.748
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | 52.7869 | -1.2096 | WPD Best View | Headroom (MW) | N/A | 25.9595 | 25.8634 | 25.673 | 25.5557 | 25.4258 | 25.3251 | 25.1901 | 25.036 | 24.8785 | 24.7007 | 24.5143 | 24.2597 | 24.0882 | 23.8297 | 23.5795 | 23.3644 | 21.1266 | 19.7624 | 15.9798
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Consumer Transformation | Headroom (MW) | Thermal | 29.1101 | 28.9338 | 28.5731 | 7.6768 | 7.1602 | 6.4552 | 5.4357 | 4.4658 | 3.4465 | 2.2795 | 0.96601 | -19.0409 | -20.3453 | -31.0528 | -32.2767 | -33.4752 | -42.5585 | -53.3275 | -65.7624
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Leading the Way | Headroom (MW) | Thermal | 29.1503 | 29.0208 | 28.7549 | 8.0516 | 7.8827 | -0.72767 | -20.3255 | -20.4855 | -21.146 | -21.7576 | -22.5911 | -23.3257 | -24.08 | -24.8795 | -28.9406 | -31.1823 | -39.936 | -49.2411 | -57.7032
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | Steady Progression | Headroom (MW) | N/A | 29.1229 | 28.9829 | 28.6727 | 7.9914 | 7.8188 | 7.6815 | 7.3877 | 7.275 | 7.0668 | 6.9392 | 6.7989 | 6.5457 | 6.3139 | 6.043 | 5.9036 | 5.7482 | 5.5156 | 3.7807 | 2.4108
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | System Transformation | Headroom (MW) | Thermal | 29.1258 | 28.9805 | 28.671 | 7.9607 | 7.7364 | 7.472 | 7.033 | 6.6037 | 6.089 | 5.5477 | 4.9942 | -14.199 | -14.6782 | -23.6336 | -24.0638 | -24.5013 | -27.3242 | -32.9728 | -39.1826
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | 52.7866 | -1.2097 | WPD Best View | Headroom (MW) | Thermal | 29.1503 | 29.0466 | 28.7807 | 8.1144 | 7.9453 | -0.66543 | -19.7743 | -20.2658 | -20.8509 | -21.5874 | -22.4309 | -23.3055 | -24.1499 | -24.937 | -29.0216 | -31.249 | -38.5477 | -47.9933 | -55.0049
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Consumer Transformation | Headroom (MW) | N/A | 24.2813 | 24.2397 | 24.1431 | 23.9664 | 23.7762 | 23.5145 | 23.1431 | 22.7932 | 22.446 | 22.0763 | 21.643 | 21.2071 | 20.7908 | 20.4123 | 20.0337 | 19.6192 | 17.4749 | 15.2208 | 13.0936
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Leading the Way | Headroom (MW) | N/A | 24.2839 | 24.2377 | 24.1472 | 24.0781 | 24.0219 | 23.9713 | 23.5171 | 23.4667 | 23.2295 | 23.1838 | 22.9282 | 22.7854 | 22.62 | 22.4312 | 22.2849 | 22.1135 | 21.1543 | 20.0345 | 18.8688
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | Steady Progression | Headroom (MW) | N/A | 24.2795 | 24.2347 | 24.1372 | 24.0787 | 24.0219 | 23.9685 | 23.7773 | 23.724 | 23.5796 | 23.5282 | 23.477 | 23.3013 | 23.1383 | 22.9763 | 22.9305 | 22.8859 | 22.6577 | 22.3996 | 22.01
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | System Transformation | Headroom (MW) | N/A | 24.2813 | 24.2397 | 24.1454 | 24.0885 | 24.0301 | 23.9021 | 23.7161 | 23.5269 | 23.3024 | 23.095 | 22.8782 | 22.6709 | 22.4811 | 22.3098 | 22.1497 | 21.9735 | 21.2986 | 20.5588 | 19.7327
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | 52.7815 | -1.1937 | WPD Best View | Headroom (MW) | N/A | 24.2839 | 24.2467 | 24.1562 | 24.0996 | 24.0434 | 23.9927 | 23.8585 | 23.715 | 23.5645 | 23.4103 | 23.1581 | 22.8765 | 22.6318 | 22.4535 | 22.2849 | 22.1135 | 21.1543 | 20.0345 | 18.8688
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Consumer Transformation | Headroom (MW) | Thermal | 16.6281 | 16.512 | 16.3103 | 16.1369 | 15.975 | 15.7459 | 15.3835 | 15.0308 | 14.6776 | 14.302 | 13.8904 | 13.4986 | 13.1204 | 11.8221 | 11.4785 | 11.093 | 7.8614 | 3.6872 | -1.62
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Leading the Way | Headroom (MW) | N/A | 16.657 | 16.5973 | 16.4697 | 16.4016 | 16.3269 | 16.2602 | 16.1307 | 15.942 | 15.7473 | 15.5477 | 15.3513 | 15.1746 | 14.9969 | 14.8339 | 12.9845 | 11.1209 | 8.1264 | 3.3462 | 0.039579
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | Steady Progression | Headroom (MW) | N/A | 16.6492 | 16.582 | 16.4435 | 16.3734 | 16.3025 | 16.2444 | 16.1725 | 16.1006 | 16.0252 | 15.9455 | 15.857 | 15.7755 | 15.7051 | 15.6394 | 15.592 | 15.5333 | 15.473 | 14.1358 | 13.6849
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | System Transformation | Headroom (MW) | N/A | 16.6438 | 16.5588 | 16.4063 | 16.2995 | 16.1773 | 16.0594 | 15.8734 | 15.6811 | 15.4694 | 15.2565 | 15.0339 | 14.8468 | 14.6761 | 14.5154 | 14.3655 | 14.212 | 12.4004 | 10.5578 | 7.3249
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | 52.7489 | -1.1742 | WPD Best View | Headroom (MW) | N/A | 16.657 | 16.5973 | 16.4697 | 16.4016 | 16.3269 | 16.2602 | 16.1307 | 15.942 | 15.7473 | 15.5477 | 15.3513 | 15.1746 | 14.9969 | 14.8339 | 12.9845 | 11.1209 | 8.1264 | 3.3462 | 0.039579
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Consumer Transformation | Headroom (MW) | Thermal | 16.6615 | 16.6428 | 16.5804 | 16.5402 | 16.3756 | 16.1616 | 15.8758 | 15.6085 | 15.2896 | 14.8679 | 14.3994 | 13.8913 | 13.3814 | 12.8376 | 12.336 | 11.9374 | 8.2301 | 3.8893 | -1.1112
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Leading the Way | Headroom (MW) | Thermal | 16.6701 | 16.6465 | 16.5987 | 16.5386 | 16.5006 | 16.4945 | 16.1515 | 16.2306 | 16.0021 | 15.6358 | 15.2542 | 14.8391 | 14.4278 | 13.9802 | 11.9148 | 11.7081 | 6.9081 | 3.5029 | -0.48674
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | Steady Progression | Headroom (MW) | N/A | 16.6549 | 16.627 | 16.5527 | 16.5061 | 16.4611 | 16.4353 | 16.4046 | 16.4171 | 16.4287 | 16.4323 | 16.4316 | 16.4356 | 16.4372 | 16.394 | 16.3478 | 16.2957 | 16.3516 | 16.212 | 15.6826
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | System Transformation | Headroom (MW) | N/A | 16.6614 | 16.6427 | 16.58 | 16.5395 | 16.4958 | 16.4773 | 16.4102 | 16.3624 | 16.2839 | 16.163 | 16.0488 | 15.9212 | 15.8025 | 15.666 | 15.5458 | 15.438 | 15.1016 | 12.0354 | 9.8846
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | 52.7697 | -1.2851 | WPD Best View | Headroom (MW) | N/A | 16.6701 | 16.6633 | 16.6154 | 16.58 | 16.5417 | 16.5353 | 16.3613 | 16.2021 | 15.9621 | 15.5794 | 15.1845 | 14.7682 | 14.3463 | 13.9004 | 11.8338 | 11.6414 | 8.2965 | 4.7507 | 2.2115
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Consumer Transformation | Headroom (MW) | N/A | 95.7812 | 95.073 | 93.7348 | 92.7614 | 90.5888 | 88.8808 | 85.3079 | 82.8071 | 80.0106 | 77.508 | 74.2985 | 69.7389 | 65.9856 | 62.0846 | 58.2575 | 55.2145 | 83.128 | 71.1972 | 62.2403
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Leading the Way | Headroom (MW) | N/A | 94.9244 | 94.3405 | 93.3007 | 92.27 | 90.6459 | 90.1403 | 86.1628 | 84.3453 | 82.1045 | 80.3294 | 77.9257 | 90.0759 | 88.0553 | 84.428 | 81.1483 | 127.974 | 140.1717 | 143.2445 | 125.1775
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | Steady Progression | Headroom (MW) | N/A | 95.8377 | 95.2306 | 94.1636 | 93.5976 | 93.0763 | 92.6494 | 90.1766 | 88.5848 | 86.5603 | 84.9604 | 83.2404 | 81.1787 | 78.8561 | 76.5777 | 74.7071 | 74.2418 | 69.6794 | 63.3429 | 57.8091
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | System Transformation | Headroom (MW) | N/A | 95.857 | 95.5161 | 94.3853 | 93.7331 | 93.0501 | 92.4382 | 90.6215 | 89.3398 | 87.351 | 85.8403 | 83.9244 | 81.8474 | 79.8151 | 77.8779 | 75.8176 | 123.8884 | 117.0709 | 120.1023 | 128.0422
Ratcliffe 132kV | Nottingham | Nottingham | Bulk Supply Point | 33 | 52.9321 | -1.1624 | WPD Best View | Headroom (MW) | N/A | 97.9516 | 97.6394 | 96.5236 | 95.7999 | 94.8901 | 93.5127 | 91.2712 | 88.8179 | 86.4731 | 84.1821 | 81.8086 | 92.8298 | 90.7465 | 88.6472 | 86.5853 | 133.5337 | 142.9495 | 144.8817 | 121.3014
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Consumer Transformation | Headroom (MW) | N/A | 18.208 | 18.1725 | 18.0955 | 18.0577 | 18.0175 | 17.8232 | 17.4616 | 17.1249 | 16.7971 | 16.4621 | 16.1168 | 15.8052 | 15.514 | 15.2163 | 14.9568 | 14.6631 | 12.5942 | 10.1741 | 7.7779
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Leading the Way | Headroom (MW) | N/A | 18.2094 | 18.1627 | 18.0883 | 18.0347 | 17.996 | 17.9567 | 17.8007 | 17.7655 | 17.6946 | 17.6654 | 17.5959 | 17.4742 | 17.3458 | 17.2028 | 17.2595 | 17.327 | 16.9012 | 15.5857 | 14.0826
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | Steady Progression | Headroom (MW) | N/A | 18.207 | 18.1693 | 18.0901 | 18.0475 | 18.0054 | 17.9629 | 17.9074 | 17.8664 | 17.8206 | 17.7801 | 17.7359 | 17.6974 | 17.6579 | 17.622 | 17.6131 | 17.6107 | 17.4658 | 17.2951 | 16.925
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | System Transformation | Headroom (MW) | N/A | 18.2079 | 18.1722 | 18.095 | 18.0568 | 18.0157 | 17.9737 | 17.9273 | 17.8408 | 17.6254 | 17.4076 | 17.1973 | 17.0146 | 16.8621 | 16.7321 | 16.6541 | 16.574 | 16.1124 | 15.3954 | 14.4404
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | 52.9303 | -1.2151 | WPD Best View | Headroom (MW) | N/A | 18.208 | 18.1726 | 18.0959 | 18.0582 | 18.0183 | 17.9382 | 17.6254 | 17.3433 | 17.0689 | 16.7837 | 16.4946 | 16.2308 | 15.9883 | 15.7437 | 15.5434 | 15.3143 | 13.4721 | 11.204 | 8.9297
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Consumer Transformation | Headroom (MW) | N/A | 19.6455 | 19.3913 | 19.3158 | 19.2972 | 19.2443 | 19.1979 | 18.4725 | 18.4438 | 18.0433 | 17.9946 | 17.5006 | 16.6828 | 15.7889 | 14.9263 | 13.8596 | 13.8187 | 12.2887 | 10.4414 | 8.4897
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Leading the Way | Headroom (MW) | N/A | 18.641 | 18.281 | 18.2212 | 17.8829 | 17.8343 | 17.7925 | 16.1465 | 15.0996 | 14.2619 | 13.185 | 12.2528 | 11.7571 | 11.36 | 10.8378 | 10.7951 | 10.7523 | 9.1542 | 7.5092 | 5.8679
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | Steady Progression | Headroom (MW) | N/A | 19.6299 | 19.3691 | 19.2808 | 19.2513 | 19.1965 | 19.1485 | 18.4892 | 18.448 | 17.9799 | 17.9284 | 17.5468 | 16.8905 | 16.3005 | 15.7127 | 14.6383 | 14.5895 | 13.1851 | 11.9529 | 10.5708
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | System Transformation | Headroom (MW) | N/A | 19.6455 | 19.6107 | 19.5351 | 19.5163 | 19.4632 | 19.4165 | 18.8297 | 18.7998 | 18.334 | 18.2825 | 17.8184 | 17.2311 | 16.6448 | 16.0586 | 14.9852 | 14.939 | 13.7514 | 12.5427 | 11.4621
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | 52.9491 | -1.1518 | WPD Best View | Headroom (MW) | N/A | 19.6663 | 19.6391 | 19.5792 | 19.577 | 19.5284 | 19.4865 | 19.4314 | 19.2555 | 19.0916 | 18.9316 | 18.7856 | 18.6719 | 18.56 | 18.4496 | 18.3182 | 18.1709 | 17.2841 | 16.2867 | 15.231
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Consumer Transformation | Headroom (MW) | N/A | 23.7556 | 23.6739 | 23.4115 | 23.1769 | 22.9372 | 22.6161 | 22.1446 | 21.6998 | 21.2608 | 20.7679 | 20.2196 | 19.7185 | 19.229 | 18.7286 | 18.2554 | 17.7598 | 15.0258 | 12.0652 | 8.2179
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Leading the Way | Headroom (MW) | N/A | 23.7851 | 23.8112 | 23.6464 | 23.5304 | 23.4046 | 23.2834 | 23.1329 | 22.9593 | 22.7562 | 22.5505 | 22.3014 | 22.0592 | 21.8248 | 21.5101 | 21.294 | 21.1496 | 20.1117 | 17.2776 | 14.159
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | Steady Progression | Headroom (MW) | N/A | 23.7907 | 23.7552 | 23.6001 | 23.5201 | 23.4492 | 23.3861 | 23.3028 | 23.2226 | 23.1322 | 23.0304 | 22.901 | 22.8145 | 22.7278 | 22.6504 | 22.6209 | 22.573 | 22.5745 | 22.5412 | 21.8874
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | System Transformation | Headroom (MW) | N/A | 23.7763 | 23.7528 | 23.5614 | 23.4533 | 23.3115 | 23.164 | 22.9241 | 22.6912 | 22.4173 | 22.1545 | 21.865 | 21.6206 | 21.3978 | 21.1923 | 21.0431 | 20.8711 | 20.2287 | 19.4504 | 18.3389
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | 52.9039 | -1.1785 | WPD Best View | Headroom (MW) | N/A | 23.7768 | 23.7682 | 23.58 | 23.4258 | 23.2676 | 23.0862 | 22.85 | 22.6071 | 22.3588 | 22.0954 | 21.7644 | 21.4386 | 21.1083 | 20.7656 | 20.4594 | 20.161 | 18.6575 | 16.7932 | 12.5313
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Consumer Transformation | Headroom (MW) | Thermal | 0.038325 | 0.0043959 | -0.12607 | -0.27021 | -0.42954 | -0.60932 | -0.87882 | -1.1477 | -1.4252 | -1.7031 | -2.0321 | -3.2737 | -3.5803 | -3.882 | -4.1594 | -4.4662 | -8.2745 | -14.647 | -20.6133
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Leading the Way | Headroom (MW) | Thermal | 0.067825 | 0.080368 | -0.0083928 | -0.088124 | -0.17724 | -0.24779 | -0.36867 | -0.49612 | -0.64236 | -0.7766 | -0.92275 | -1.0172 | -1.1144 | -2.4866 | -5.1949 | -6.9842 | -11.4905 | -16.9977 | -22.5383
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | Steady Progression | Headroom (MW) | Thermal | 0.054945 | 0.047526 | -0.024414 | -0.065132 | -0.10366 | -0.11817 | -0.16193 | -0.21385 | -0.26074 | -0.31833 | -0.38842 | -0.43748 | -0.48809 | -0.54898 | -0.59271 | -0.64553 | -0.78682 | -2.1162 | -2.4139
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | System Transformation | Headroom (MW) | Thermal | 0.057063 | 0.046944 | -0.044087 | -0.11296 | -0.19045 | -0.25706 | -0.38816 | -0.5251 | -0.69796 | -0.85728 | -1.0227 | -1.1559 | -1.2954 | -1.4268 | -1.5485 | -1.67 | -3.428 | -8.6993 | -11.7478
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | 52.9236 | -1.0308 | WPD Best View | Headroom (MW) | Thermal | 0.038325 | 0.0043959 | -0.12607 | -0.27021 | -0.42954 | -0.60932 | -0.87882 | -1.1477 | -1.4252 | -1.7031 | -2.0321 | -3.2737 | -3.5803 | -3.882 | -4.1594 | -4.4662 | -8.2745 | -14.647 | -20.6133
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Consumer Transformation | Headroom (MW) | N/A | 6.4861 | 6.435 | 6.3351 | 6.2801 | 6.2265 | 6.1735 | 6.118 | 6.0665 | 6.0124 | 5.9631 | 5.9102 | 5.8609 | 5.7811 | 5.6749 | 5.5777 | 5.4674 | 4.7942 | 3.9886 | 7.2521
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Leading the Way | Headroom (MW) | N/A | 6.4865 | 6.4343 | 6.3343 | 6.2783 | 6.225 | 6.1723 | 6.1114 | 6.0602 | 6.0074 | 5.9594 | 5.9091 | 5.8533 | 5.7958 | 5.7348 | 5.6968 | 5.659 | 15.3613 | 14.7371 | 14.0551
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | Steady Progression | Headroom (MW) | Thermal | 6.4857 | 6.4344 | 6.3342 | 6.2788 | 6.2247 | 6.1711 | 5.0918 | 4.0141 | 2.9366 | 1.8602 | 1.0555 | 0.31674 | -0.7577 | -1.8311 | -2.3101 | -2.3565 | -4.1167 | -6.3658 | -6.6097
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | System Transformation | Headroom (MW) | N/A | 6.4861 | 6.4349 | 6.3349 | 6.2798 | 6.226 | 6.1727 | 6.1197 | 6.0674 | 6.0156 | 5.9647 | 5.9148 | 5.8658 | 5.8178 | 5.7714 | 5.7268 | 5.6836 | 5.4878 | 5.1679 | 8.7797
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | 52.944 | -1.1888 | WPD Best View | Headroom (MW) | N/A | 6.4865 | 6.4351 | 6.3352 | 6.2803 | 6.227 | 6.1743 | 6.1224 | 6.0712 | 6.0214 | 5.9734 | 5.9277 | 5.8845 | 5.8435 | 5.8044 | 5.7664 | 5.7287 | 15.3613 | 14.7371 | 14.0551
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Consumer Transformation | Headroom (MW) | N/A | 24.0006 | 23.9483 | 23.8532 | 23.7828 | 23.7182 | 23.6507 | 23.5739 | 23.5112 | 23.4356 | 23.3885 | 23.3105 | 23.2756 | 23.2115 | 23.19 | 23.1452 | 23.102 | 22.2206 | 21.0359 | 19.8317
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Leading the Way | Headroom (MW) | N/A | 24.0017 | 23.9496 | 23.8675 | 23.7907 | 23.7286 | 23.6624 | 23.3919 | 23.3316 | 23.2535 | 23.212 | 23.1371 | 23.0862 | 22.9911 | 22.9451 | 22.9073 | 22.867 | 22.6026 | 22.2134 | 21.7432
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | Steady Progression | Headroom (MW) | N/A | 23.9996 | 23.9432 | 23.8381 | 23.7666 | 23.7006 | 23.6337 | 23.5626 | 23.4972 | 23.4304 | 23.3743 | 23.3099 | 23.2681 | 23.2084 | 23.1753 | 23.1211 | 23.0673 | 22.8536 | 22.6496 | 22.3331
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | System Transformation | Headroom (MW) | N/A | 24.0006 | 23.9482 | 23.8529 | 23.7824 | 23.7174 | 23.6494 | 23.5835 | 23.5196 | 23.4549 | 23.4052 | 23.3429 | 23.315 | 23.2572 | 23.2433 | 23.1928 | 23.1448 | 23.0067 | 22.8092 | 22.4291
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | 52.9347 | -1.1639 | WPD Best View | Headroom (MW) | N/A | 24.0017 | 23.9547 | 23.8726 | 23.8027 | 23.7405 | 23.6743 | 23.6111 | 23.5506 | 23.487 | 23.4449 | 23.3884 | 23.3806 | 23.3347 | 23.3464 | 23.3076 | 23.2665 | 23.1441 | 22.8896 | 21.9625
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Consumer Transformation | Headroom (MW) | N/A | 14.1631 | 14.1575 | 14.0924 | 14.0758 | 13.0415 | 13.0799 | 12.931 | 12.9238 | 12.919 | 12.9674 | 12.9439 | 12.744 | 12.5563 | 12.1515 | 11.7646 | 11.3669 | 9.4725 | 7.3041 | 5.1248
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Leading the Way | Headroom (MW) | N/A | 14.1761 | 14.1784 | 14.1216 | 14.104 | 13.0834 | 13.1504 | 12.6942 | 12.7011 | 12.5292 | 12.6105 | 12.382 | 12.0479 | 11.7258 | 11.3164 | 11.3127 | 11.3018 | 10.418 | 9.4342 | 8.461
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | Steady Progression | Headroom (MW) | N/A | 14.1533 | 14.1371 | 14.0646 | 14.0393 | 14.0204 | 14.0361 | 13.9041 | 13.8846 | 13.8971 | 13.912 | 13.9259 | 13.7889 | 13.6826 | 13.562 | 13.5526 | 13.5441 | 13.5086 | 13.3569 | 12.8847
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | System Transformation | Headroom (MW) | N/A | 14.163 | 14.1573 | 14.092 | 14.0752 | 14.0658 | 14.1037 | 14.0157 | 14.0068 | 14.0484 | 14.0925 | 14.1422 | 14.0289 | 13.9446 | 13.831 | 13.8308 | 13.8288 | 13.8631 | 13.6498 | 13.0495
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | 52.9487 | -1.1326 | WPD Best View | Headroom (MW) | N/A | 16.2227 | 16.2266 | 16.1655 | 16.1565 | 16.1053 | 15.9328 | 15.6235 | 15.1763 | 14.7712 | 14.4655 | 14.2001 | 13.9507 | 13.8609 | 13.7087 | 13.5439 | 13.3599 | 12.1805 | 10.8343 | 9.3822
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Consumer Transformation | Headroom (MW) | N/A | 15.9784 | 15.9407 | 15.853 | 15.8052 | 15.7582 | 15.7117 | 15.5477 | 15.5026 | 15.4523 | 15.4087 | 15.3583 | 15.1827 | 14.9948 | 14.8139 | 14.7779 | 14.7427 | 14.1601 | 13.0149 | 11.8636
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Leading the Way | Headroom (MW) | N/A | 15.9847 | 15.9475 | 15.8597 | 15.81 | 15.7628 | 15.7163 | 15.3925 | 15.3469 | 15.1662 | 15.1235 | 14.9301 | 14.8671 | 14.8001 | 14.7264 | 14.6936 | 14.6609 | 14.3954 | 14.0789 | 13.7473
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | Steady Progression | Headroom (MW) | N/A | 14.5657 | 14.5537 | 14.5444 | 14.5354 | 14.5266 | 14.5186 | 14.5088 | 14.4994 | 14.4841 | 14.4683 | 14.4516 | 14.4348 | 14.412 | 14.3944 | 14.3762 | 14.3512 | 14.2116 | 14.0523 | 13.8727
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | System Transformation | Headroom (MW) | N/A | 15.9784 | 15.9406 | 15.8529 | 15.8051 | 15.7579 | 15.7113 | 15.5723 | 15.5266 | 15.4807 | 15.4357 | 15.3915 | 15.2555 | 15.1202 | 14.9865 | 14.9472 | 14.9092 | 14.7555 | 14.5881 | 14.3808
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | 52.9557 | -1.1544 | WPD Best View | Headroom (MW) | N/A | 15.9847 | 15.9489 | 15.8611 | 15.8137 | 15.7665 | 15.7199 | 15.6736 | 15.628 | 15.5836 | 15.541 | 15.5007 | 15.4628 | 15.4272 | 15.3932 | 15.3605 | 15.3278 | 15.1717 | 14.6109 | 13.7748
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Consumer Transformation | Headroom (MW) | N/A | 20.0371 | 19.8984 | 19.7071 | 19.4702 | 19.2213 | 18.8138 | 18.2137 | 17.6202 | 17.0717 | 16.4591 | 15.7853 | 15.1132 | 14.4428 | 13.7583 | 13.0851 | 12.4086 | 9.0947 | 6.1507 | 2.5575
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Leading the Way | Headroom (MW) | N/A | 19.9463 | 19.872 | 19.7921 | 19.6792 | 19.5632 | 19.372 | 19.0803 | 18.7629 | 18.4814 | 18.1731 | 17.8422 | 17.506 | 17.1515 | 16.7631 | 16.3554 | 16.0191 | 14.9323 | 12.6423 | 11.4666
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | Steady Progression | Headroom (MW) | N/A | 16.6142 | 16.5817 | 16.5457 | 16.5172 | 16.4852 | 16.4572 | 16.4109 | 16.3474 | 16.2862 | 16.2102 | 16.109 | 16.0255 | 15.942 | 15.8516 | 15.7659 | 15.6731 | 15.2748 | 14.8668 | 14.3826
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | System Transformation | Headroom (MW) | N/A | 19.3836 | 19.3133 | 19.2326 | 19.1263 | 19.0109 | 18.8634 | 18.5961 | 18.334 | 18.032 | 17.721 | 17.3982 | 17.0954 | 16.7917 | 16.4814 | 16.1774 | 15.8581 | 14.4868 | 13.4841 | 12.6795
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | 52.925 | -1.1398 | WPD Best View | Headroom (MW) | N/A | 19.0482 | 18.9186 | 18.7469 | 18.5256 | 18.2998 | 17.9258 | 17.3728 | 16.8249 | 16.3185 | 15.7487 | 15.1142 | 14.473 | 13.8278 | 13.1755 | 12.527 | 11.8701 | 8.8093 | 6.0768 | 2.7276
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Consumer Transformation | Headroom (MW) | N/A | 21.9874 | 21.8151 | 21.5017 | 21.2184 | 20.9144 | 20.4803 | 19.8597 | 19.2677 | 18.7024 | 18.0948 | 17.4548 | 16.8412 | 16.2292 | 15.6297 | 15.0242 | 14.3403 | 10.6563 | 6.9052 | 3.4454
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Leading the Way | Headroom (MW) | N/A | 22.0484 | 21.9553 | 21.7574 | 21.6182 | 21.4655 | 21.297 | 21.0551 | 20.8166 | 20.574 | 20.332 | 20.0922 | 19.8471 | 19.6031 | 19.3296 | 19.0357 | 18.7248 | 17.215 | 15.5237 | 13.8244
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | Steady Progression | Headroom (MW) | N/A | 22.0292 | 21.9353 | 21.7639 | 21.6651 | 21.5634 | 21.4733 | 21.3676 | 21.2561 | 21.1287 | 20.9984 | 20.8418 | 20.7007 | 20.5756 | 20.4615 | 20.3559 | 20.2453 | 19.8174 | 19.4027 | 18.6063
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | System Transformation | Headroom (MW) | N/A | 22.0242 | 21.9182 | 21.7031 | 21.5403 | 21.3589 | 21.1727 | 20.8607 | 20.564 | 20.2063 | 19.8589 | 19.5037 | 19.1746 | 18.87 | 18.5723 | 18.2843 | 17.9803 | 16.6429 | 15.3793 | 14.1447
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | 52.9552 | -1.1839 | WPD Best View | Headroom (MW) | N/A | 22.0484 | 21.9553 | 21.7574 | 21.6182 | 21.4655 | 21.297 | 21.0551 | 20.8166 | 20.574 | 20.332 | 20.0922 | 19.8471 | 19.6031 | 19.3296 | 19.0357 | 18.7248 | 17.215 | 15.5237 | 13.8244
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Consumer Transformation | Headroom (MW) | Thermal | 29.0031 | 28.7078 | 19.8755 | 19.3744 | 18.846 | 18.1848 | 17.0524 | 16.0741 | 15.1713 | 14.1639 | 13.1277 | 12.234 | 11.4247 | 10.63 | 9.8186 | 8.8597 | 2.796 | -4.8596 | -13.86
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Leading the Way | Headroom (MW) | N/A | 29.0579 | 28.8444 | 20.2631 | 19.978 | 19.7314 | 19.5081 | 18.7659 | 18.6015 | 18.377 | 18.2397 | 17.9899 | 17.6155 | 16.9806 | 16.2775 | 16.246 | 16.2469 | 13.61 | 37.628 | 29.9538
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | Steady Progression | Headroom (MW) | Thermal | 29.0216 | 28.8469 | 20.2566 | 20.0384 | 19.8286 | 19.6383 | 15.3035 | 11.0138 | 6.716 | 2.3811 | -0.066667 | -2.2539 | -2.4162 | -2.5582 | -2.6516 | -2.738 | -3.0407 | -3.6556 | -5.4369
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | System Transformation | Headroom (MW) | N/A | 29.028 | 28.8449 | 20.1771 | 19.8653 | 19.5363 | 19.1722 | 18.6378 | 18.1767 | 17.6029 | 16.9217 | 16.2604 | 15.7344 | 15.2798 | 14.9175 | 14.5925 | 14.2988 | 13.2325 | 10.9949 | 6.3946
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | 52.9167 | -1.2642 | WPD Best View | Headroom (MW) | Thermal | 29.0085 | 28.7184 | 19.9039 | 19.4145 | 18.8969 | 18.2555 | 17.1566 | 16.2042 | 15.335 | 14.3552 | 13.344 | 12.4514 | 11.6417 | 10.847 | 10.0217 | 9.0589 | 3.1262 | -4.4231 | -13.4053
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Consumer Transformation | Headroom (MW) | Thermal | 2.8962 | 2.873 | 2.8189 | 2.7984 | 2.7729 | 2.7367 | 2.506 | 2.2941 | 2.1139 | 1.9228 | 1.7249 | 1.5674 | 1.4288 | 1.2965 | 1.1643 | 0.98947 | -0.17572 | -1.7905 | -3.446
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Leading the Way | Headroom (MW) | N/A | 2.8993 | 2.8649 | 2.8128 | 2.7774 | 2.7537 | 2.7281 | 2.579 | 2.5566 | 2.4965 | 2.4795 | 2.4209 | 2.3129 | 2.203 | 2.0852 | 2.0927 | 2.0996 | 1.8061 | 8.5854 | 6.3948
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | Steady Progression | Headroom (MW) | Thermal | 2.8938 | 2.8685 | 2.8124 | 2.7859 | 2.7578 | 2.7284 | -1.4155 | -5.5449 | -9.6794 | -13.8089 | -16.0117 | -18.0222 | -18.0499 | -18.0741 | -18.0968 | -18.1176 | -18.2147 | -18.3351 | -18.6719
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | System Transformation | Headroom (MW) | N/A | 2.8961 | 2.8727 | 2.8182 | 2.7972 | 2.7708 | 2.7423 | 2.7092 | 2.6815 | 2.615 | 2.4772 | 2.3477 | 2.2569 | 2.1782 | 2.1251 | 2.0838 | 2.0408 | 1.9803 | 1.5713 | 0.84518
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | 52.9158 | -1.2292 | WPD Best View | Headroom (MW) | Thermal | 2.8962 | 2.873 | 2.8189 | 2.7984 | 2.7729 | 2.7373 | 2.5069 | 2.2963 | 2.1178 | 1.9297 | 1.7358 | 1.5825 | 1.446 | 1.3178 | 1.1884 | 1.0114 | -0.18795 | -1.843 | -3.5433
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Consumer Transformation | Headroom (MW) | Fault level | 6.9677 | 6.8778 | 6.738 | 6.573 | 6.384 | 6.1162 | 5.7048 | 5.3078 | 4.9078 | 4.4535 | 3.9599 | 3.4785 | 3.0086 | 2.5256 | 2.0276 | 1.4613 | -1.4964 | -4.4015 | -8.1677
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Leading the Way | Headroom (MW) | Fault level | 6.9531 | 6.9356 | 6.9004 | 6.8465 | 6.7811 | 6.7147 | 6.6263 | 6.5202 | 6.3911 | 6.199 | 5.9547 | 5.6795 | 5.4112 | 5.1462 | 4.87 | 4.5727 | 2.2866 | 0.9426 | -1.4673
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | Steady Progression | Headroom (MW) | N/A | 5.7982 | 5.775 | 5.7567 | 5.7344 | 5.7182 | 5.7027 | 5.6798 | 5.6453 | 5.6036 | 5.5543 | 5.4757 | 5.4163 | 5.3623 | 5.3119 | 5.266 | 5.2027 | 4.8397 | 4.3918 | 3.8446
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | System Transformation | Headroom (MW) | Fault level | 6.7544 | 6.7184 | 6.6622 | 6.5843 | 6.4956 | 6.396 | 6.2082 | 6.0148 | 5.7809 | 5.5283 | 5.2718 | 5.033 | 4.7988 | 4.5755 | 4.3429 | 4.0754 | 2.8442 | 1.8004 | -0.1535
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | 52.8983 | -1.2748 | WPD Best View | Headroom (MW) | Fault level | 6.6235 | 6.538 | 6.4051 | 6.2483 | 6.0686 | 5.814 | 5.423 | 5.0455 | 4.6654 | 4.2335 | 3.7643 | 3.3067 | 2.8599 | 2.4008 | 1.9274 | 1.3912 | -1.4025 | -4.1347 | -7.6889
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Consumer Transformation | Headroom (MW) | Fault level | -23.5327 | -23.6246 | -23.7638 | -23.952 | -24.1517 | -24.3769 | -24.7229 | -25.0578 | -25.3689 | -25.7078 | -26.0742 | -26.4282 | -26.7841 | -27.1377 | -27.5049 | -27.9252 | -30.1108 | -32.246 | -34.2199
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Leading the Way | Headroom (MW) | Fault level | -23.3549 | -23.4107 | -23.4833 | -23.6041 | -23.7325 | -23.8259 | -23.9465 | -24.1012 | -24.2136 | -24.3296 | -24.4635 | -24.6022 | -24.7731 | -24.9549 | -25.1734 | -25.3975 | -26.3397 | -27.3907 | -28.4974
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | Steady Progression | Headroom (MW) | Fault level | -19.4317 | -19.4544 | -19.4831 | -19.5099 | -19.5396 | -19.5527 | -19.5812 | -19.6149 | -19.6507 | -19.6912 | -19.7523 | -19.7961 | -19.8374 | -19.8828 | -19.9203 | -19.975 | -20.2415 | -20.6071 | -21.0607
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | System Transformation | Headroom (MW) | Fault level | -22.6936 | -22.7419 | -22.8017 | -22.8806 | -22.972 | -23.057 | -23.2074 | -23.3642 | -23.5399 | -23.7168 | -23.9087 | -24.0788 | -24.2517 | -24.4125 | -24.5877 | -24.7773 | -25.698 | -26.4617 | -27.1678
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | 52.9168 | -1.2645 | WPD Best View | Headroom (MW) | Fault level | -22.3677 | -22.4501 | -22.5688 | -22.7395 | -22.9211 | -23.1205 | -23.4191 | -23.7161 | -23.9855 | -24.2921 | -24.6291 | -24.9757 | -25.327 | -25.6771 | -26.0471 | -26.4528 | -28.3996 | -30.3109 | -32.0855
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Consumer Transformation | Headroom (MW) | Thermal | 4.0933 | 3.7387 | 3.0203 | 2.3786 | 1.5804 | 0.50383 | -1.0553 | -2.5096 | -4.0971 | -7.3776 | -10.9092 | -12.4986 | -16.7627 | -0.89115 | -2.9263 | -14.3712 | -40.5151 | -79.4596 | -129.9319
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Leading the Way | Headroom (MW) | Thermal | 4.2155 | 4.017 | 3.6671 | 3.4215 | 3.063 | 2.5097 | 1.7224 | 0.92601 | -8.6233 | -9.3482 | -9.995 | -12.2365 | -12.5885 | -0.30581 | -8.6923 | -30.7365 | -63.7445 | -109.329 | -143.3795
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | Steady Progression | Headroom (MW) | Thermal | 4.1552 | 3.9182 | 3.4784 | 3.2821 | 3.077 | 2.8952 | 2.7117 | 2.5577 | 2.347 | 2.2002 | 1.9343 | 1.7934 | 1.6546 | 1.6132 | 1.6027 | 1.5808 | 3.0212 | -8.5443 | -13.488
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | System Transformation | Headroom (MW) | Thermal | 4.1601 | 3.8872 | 3.4183 | 3.0881 | 2.6794 | 2.226 | 1.5316 | 0.94767 | 0.19867 | -0.3995 | -1.0201 | -1.5329 | -1.9915 | 18.2074 | 16.1799 | 15.9769 | -0.59254 | -19.5333 | -49.7897
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | 52.8263 | -1.0702 | WPD Best View | Headroom (MW) | Thermal | 4.1316 | 3.847 | 3.325 | 2.8993 | 2.2949 | 1.5024 | 0.36985 | -0.74987 | -2.0858 | -3.2604 | -6.3867 | -8.4459 | -10.4685 | 6.8428 | 1.7712 | -6.9139 | -28.9544 | -62.346 | -102.2819
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Consumer Transformation | Headroom (MW) | N/A | 14.6287 | 14.597 | 14.5022 | 14.3552 | 14.195 | 13.9682 | 13.6675 | 13.3783 | 13.1186 | 12.9622 | 12.7302 | 12.5189 | 12.2779 | 12.0528 | 11.8633 | 11.6412 | 8.1745 | 5.3524 | 1.6173
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Leading the Way | Headroom (MW) | N/A | 14.6704 | 14.6897 | 14.6666 | 14.5711 | 14.4766 | 14.3411 | 14.157 | 13.9624 | 13.8154 | 13.852 | 13.8768 | 13.9201 | 13.9182 | 13.9145 | 12.2079 | 10.4457 | 7.653 | 4.2058 | 0.59909
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | Steady Progression | Headroom (MW) | N/A | 14.6343 | 14.6154 | 14.5709 | 14.5232 | 14.486 | 14.4617 | 14.418 | 14.3743 | 14.3191 | 14.3301 | 14.3058 | 14.29 | 14.2522 | 14.219 | 14.1921 | 14.1691 | 14.2019 | 14.2492 | 12.6084
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | System Transformation | Headroom (MW) | N/A | 14.6463 | 14.6386 | 14.5872 | 14.5178 | 14.4458 | 14.3657 | 14.2297 | 14.0937 | 13.945 | 13.9023 | 13.8251 | 13.751 | 13.6515 | 13.5444 | 13.4825 | 13.4046 | 11.9034 | 10.1625 | 8.2266
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | 52.9491 | -0.9455 | WPD Best View | Headroom (MW) | N/A | 14.628 | 14.5954 | 14.4988 | 14.3497 | 14.1868 | 13.9562 | 13.6507 | 13.3555 | 13.088 | 12.9224 | 12.6798 | 12.4554 | 12.2003 | 11.9605 | 11.7571 | 11.5269 | 8.0863 | 5.3873 | 1.7204
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Consumer Transformation | Headroom (MW) | N/A | 19.0205 | 18.9131 | 18.704 | 18.5572 | 18.3998 | 18.227 | 18.0233 | 17.8454 | 17.667 | 17.4911 | 17.2959 | 17.113 | 16.0146 | 15.8466 | 15.6934 | 15.5175 | 12.2964 | 8.9332 | 5.5867
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Leading the Way | Headroom (MW) | N/A | 19.0307 | 18.9446 | 18.7624 | 18.6433 | 18.5194 | 18.3882 | 18.2818 | 18.1845 | 18.0938 | 18.0191 | 17.929 | 17.8634 | 17.7237 | 17.5491 | 15.9808 | 15.9068 | 11.8465 | 8.861 | 6.7134
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | Steady Progression | Headroom (MW) | N/A | 19.0251 | 18.9374 | 18.7703 | 18.6718 | 18.5824 | 18.496 | 18.4016 | 18.3158 | 18.2241 | 18.1335 | 18.0387 | 17.9527 | 17.8763 | 17.8035 | 17.7387 | 17.6702 | 17.4303 | 17.1509 | 15.4464
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | System Transformation | Headroom (MW) | N/A | 19.0254 | 18.9344 | 18.7515 | 18.6423 | 18.5292 | 18.4075 | 18.2725 | 18.1447 | 18.0026 | 17.8681 | 17.7266 | 17.6067 | 17.4983 | 17.3953 | 17.3009 | 17.2062 | 15.5459 | 13.778 | 10.9743
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | 52.8435 | -1.1815 | WPD Best View | Headroom (MW) | N/A | 19.0205 | 18.9131 | 18.704 | 18.5572 | 18.3998 | 18.227 | 18.0233 | 17.8454 | 17.667 | 17.4911 | 17.2959 | 17.113 | 16.0146 | 15.8466 | 15.6934 | 15.5175 | 12.2964 | 8.9332 | 5.5867
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Consumer Transformation | Headroom (MW) | Thermal | 7.3234 | 7.277 | 7.1745 | 7.1392 | 7.0287 | 6.888 | 6.68 | 6.5011 | 6.2848 | 6.0642 | 4.8755 | 4.6041 | 4.3375 | 4.1154 | 3.8647 | 2.7154 | -0.69532 | -5.0371 | -9.7413
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Leading the Way | Headroom (MW) | Thermal | 7.3428 | 7.3185 | 7.2611 | 7.2871 | 7.2343 | 7.1677 | 7.0846 | 6.9961 | 6.8783 | 6.7503 | 6.5883 | 6.4447 | 6.3017 | 4.0083 | 3.8665 | 2.1039 | -2.003 | -6.1596 | -10.4146
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | Steady Progression | Headroom (MW) | N/A | 7.3417 | 7.3177 | 7.2636 | 7.2815 | 7.2622 | 7.2368 | 7.2193 | 7.196 | 7.1663 | 7.1429 | 7.0927 | 7.0582 | 7.0241 | 7.0291 | 7.0128 | 6.9867 | 7.0206 | 5.7759 | 5.5371
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | System Transformation | Headroom (MW) | Thermal | 7.339 | 7.3048 | 7.2437 | 7.257 | 7.2103 | 7.1515 | 7.0517 | 6.972 | 6.8673 | 6.7591 | 6.6505 | 6.5572 | 6.4584 | 6.4123 | 6.3395 | 6.2652 | 3.8396 | 2.2546 | -0.72526
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | 52.869 | -1.0799 | WPD Best View | Headroom (MW) | Thermal | 7.3234 | 7.277 | 7.1745 | 7.1392 | 7.0287 | 6.888 | 6.68 | 6.5011 | 6.2848 | 6.0642 | 4.8755 | 4.6041 | 4.3375 | 4.1154 | 3.8647 | 2.7154 | -0.69532 | -5.0371 | -9.7413
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Consumer Transformation | Headroom (MW) | Thermal | 12.7964 | 12.7585 | 12.6393 | 12.4915 | 12.3144 | 12.0555 | 11.6915 | 11.3175 | 10.9494 | 10.5571 | 10.1886 | 9.8372 | 9.5077 | 6.8756 | 6.5933 | 6.2843 | 4.6787 | 1.6085 | -1.3945
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Leading the Way | Headroom (MW) | N/A | 12.7981 | 12.7442 | 12.754 | 12.6998 | 12.6603 | 12.5185 | 12.2743 | 12.0642 | 11.7726 | 11.5064 | 11.358 | 11.2738 | 11.2045 | 8.8471 | 8.7921 | 6.993 | 5.0812 | 2.8082 | 1.6427
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | Steady Progression | Headroom (MW) | N/A | 12.7952 | 12.7544 | 12.7156 | 12.6738 | 12.641 | 12.5937 | 12.5399 | 12.4849 | 12.4166 | 12.3477 | 12.2641 | 12.1974 | 12.134 | 12.0856 | 12.0366 | 11.9902 | 12.0397 | 9.5499 | 9.0423
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | System Transformation | Headroom (MW) | N/A | 12.7963 | 12.7584 | 12.7404 | 12.6477 | 12.556 | 12.4472 | 12.2841 | 12.1246 | 11.926 | 11.7426 | 11.5609 | 11.4012 | 11.2492 | 11.1243 | 11.0169 | 10.8959 | 8.2394 | 6.462 | 4.4597
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | 52.7236 | -1.1325 | WPD Best View | Headroom (MW) | N/A | 12.7978 | 12.7634 | 12.773 | 12.7443 | 12.6697 | 12.5404 | 12.3649 | 12.1613 | 11.9429 | 11.7402 | 11.6006 | 11.4839 | 11.3541 | 8.9401 | 8.8414 | 7.0203 | 5.1664 | 2.9342 | 1.8136
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Consumer Transformation | Headroom (MW) | Thermal | 2.9962 | 2.9874 | 2.98 | 2.9757 | 2.9747 | 2.9774 | 2.9629 | 2.9539 | 2.9218 | 2.0175 | 1.9717 | 1.9209 | 0.98913 | 0.024439 | 0.089289 | -0.82492 | -6.7902 | -16.7036 | -28.9303
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Leading the Way | Headroom (MW) | Thermal | 3.007 | 2.9946 | 2.9919 | 3.005 | 3.0193 | 3.0315 | 3.054 | 3.0692 | 3.0678 | 3.0993 | 3.0853 | 2.1531 | 2.1786 | 0.94228 | -2.3627 | -5.7244 | -15.5688 | -26.2043 | -36.3086
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | Steady Progression | Headroom (MW) | N/A | 3.0031 | 2.989 | 2.9665 | 2.9653 | 2.968 | 2.9746 | 2.9931 | 3.0079 | 3.0263 | 3.0595 | 3.0684 | 3.1082 | 3.1515 | 3.2071 | 3.2652 | 3.3369 | 3.7173 | 1.489 | 1.2723
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | System Transformation | Headroom (MW) | Thermal | 3.0021 | 2.9807 | 2.9658 | 2.9647 | 2.9657 | 2.9614 | 2.9629 | 2.9659 | 2.9736 | 3.0012 | 3.0243 | 3.0711 | 3.1317 | 3.2004 | 2.3848 | 2.4889 | 0.4033 | -4.7653 | -12.5506
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | 52.6964 | -0.9989 | WPD Best View | Headroom (MW) | Thermal | 3.0039 | 2.9932 | 2.9715 | 2.969 | 2.9651 | 2.9528 | 2.9489 | 2.9158 | 2.8707 | 2.8422 | 2.7877 | 2.7577 | 2.7314 | 2.7425 | 0.15756 | 0.18726 | -2.4441 | -7.8328 | -14.0905
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Consumer Transformation | Headroom (MW) | Thermal | 12.9959 | 12.9209 | 12.7995 | 12.676 | 12.5142 | 12.27 | 11.8759 | 11.4792 | 10.9785 | 10.4637 | 9.9358 | 9.426 | 8.9245 | 8.4895 | 8.0825 | 7.6726 | 5.9859 | 2.5711 | -0.90109
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Leading the Way | Headroom (MW) | N/A | 13.0279 | 13.0064 | 12.9581 | 12.9444 | 12.8689 | 12.7605 | 12.5402 | 12.249 | 11.755 | 11.3006 | 10.9375 | 10.6907 | 10.5048 | 10.4128 | 10.3068 | 8.4765 | 6.3021 | 3.7589 | 0.96044
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | Steady Progression | Headroom (MW) | N/A | 13.0216 | 12.996 | 12.9454 | 12.9427 | 12.9397 | 12.9622 | 12.9728 | 13.0152 | 13.0305 | 13.0275 | 12.9995 | 12.9988 | 12.9957 | 12.9998 | 13.0036 | 12.9979 | 13.5973 | 13.9622 | 13.5718
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | System Transformation | Headroom (MW) | N/A | 13.0176 | 12.973 | 12.9063 | 12.8707 | 12.8109 | 12.768 | 12.6624 | 12.6138 | 12.4827 | 12.3443 | 12.2126 | 12.0894 | 11.9799 | 11.8964 | 11.8309 | 11.7688 | 11.8873 | 10.1515 | 7.9972
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | 52.7008 | -1.0613 | WPD Best View | Headroom (MW) | N/A | 13.0237 | 13.0072 | 12.9471 | 12.9148 | 12.8439 | 12.7495 | 12.5526 | 12.3197 | 11.9085 | 11.4841 | 11.1053 | 10.7844 | 10.4824 | 10.2789 | 10.0818 | 8.2136 | 6.2542 | 5.3581 | 2.8776
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Consumer Transformation | Headroom (MW) | Thermal | 5.481 | 5.4334 | 5.3696 | 5.3326 | 5.3023 | 5.2663 | 5.1923 | 5.1637 | 5.1316 | 4.2153 | 3.2419 | 3.2301 | 2.3347 | 2.3473 | 1.5298 | 0.68783 | -6.0999 | -18.1188 | -28.5067
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Leading the Way | Headroom (MW) | Thermal | 5.4873 | 5.4675 | 5.4217 | 5.4195 | 5.4328 | 5.451 | 5.4792 | 5.5493 | 5.6294 | 5.7597 | 5.8658 | 5.0532 | 5.2157 | 3.1497 | 1.646 | -4.2416 | -12.359 | -23.9052 | -33.8781
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | Steady Progression | Headroom (MW) | N/A | 5.483 | 5.457 | 5.3949 | 5.3725 | 5.3465 | 5.3188 | 5.3157 | 5.3124 | 5.3127 | 5.3076 | 5.3138 | 5.3369 | 5.3694 | 5.4177 | 5.5024 | 5.5786 | 6.1627 | 3.9761 | 3.7312
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | System Transformation | Headroom (MW) | Thermal | 5.482 | 5.446 | 5.372 | 5.3366 | 5.3101 | 5.2735 | 5.217 | 5.1816 | 5.1501 | 5.1316 | 5.1287 | 5.1392 | 5.1881 | 5.2769 | 4.4671 | 4.5901 | 1.7801 | -3.3849 | -9.9815
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | 52.8256 | -1.0713 | WPD Best View | Headroom (MW) | Thermal | 5.483 | 5.4464 | 5.405 | 5.374 | 5.3497 | 5.3373 | 5.2982 | 5.3 | 5.301 | 5.3442 | 4.4172 | 3.5043 | 3.56 | 3.6015 | 2.018 | -1.4522 | -6.9756 | -17.8974 | -26.6601
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Consumer Transformation | Headroom (MW) | Thermal | 5.4016 | 5.228 | 4.9792 | 4.6738 | 4.3379 | 3.8281 | 3.0936 | 2.3665 | 1.6491 | 0.8642 | 0.060743 | -0.76012 | -1.5786 | -2.3876 | -3.1958 | -4.0299 | -8.3804 | -12.8551 | -16.712
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Leading the Way | Headroom (MW) | Thermal | 5.453 | 5.3644 | 5.2431 | 5.1092 | 4.9531 | 4.769 | 4.4495 | 4.1391 | 3.7743 | 3.4216 | 3.0734 | 2.7341 | 2.4114 | 2.0883 | 1.7577 | 1.3962 | -0.50955 | -1.1148 | -2.7902
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | Steady Progression | Headroom (MW) | N/A | 5.4678 | 5.4097 | 5.3425 | 5.2849 | 5.2292 | 5.1751 | 5.106 | 5.026 | 4.9295 | 4.8226 | 4.4968 | 4.3752 | 4.2612 | 4.1456 | 4.0416 | 3.9427 | 3.5062 | 3.1042 | 2.4526
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | System Transformation | Headroom (MW) | Thermal | 5.4508 | 5.3589 | 5.2318 | 5.0901 | 4.9232 | 4.7255 | 4.3876 | 4.0515 | 3.6543 | 3.2617 | 2.8714 | 2.4861 | 2.1183 | 1.7615 | 1.4143 | 1.0716 | -0.47096 | -2.0067 | -3.0461
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | 53.2151 | -1.7819 | WPD Best View | Headroom (MW) | Thermal | 5.4008 | 5.2264 | 4.9758 | 4.6683 | 4.3296 | 3.8161 | 3.0768 | 2.3437 | 1.6185 | 0.82445 | -0.056162 | -0.89012 | -1.7227 | -2.5464 | -3.3685 | -4.2107 | -8.5351 | -12.8866 | -16.6755
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Consumer Transformation | Headroom (MW) | Thermal | 10.0528 | 9.8093 | 9.4788 | 9.0101 | 8.5257 | 7.7744 | 6.6778 | 5.5783 | 4.5244 | 3.3803 | 2.1894 | 0.96466 | -0.20847 | -2.306 | -3.46 | -4.6365 | -10.2434 | -18.4661 | -27.7181
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Leading the Way | Headroom (MW) | Thermal | 10.1446 | 10.0347 | 9.9214 | 9.7276 | 9.5085 | 9.2494 | 8.7954 | 8.3547 | 7.832 | 7.363 | 6.9103 | 6.5097 | 6.1336 | 5.7631 | 5.3846 | 4.9444 | 0.12396 | -2.3728 | -7.8592
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | Steady Progression | Headroom (MW) | N/A | 10.1534 | 10.0844 | 10.0062 | 9.9351 | 9.8625 | 9.7968 | 9.7228 | 9.618 | 9.4933 | 9.3345 | 8.8528 | 8.7058 | 8.5614 | 8.429 | 8.3349 | 8.2295 | 8.7273 | 8.5491 | 7.4617
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | System Transformation | Headroom (MW) | Thermal | 10.1262 | 10.0031 | 9.8602 | 9.6473 | 9.4056 | 9.1031 | 8.5959 | 8.0892 | 7.496 | 6.9088 | 6.3288 | 5.794 | 5.2815 | 4.7963 | 4.3449 | 3.9311 | 3.0524 | 0.76046 | -2.9499
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | 53.2115 | -1.8546 | WPD Best View | Headroom (MW) | Thermal | 10.1046 | 9.9495 | 9.7494 | 9.4664 | 9.1917 | 8.7728 | 8.1806 | 7.57 | 6.972 | 6.3243 | 5.4715 | 4.7733 | 4.1086 | 2.5157 | 1.8787 | 1.2398 | -1.2491 | -5.9668 | -12.2839
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Consumer Transformation | Headroom (MW) | Thermal | -17.5819 | -18.1188 | -18.9602 | -19.9367 | -20.7708 | -21.7214 | -23.2811 | -24.7206 | -26.0908 | -27.4103 | -29.9128 | -33.0154 | -35.1605 | -38.1633 | -43.1764 | -45.4645 | -88.9457 | -132.5094 | -171.8242
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Leading the Way | Headroom (MW) | Thermal | -17.4343 | -17.7159 | -18.2163 | -18.6714 | -18.9569 | -18.8547 | -19.1588 | -19.2482 | -19.3709 | -19.2493 | -13.5697 | -13.1584 | -15.1138 | -22.3775 | -30.5281 | -46.165 | -93.2396 | -143.6532 | -189.8073
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | Steady Progression | Headroom (MW) | Thermal | -17.4352 | -17.6924 | -18.1037 | -18.4058 | -18.5789 | -18.5164 | -18.5555 | -19.6321 | -19.6263 | -19.7014 | -20.5475 | -21.1134 | -21.056 | -22.1744 | -24.1479 | -26.1246 | -36.9962 | -52.7135 | -56.6931
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | System Transformation | Headroom (MW) | Thermal | -17.4715 | -17.794 | -18.3615 | -18.9242 | -19.4064 | -19.6285 | -20.278 | -20.8334 | -21.526 | -22.1109 | -22.6923 | -22.9555 | -23.1339 | -24.227 | -26.4437 | -27.6624 | -48.6656 | -67.1041 | -79.8851
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | 53.3071 | -0.9957 | WPD Best View | Headroom (MW) | Thermal | -17.584 | -18.1145 | -18.9541 | -19.8303 | -20.5581 | -21.3917 | -22.84 | -24.1679 | -25.4276 | -26.7549 | -29.2848 | -32.4127 | -34.6166 | -36.8542 | -40.0137 | -40.4219 | -67.0708 | -104.7911 | -135.2009
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Consumer Transformation | Headroom (MW) | Thermal | 5.6721 | 5.6318 | 5.5743 | 5.5112 | 5.4509 | 5.3676 | 5.2247 | 5.1132 | 4.9911 | 4.8843 | 4.7476 | 3.6992 | 3.5811 | 3.4729 | 3.3805 | 3.2685 | 0.23548 | -2.7007 | -3.4179
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Leading the Way | Headroom (MW) | Thermal | 5.6912 | 5.6825 | 5.6421 | 5.6184 | 5.6001 | 5.5739 | 5.5253 | 5.501 | 5.4655 | 5.4445 | 10.9048 | 10.8992 | 10.887 | 10.8755 | 9.1844 | 8.2415 | 5.354 | 0.23271 | -2.7077
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | Steady Progression | Headroom (MW) | N/A | 5.6691 | 5.6549 | 5.6288 | 5.6024 | 5.5917 | 5.5835 | 5.5652 | 4.5294 | 4.5107 | 4.4852 | 3.7887 | 3.1649 | 3.1438 | 3.1414 | 3.1468 | 3.1421 | 3.2319 | 3.3081 | 3.0926
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | System Transformation | Headroom (MW) | N/A | 5.6761 | 5.6594 | 5.6172 | 5.5845 | 5.5505 | 5.5071 | 5.4384 | 5.376 | 5.3001 | 5.2292 | 5.1637 | 5.1222 | 5.0739 | 5.0299 | 5.0119 | 4.9824 | 3.6537 | 2.4736 | 4.1514
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | 53.2618 | -0.9599 | WPD Best View | Headroom (MW) | Thermal | 5.6721 | 5.6318 | 5.5743 | 5.5112 | 5.4509 | 5.3676 | 5.2247 | 5.1132 | 4.9911 | 4.8843 | 4.7476 | 3.6992 | 3.5811 | 3.4729 | 3.3805 | 3.2685 | 0.23548 | -2.7007 | -3.4179
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Consumer Transformation | Headroom (MW) | N/A | 4.6681 | 4.6495 | 4.6151 | 4.5842 | 4.5647 | 4.9031 | 5.1921 | 5.5118 | 5.8317 | 6.1807 | 6.5368 | 7.0505 | 7.5742 | 8.1077 | 8.5042 | 9.9295 | 8.5965 | 6.4955 | 3.6151
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Leading the Way | Headroom (MW) | Thermal | 4.6701 | 4.6555 | 4.6267 | 4.6131 | 4.6008 | 5.0874 | 5.4914 | 5.9566 | 6.4508 | 6.9944 | 7.5757 | 8.2727 | 8.9611 | 8.4862 | 8.9684 | 8.737 | 5.3706 | 0.22802 | -3.0967
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | Steady Progression | Headroom (MW) | N/A | 4.6701 | 4.6542 | 4.6244 | 4.6083 | 4.5936 | 4.844 | 5.03 | 5.2315 | 5.4669 | 5.7168 | 5.9692 | 6.3285 | 6.7059 | 7.1033 | 7.4341 | 7.7737 | 8.7512 | 8.8341 | 9.6576
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | System Transformation | Headroom (MW) | N/A | 4.6691 | 4.6523 | 4.6202 | 4.6015 | 4.5828 | 4.928 | 5.225 | 5.5509 | 5.8874 | 6.2589 | 6.6538 | 7.22 | 7.8035 | 8.3967 | 8.8744 | 10.3877 | 10.4411 | 8.6499 | 5.9686
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | 53.307 | -0.9961 | WPD Best View | Headroom (MW) | N/A | 4.6681 | 4.6495 | 4.6151 | 4.5842 | 4.5647 | 4.9031 | 5.1921 | 5.5118 | 5.8317 | 6.1807 | 6.5368 | 7.0505 | 7.5742 | 8.1077 | 8.5042 | 9.9295 | 8.5965 | 6.4955 | 3.6151
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Consumer Transformation | Headroom (MW) | Thermal | 6.3187 | 6.184 | 5.9609 | 5.7184 | 5.6166 | 5.2385 | 4.6773 | 4.1303 | 3.6167 | 3.061 | 2.4476 | 1.862 | 1.2719 | 0.7138 | -0.76627 | -1.3648 | -5.6693 | -12.0991 | -17.3198
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Leading the Way | Headroom (MW) | Thermal | 6.3546 | 6.2955 | 6.1717 | 6.061 | 6.1523 | 6.0127 | 5.7598 | 5.5326 | 5.28 | 5.0681 | 4.8276 | 4.6413 | 4.4653 | 3.0294 | 2.8622 | 1.0131 | -4.6294 | -8.3549 | -12.7579
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | Steady Progression | Headroom (MW) | N/A | 6.3668 | 6.319 | 6.2257 | 6.1703 | 6.2307 | 6.1824 | 6.1157 | 6.0496 | 5.9728 | 5.89 | 5.78 | 5.6844 | 5.5935 | 5.5101 | 5.4319 | 5.3444 | 5.0754 | 3.6701 | 3.2931
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | System Transformation | Headroom (MW) | Thermal | 6.351 | 6.2848 | 6.1559 | 6.0348 | 6.0609 | 5.9151 | 5.6512 | 5.3927 | 5.1043 | 4.8153 | 4.5081 | 4.2192 | 3.9472 | 3.6943 | 3.4447 | 3.1768 | 0.81269 | -2.676 | -4.8949
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | 53.3353 | -0.9562 | WPD Best View | Headroom (MW) | Thermal | 6.3187 | 6.184 | 5.9609 | 5.7184 | 5.6166 | 5.2385 | 4.6773 | 4.1303 | 3.6167 | 3.061 | 2.4476 | 1.862 | 1.2719 | 0.7138 | -0.76627 | -1.3648 | -5.6693 | -12.0991 | -17.3198
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Consumer Transformation | Headroom (MW) | Thermal | 8.4438 | 8.3752 | 8.3084 | 8.1207 | 7.9431 | 7.7186 | 7.4529 | 7.1959 | 6.9332 | 6.6976 | 6.4428 | 6.201 | 5.9874 | 5.7834 | 5.5869 | 5.3691 | 1.8529 | -0.8197 | -4.5587
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Leading the Way | Headroom (MW) | Thermal | 8.4535 | 8.4274 | 8.4011 | 8.2739 | 8.1336 | 8.0091 | 7.8654 | 7.7472 | 7.6109 | 7.5002 | 7.4275 | 7.3512 | 7.2928 | 7.2547 | 5.4942 | 3.7296 | 1.7609 | -4.0967 | -7.965
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | Steady Progression | Headroom (MW) | N/A | 8.4541 | 8.4263 | 8.4101 | 8.3725 | 8.3322 | 8.3118 | 8.2988 | 8.2736 | 8.2498 | 8.1536 | 8.0339 | 7.9289 | 7.8286 | 7.749 | 7.6696 | 7.6111 | 7.5939 | 7.7887 | 6.265
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | System Transformation | Headroom (MW) | N/A | 8.4501 | 8.4173 | 8.3634 | 8.2253 | 8.0665 | 7.9181 | 7.7345 | 7.5675 | 7.3782 | 7.1925 | 7.0082 | 6.8418 | 6.7004 | 6.5575 | 6.4415 | 6.3382 | 4.7401 | 3.1639 | 1.349
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | 53.4481 | -0.9691 | WPD Best View | Headroom (MW) | Thermal | 8.4453 | 8.3876 | 8.3315 | 8.2476 | 8.1824 | 8.0837 | 7.9424 | 7.81 | 7.6765 | 7.4659 | 7.2269 | 7.0148 | 6.8044 | 6.6173 | 6.4324 | 6.2503 | 3.2457 | 1.2245 | -1.9655
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Consumer Transformation | Headroom (MW) | Thermal | 4.256 | 4.2208 | 4.1679 | 4.0133 | 3.8591 | 3.6621 | 3.4521 | 3.2558 | 3.0637 | 2.8835 | 2.6921 | 2.5113 | 2.3589 | 2.1953 | 2.0424 | 1.8862 | 0.90831 | -2.4833 | -3.7506
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Leading the Way | Headroom (MW) | Thermal | 4.262 | 4.2458 | 4.2082 | 4.08 | 3.9459 | 3.8022 | 3.6568 | 3.5228 | 3.4029 | 3.2897 | 3.1994 | 3.1318 | 2.9795 | 2.7944 | 2.6904 | 1.157 | 0.51406 | -1.6847 | -4.9632
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | Steady Progression | Headroom (MW) | N/A | 4.2617 | 4.245 | 4.2144 | 4.0971 | 3.972 | 3.8582 | 3.7543 | 3.6419 | 3.5352 | 3.4308 | 3.316 | 3.2076 | 3.1093 | 3.0112 | 2.9267 | 2.8486 | 2.5883 | 2.3767 | 1.8401
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | System Transformation | Headroom (MW) | Thermal | 4.2596 | 4.2399 | 4.1944 | 4.0646 | 3.9225 | 3.7788 | 3.6297 | 3.4768 | 3.3246 | 3.1727 | 3.0159 | 2.8799 | 2.7481 | 2.6239 | 2.5248 | 2.4175 | 2.0528 | 0.23297 | -0.51176
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | 53.4342 | -0.8439 | WPD Best View | Headroom (MW) | Thermal | 4.2545 | 4.2175 | 4.1611 | 4.0092 | 3.8573 | 3.6627 | 3.454 | 3.2627 | 3.0755 | 2.8899 | 2.6872 | 2.4906 | 2.3185 | 2.1371 | 1.9665 | 1.8044 | 0.92398 | -2.2036 | -3.3096
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Consumer Transformation | Headroom (MW) | Thermal | 4.2311 | 4.1863 | 4.1119 | 4.0397 | 3.9693 | 3.8802 | 3.7491 | 3.6349 | 3.5134 | 3.4027 | 2.3236 | 2.1881 | 2.0487 | 1.9082 | 0.87426 | 0.74809 | -5.1673 | -10.3609 | -18.3734
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Leading the Way | Headroom (MW) | Thermal | 4.2461 | 4.2126 | 4.1637 | 4.1232 | 4.0853 | 4.0563 | 4.0009 | 3.9651 | 3.9179 | 3.9056 | 3.8663 | 3.8291 | 2.5163 | 1.5473 | -0.172 | -2.7528 | -10.5325 | -18.471 | -24.8722
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | Steady Progression | Headroom (MW) | N/A | 4.2468 | 4.2217 | 4.1681 | 4.144 | 4.1209 | 4.0904 | 4.0682 | 4.0371 | 4.0185 | 3.9886 | 3.9567 | 3.9333 | 3.9149 | 3.9008 | 3.8916 | 3.8853 | 3.9071 | 2.6963 | 1.2183
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | System Transformation | Headroom (MW) | Thermal | 4.2439 | 4.2076 | 4.155 | 4.1123 | 4.0666 | 4.0197 | 3.9493 | 3.8808 | 3.7968 | 3.7293 | 3.6601 | 3.5884 | 3.5445 | 3.4999 | 3.4732 | 3.4419 | -0.12963 | -4.2027 | -9.6627
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | 53.3719 | -0.8825 | WPD Best View | Headroom (MW) | Thermal | 4.2303 | 4.1847 | 4.1085 | 4.0342 | 3.961 | 3.8682 | 3.7323 | 3.6121 | 3.4828 | 3.3629 | 2.2732 | 2.1246 | 1.9711 | 1.8158 | 0.76804 | 0.63381 | -3.7296 | -10.326 | -18.2703
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Consumer Transformation | Headroom (MW) | Thermal | 11.034 | 10.923 | 10.7481 | 10.5604 | 10.3615 | 10.0719 | 9.6677 | 9.2552 | 8.8538 | 8.4342 | 7.9896 | 7.5529 | 7.1338 | 6.7095 | 6.2989 | 5.8464 | 3.6109 | 1.3626 | -0.74147
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Leading the Way | Headroom (MW) | N/A | 11.071 | 11.0068 | 10.8972 | 10.8065 | 10.7092 | 10.609 | 10.4344 | 10.2573 | 10.064 | 9.884 | 9.7309 | 9.5899 | 9.4582 | 9.3334 | 9.1988 | 9.076 | 8.3748 | 6.3335 | 5.5667
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | Steady Progression | Headroom (MW) | N/A | 11.0697 | 11.0206 | 10.9438 | 10.8866 | 10.8381 | 10.7909 | 10.7339 | 10.6673 | 10.601 | 10.5228 | 10.4291 | 10.3563 | 10.2746 | 10.2014 | 10.1413 | 10.0684 | 9.8627 | 9.7369 | 9.4067
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | System Transformation | Headroom (MW) | N/A | 11.0665 | 11.0006 | 10.8889 | 10.7882 | 10.6788 | 10.5584 | 10.357 | 10.157 | 9.9207 | 9.6889 | 9.4591 | 9.2396 | 9.032 | 8.8376 | 8.6475 | 8.444 | 7.6377 | 6.9087 | 6.3148
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | 53.3129 | -0.9498 | WPD Best View | Headroom (MW) | Thermal | 11.034 | 10.923 | 10.7481 | 10.5604 | 10.3615 | 10.0719 | 9.6677 | 9.2552 | 8.8538 | 8.4342 | 7.9896 | 7.5529 | 7.1338 | 6.7095 | 6.2989 | 5.8464 | 3.6109 | 1.3626 | -0.74147
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Consumer Transformation | Headroom (MW) | Thermal | -0.36529 | -0.42151 | -0.52227 | -0.51345 | -0.51986 | -0.49125 | -0.53089 | -0.56606 | -0.56606 | -0.56081 | -0.59569 | -0.5707 | -1.5103 | -3.3584 | -5.328 | -7.2914 | -26.5782 | -39.9533 | -54.0924
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Leading the Way | Headroom (MW) | Thermal | -0.35634 | -0.38882 | -0.44078 | -0.34427 | -0.25715 | -0.06744 | 0.069771 | 0.2506 | 0.44551 | 0.66865 | 0.91669 | 1.1686 | 0.38213 | -2.3342 | -5.375 | -9.3265 | -29.2292 | -45.4125 | -62.5
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | Steady Progression | Headroom (MW) | Thermal | -0.34738 | -0.38098 | -0.43299 | -0.38266 | -0.33734 | -0.24212 | -0.17144 | -0.088964 | 0.0037311 | 0.1097 | 0.20196 | 0.31527 | 0.41856 | -0.7384 | -2.7409 | -4.7437 | -16.0039 | -27.9335 | -28.1143
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | System Transformation | Headroom (MW) | Thermal | -0.35936 | -0.39765 | -0.45931 | -0.41126 | -0.37483 | -0.26599 | -0.22686 | -0.14918 | -0.084122 | 0.0044565 | 0.0886 | 0.21532 | 0.32581 | -0.5301 | -2.5109 | -4.4831 | -14.2006 | -14.3197 | -15.4962
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | 53.2344 | -0.9022 | WPD Best View | Headroom (MW) | Thermal | -0.36601 | -0.42313 | -0.52566 | -0.51895 | -0.52811 | -0.50327 | -0.54769 | -0.58881 | -0.59669 | -0.60057 | -0.64608 | -0.63418 | -1.5879 | -2.6404 | -2.7226 | -2.8196 | -7.4613 | -14.6288 | -20.7096
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Consumer Transformation | Headroom (MW) | Thermal | 1.3419 | 1.3145 | 1.2576 | 1.2112 | 1.1663 | 1.1102 | 1.0163 | 0.93074 | 0.85403 | 0.78889 | 0.68521 | -0.3273 | -0.42378 | -0.51331 | -0.58682 | -0.67373 | -3.5525 | -8.7681 | -13.0785
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Leading the Way | Headroom (MW) | Thermal | 1.3559 | 1.3292 | 1.2961 | 1.2791 | 1.2554 | 1.2445 | 1.2198 | 1.2011 | 1.1739 | 1.1778 | 1.1637 | 1.1402 | 1.1261 | -0.18184 | -0.19709 | -2.8574 | -7.0405 | -12.3212 | -16.4048
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | Steady Progression | Headroom (MW) | Thermal | 1.3563 | 1.3293 | 1.2964 | 1.278 | 1.2617 | 1.247 | 1.232 | 1.2087 | 1.1975 | 1.1834 | 1.1594 | 1.1498 | 1.1372 | 1.129 | 1.1335 | 1.1278 | 1.1795 | -0.0084204 | -0.16988
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | System Transformation | Headroom (MW) | Thermal | 1.3539 | 1.3241 | 1.2851 | 1.2584 | 1.2223 | 1.1945 | 1.146 | 1.0964 | 1.0285 | 0.98013 | 0.93253 | 0.90049 | 0.87305 | 0.84571 | 0.83135 | 0.81464 | -0.49111 | -4.1526 | -6.9968
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | 53.2976 | -0.8341 | WPD Best View | Headroom (MW) | Thermal | 1.3412 | 1.3129 | 1.2542 | 1.2057 | 1.1581 | 1.0982 | 0.9995 | 0.90799 | 0.82339 | 0.74914 | 0.63482 | -0.39078 | -0.5014 | -0.60564 | -0.69303 | -0.78801 | -3.6407 | -8.7332 | -12.9754
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Consumer Transformation | Headroom (MW) | Thermal | 14.5678 | 14.4907 | 14.342 | 14.2197 | 14.09 | 13.9017 | 13.6434 | 13.3905 | 13.1254 | 12.8494 | 12.5354 | 11.3072 | 11.0245 | 10.7314 | 10.4856 | 10.2273 | 6.669 | -0.47447 | -5.4089
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Leading the Way | Headroom (MW) | Thermal | 14.5872 | 14.5367 | 14.4336 | 14.3686 | 14.2838 | 14.1978 | 14.05 | 13.9159 | 13.7467 | 13.5625 | 13.3844 | 13.2745 | 13.1517 | 11.7797 | 11.6951 | 8.1219 | 4.9422 | -1.9089 | -6.312
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | Steady Progression | Headroom (MW) | N/A | 14.5844 | 14.5374 | 14.4426 | 14.394 | 14.3393 | 14.2947 | 14.2389 | 14.1816 | 14.123 | 14.0666 | 13.9908 | 13.9364 | 13.8681 | 13.8223 | 13.7792 | 13.724 | 13.6652 | 12.3326 | 11.9815
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | System Transformation | Headroom (MW) | N/A | 14.5821 | 14.5275 | 14.4208 | 14.3475 | 14.2611 | 14.169 | 14.0307 | 13.9065 | 13.7532 | 13.6026 | 13.462 | 13.337 | 13.2197 | 13.1097 | 13.0016 | 12.9007 | 11.2834 | 6.0829 | 2.9813
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | 52.9375 | -0.6471 | WPD Best View | Headroom (MW) | Thermal | 14.5671 | 14.489 | 14.3386 | 14.2142 | 14.0818 | 13.8897 | 13.6266 | 13.3677 | 13.0947 | 12.8097 | 12.485 | 11.253 | 10.9561 | 10.6483 | 10.3887 | 10.1223 | 6.5994 | -0.41168 | -5.2687
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Consumer Transformation | Headroom (MW) | Thermal | 24.9704 | 24.7373 | 24.3656 | 24.1372 | 23.8796 | 23.5625 | 23.0158 | 22.5004 | 21.8986 | 20.3103 | 19.5261 | 18.7952 | 17.0821 | 16.2119 | 14.4859 | 13.6243 | 3.5475 | -6.648 | -19.591
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Leading the Way | Headroom (MW) | Thermal | 25.0241 | 24.8769 | 24.6321 | 24.6267 | 24.5908 | 24.6843 | 24.6539 | 24.6772 | 24.5215 | 24.3724 | 24.1714 | 23.068 | 22.7843 | 21.1365 | 19.0582 | 16.0646 | 8.3182 | -0.71765 | -8.2657
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | Steady Progression | Headroom (MW) | N/A | 25.041 | 24.9122 | 24.7191 | 24.6917 | 24.678 | 24.7384 | 24.7705 | 24.8084 | 24.7959 | 24.7556 | 24.6766 | 24.6367 | 24.5641 | 24.4622 | 24.3615 | 24.2539 | 23.833 | 22.4026 | 21.7554
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | System Transformation | Headroom (MW) | N/A | 25.0215 | 24.8685 | 24.6179 | 24.5488 | 24.4595 | 24.4578 | 24.3138 | 24.2056 | 23.9459 | 23.6854 | 23.3928 | 23.1679 | 22.8871 | 21.6207 | 21.2882 | 20.9461 | 16.8803 | 11.7444 | 6.5938
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | 52.904 | -0.6384 | WPD Best View | Headroom (MW) | Thermal | 24.9697 | 24.7357 | 24.3622 | 24.1317 | 23.8714 | 23.5504 | 22.999 | 22.4776 | 21.868 | 20.2706 | 19.485 | 18.741 | 17.0137 | 16.1381 | 14.3982 | 13.5286 | 3.4965 | -6.5573 | -18.4951
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Consumer Transformation | Headroom (MW) | Thermal | 4.4027 | 3.6873 | 2.3806 | 1.1511 | -6.4161 | -8.5829 | -11.808 | -14.9363 | -18.3126 | -22.6233 | -26.9525 | -32.8461 | -38.6323 | -26.6142 | -31.5438 | -36.7182 | -92.7409 | -150.5484 | -214.4111
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Leading the Way | Headroom (MW) | Thermal | 4.6978 | 4.4002 | 3.767 | 3.466 | 2.9822 | 2.3785 | 0.7726 | -0.39546 | -1.8344 | -3.1144 | -4.5546 | -5.8448 | -10.5652 | 1.3658 | -14.1226 | -34.8676 | -100.2643 | -170.7015 | -225.9508
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | Steady Progression | Headroom (MW) | Thermal | 4.6493 | 4.3492 | 3.7563 | 3.5295 | 3.2771 | 3.007 | 0.6337 | -2.8174 | -5.284 | -7.812 | -9.9033 | -12.1745 | -14.5439 | -16.8594 | -18.9875 | -21.1472 | -33.0912 | -53.9128 | -69.4562
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | System Transformation | Headroom (MW) | Thermal | 4.5911 | 4.2475 | 3.4534 | 2.9349 | 2.2103 | 1.3685 | -0.17018 | -1.6678 | -3.4097 | -5.0608 | -6.8252 | -8.3005 | -9.6809 | 7.8146 | 5.0959 | 2.3667 | -22.6258 | -65.3207 | -98.0438
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | 53.0506 | -0.805 | WPD Best View | Headroom (MW) | Thermal | 4.4319 | 3.7576 | 2.506 | 1.3703 | 0.049582 | -1.9687 | -5.0325 | -8.0309 | -10.9857 | -14.1385 | -17.6115 | -21.8758 | -25.9854 | -10.4647 | -14.3115 | -18.4513 | -53.0368 | -103.1036 | -149.7178
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Consumer Transformation | Headroom (MW) | Thermal | 4.5197 | 4.4663 | 4.3866 | 4.2882 | 4.2061 | 4.0719 | 3.8697 | 3.6803 | 3.5015 | 3.332 | 3.1383 | 2.979 | 2.8331 | 1.7588 | 1.6436 | 0.57953 | -1.7576 | -10.2078 | -17.8225
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Leading the Way | Headroom (MW) | Thermal | 4.5399 | 4.515 | 4.4704 | 4.4277 | 4.397 | 4.3654 | 4.3013 | 4.2448 | 4.1617 | 4.1525 | 4.1245 | 4.1678 | 4.0666 | 2.9773 | 1.3388 | -2.0316 | -10.432 | -17.6843 | -23.5515
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | Steady Progression | Headroom (MW) | N/A | 4.5382 | 4.5211 | 4.4816 | 4.4584 | 4.444 | 4.425 | 4.4052 | 4.3931 | 4.3649 | 4.3466 | 4.3288 | 4.3166 | 4.3162 | 4.318 | 4.3393 | 4.3554 | 4.591 | 3.5208 | 3.2512
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | System Transformation | Headroom (MW) | Thermal | 4.5347 | 4.5052 | 4.4539 | 4.4065 | 4.3531 | 4.2993 | 4.2079 | 4.1132 | 4.0075 | 3.9157 | 3.8022 | 3.7439 | 3.6811 | 3.644 | 3.6327 | 3.616 | 2.4046 | -2.995 | -8.6776
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | 52.9306 | -0.8147 | WPD Best View | Headroom (MW) | Thermal | 4.5395 | 4.5247 | 4.4893 | 4.4709 | 4.4632 | 4.4522 | 4.4331 | 4.4366 | 4.4192 | 4.4258 | 4.4283 | 4.4449 | 4.4771 | 4.5017 | 4.5574 | 3.6626 | 3.6961 | -0.076374 | -3.2292
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Consumer Transformation | Headroom (MW) | Thermal | 5.3444 | 5.2955 | 5.2066 | 5.1248 | 5.0573 | 4.9571 | 4.805 | 4.673 | 4.547 | 4.4279 | 4.2904 | 3.2428 | 3.1376 | 3.043 | 2.9681 | 2.8787 | -3.3391 | -5.9776 | -11.8804
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Leading the Way | Headroom (MW) | Thermal | 5.3528 | 5.325 | 5.2633 | 5.2291 | 5.1984 | 5.1707 | 5.1224 | 5.0948 | 5.0698 | 5.0601 | 5.0522 | 5.0718 | 5.0967 | 3.8463 | 1.2623 | -0.41641 | -4.5223 | -11.4739 | -18.3293
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | Steady Progression | Headroom (MW) | N/A | 5.3611 | 5.3233 | 5.2695 | 5.2319 | 5.2053 | 5.1818 | 5.1498 | 5.1183 | 5.1 | 5.0715 | 5.0362 | 5.0203 | 5.0093 | 4.9966 | 5.0016 | 5.0112 | 5.1457 | 3.9779 | 3.746
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | System Transformation | Headroom (MW) | Thermal | 5.3495 | 5.3167 | 5.2459 | 5.197 | 5.1473 | 5.0884 | 5.005 | 4.9305 | 4.8315 | 4.7465 | 4.6715 | 4.6191 | 4.5713 | 4.5464 | 4.5348 | 4.5279 | 3.2866 | -1.7365 | -4.8557
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | 53.1687 | -0.8137 | WPD Best View | Headroom (MW) | Thermal | 5.3444 | 5.2955 | 5.2066 | 5.1248 | 5.0573 | 4.9571 | 4.805 | 4.673 | 4.547 | 4.4279 | 4.2904 | 3.2428 | 3.1376 | 3.043 | 2.9681 | 2.8787 | -0.11545 | -5.9776 | -11.8804
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Consumer Transformation | Headroom (MW) | Thermal | 12.2404 | 12.1668 | 12.0321 | 11.8987 | 11.7563 | 11.5773 | 11.3202 | 11.063 | 10.8239 | 10.6024 | 10.3592 | 10.1461 | 9.0553 | 8.8776 | 8.7368 | 8.5701 | 4.1511 | -2.4016 | -7.7953
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Leading the Way | Headroom (MW) | Thermal | 12.2583 | 12.2248 | 12.1573 | 12.1001 | 12.0567 | 12.0231 | 11.9541 | 11.8931 | 11.8684 | 11.8834 | 11.9075 | 11.9794 | 12.0514 | 10.8764 | 10.9756 | 9.3472 | 3.0467 | -3.5683 | -9.9001
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | Steady Progression | Headroom (MW) | N/A | 12.2697 | 12.2266 | 12.1685 | 12.1386 | 12.1028 | 12.0769 | 12.0471 | 12.0198 | 11.9893 | 11.9515 | 11.9264 | 11.8999 | 11.9006 | 11.9041 | 11.9333 | 11.9652 | 12.372 | 11.3808 | 11.1122
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | System Transformation | Headroom (MW) | N/A | 12.2538 | 12.2097 | 12.1251 | 12.0501 | 11.9835 | 11.9023 | 11.7489 | 11.6004 | 11.4571 | 11.311 | 11.1821 | 11.0908 | 11.0112 | 10.972 | 10.958 | 10.9442 | 9.7895 | 5.607 | 1.5045
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | 53.0069 | -0.9917 | WPD Best View | Headroom (MW) | Thermal | 12.2404 | 12.1668 | 12.0321 | 11.8987 | 11.7563 | 11.5773 | 11.3202 | 11.063 | 10.8239 | 10.6024 | 10.3592 | 10.1461 | 9.0553 | 8.8776 | 8.7368 | 8.5701 | 4.1511 | -2.4016 | -7.7953
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Consumer Transformation | Headroom (MW) | N/A | 13.8624 | 13.9021 | 13.9353 | 13.9501 | 7.8122 | 7.8185 | 7.8166 | 7.8308 | 7.8278 | 7.8425 | 7.8318 | 7.8327 | 7.8305 | 7.8203 | 7.8369 | 7.8457 | 7.6227 | 6.9749 | 6.0848
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Leading the Way | Headroom (MW) | N/A | 13.9051 | 13.9614 | 14.0235 | 14.0451 | 14.0781 | 14.0844 | 13.7989 | 13.8163 | 13.7982 | 13.6847 | 13.4848 | 13.3044 | 13.1554 | 13.0123 | 12.9104 | 12.7976 | 11.8292 | 9.8194 | 9.2083
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | Steady Progression | Headroom (MW) | N/A | 13.8303 | 13.8536 | 13.8632 | 13.8737 | 13.8853 | 13.8911 | 13.8949 | 13.9016 | 13.9059 | 13.9142 | 13.9214 | 13.9311 | 13.9351 | 13.9411 | 13.9432 | 13.9409 | 13.8935 | 13.8184 | 13.5495
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | System Transformation | Headroom (MW) | N/A | 13.8623 | 13.9019 | 13.9348 | 13.9493 | 13.9627 | 13.9683 | 13.9775 | 13.99 | 14.0014 | 14.0099 | 13.9915 | 13.978 | 13.9536 | 13.9255 | 13.9013 | 13.8775 | 13.6939 | 13.3993 | 13.0304
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | 53.0423 | -0.7772 | WPD Best View | Headroom (MW) | N/A | 13.8624 | 13.9021 | 13.9353 | 13.9501 | 13.964 | 13.9703 | 13.8951 | 13.8014 | 13.6969 | 13.5665 | 13.4021 | 13.2267 | 13.0622 | 12.8858 | 12.7391 | 12.5662 | 11.6614 | 10.9066 | 10.257
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Consumer Transformation | Headroom (MW) | Thermal | 12.3082 | 12.0573 | 11.6684 | 11.3992 | 10.9619 | 10.3113 | 9.3431 | 8.4012 | 7.4544 | 6.4221 | 5.2923 | 4.1675 | 3.0507 | 1.9426 | 0.84009 | -0.34287 | -7.6819 | -14.4118 | -20.5178
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Leading the Way | Headroom (MW) | Thermal | 12.3676 | 12.2397 | 12.0178 | 12.0285 | 11.8286 | 11.5967 | 11.1704 | 10.7422 | 10.2378 | 9.7334 | 9.2048 | 8.7205 | 8.2647 | 7.7973 | 5.625 | 5.1785 | -0.044994 | -3.4833 | -6.1601
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | Steady Progression | Headroom (MW) | Thermal | 12.3818 | 12.2857 | 12.1299 | 12.1306 | 12.0533 | 11.9855 | 9.8423 | 6.6614 | 4.489 | 2.3036 | 0.59994 | -0.95393 | -1.1041 | -1.245 | -1.3792 | -1.5406 | -2.1902 | -2.461 | -4.3681
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | System Transformation | Headroom (MW) | Thermal | 12.3604 | 12.2268 | 11.9939 | 11.9434 | 11.729 | 11.4917 | 11.0643 | 10.6564 | 10.1622 | 9.6837 | 9.1701 | 8.6901 | 8.23 | 7.7735 | 7.3258 | 6.8474 | 3.406 | 0.32087 | -2.2852
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | 53.0499 | -0.8053 | WPD Best View | Headroom (MW) | Thermal | 12.3082 | 12.0573 | 11.6684 | 11.3992 | 10.9619 | 10.3113 | 9.3431 | 8.4012 | 7.4544 | 6.4221 | 5.2923 | 4.1675 | 3.0507 | 1.9426 | 0.84009 | -0.34287 | -7.6819 | -14.4118 | -20.5178
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Consumer Transformation | Headroom (MW) | Thermal | 15.5723 | 15.4388 | 15.1292 | 14.7951 | 14.4353 | 13.8465 | 13.0042 | 12.1326 | 10.9063 | 8.831 | 6.999 | 4.3172 | 1.6034 | -1.9994 | -4.0776 | -6.1616 | -27.1503 | -41.1836 | -56.3288
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Leading the Way | Headroom (MW) | Thermal | 15.6499 | 15.6639 | 15.5462 | 15.4412 | 15.3247 | 15.1301 | 14.7726 | 14.3598 | 13.8234 | 13.273 | 12.7068 | 12.1546 | 9.2329 | 6.0995 | 2.9783 | -1.1797 | -22.7587 | -39.6245 | -55.5558
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | Steady Progression | Headroom (MW) | Thermal | 14.5047 | 14.4624 | 14.4203 | 14.378 | 14.3319 | 14.2865 | 14.2273 | 14.153 | 14.0606 | 13.952 | 13.8198 | 13.6935 | 11.7731 | 9.5865 | 7.4916 | 5.3935 | -7.1912 | -19.7643 | -29.4371
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | System Transformation | Headroom (MW) | Thermal | 15.621 | 15.5864 | 15.4169 | 15.2672 | 15.1028 | 14.8903 | 14.5066 | 14.0997 | 13.6233 | 13.1536 | 12.6565 | 12.1905 | 11.7214 | 9.4768 | 7.3895 | 5.2986 | -4.7702 | -16.7925 | -17.4483
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | 53.0784 | -0.7986 | WPD Best View | Headroom (MW) | Thermal | 15.5716 | 15.4372 | 15.1259 | 14.7896 | 14.4271 | 13.8344 | 12.9874 | 12.1098 | 11.2116 | 10.2233 | 9.1368 | 8.0487 | 6.9638 | 4.9834 | 3.9559 | 2.8787 | -4.395 | -13.0484 | -21.1149
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Consumer Transformation | Headroom (MW) | Thermal | 2.8843 | 2.8533 | 2.8215 | 2.7851 | 2.7475 | 2.6888 | 2.5839 | 2.5034 | 2.4549 | 2.398 | 2.3354 | 2.3056 | 2.29 | 2.2894 | 1.3703 | 1.3591 | -0.3334 | -4.7173 | -8.3053
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Leading the Way | Headroom (MW) | Thermal | 2.8897 | 2.8852 | 2.8591 | 2.8626 | 2.8635 | 2.8595 | 2.7563 | 2.7559 | 2.7292 | 2.7352 | 2.7128 | 2.6656 | 2.6187 | 2.5682 | 1.6418 | 0.020295 | -3.5562 | -8.0225 | -11.1145
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | Steady Progression | Headroom (MW) | N/A | 2.8973 | 2.8806 | 2.8655 | 2.851 | 2.8479 | 2.8411 | 2.8436 | 2.8391 | 2.8454 | 2.8383 | 2.8517 | 2.8602 | 2.8832 | 2.9259 | 2.9589 | 3.0105 | 3.1337 | 3.1452 | 2.2093
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | System Transformation | Headroom (MW) | Thermal | 2.8869 | 2.8754 | 2.8376 | 2.8245 | 2.8023 | 2.7744 | 2.7232 | 2.6817 | 2.6416 | 2.6066 | 2.5803 | 2.5665 | 2.5804 | 2.6103 | 2.6499 | 2.707 | 1.78 | -0.88297 | -3.8517
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | 52.9994 | -0.8755 | WPD Best View | Headroom (MW) | Thermal | 2.8835 | 2.8517 | 2.8181 | 2.7796 | 2.7392 | 2.6768 | 2.5671 | 2.4806 | 2.4243 | 2.3583 | 2.285 | 2.2421 | 2.2124 | 2.1971 | 1.2641 | 1.2448 | -0.42159 | -4.6824 | -8.2022
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Consumer Transformation | Headroom (MW) | Thermal | 5.6862 | 5.5823 | 5.4363 | 5.2927 | 5.1537 | 4.9266 | 4.5714 | 4.2292 | 3.9084 | 3.5729 | 3.1888 | 2.8351 | 2.4828 | 1.2183 | 0.90104 | 0.56461 | -3.473 | -6.6684 | -11.0733
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Leading the Way | Headroom (MW) | Thermal | 5.712 | 5.6553 | 5.5689 | 5.5273 | 5.4873 | 5.4341 | 5.2859 | 5.1585 | 5.0218 | 4.9171 | 4.815 | 4.7377 | 4.649 | 4.5802 | 2.8191 | 1.0624 | -0.91297 | -6.3683 | -8.5236
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | Steady Progression | Headroom (MW) | N/A | 5.7148 | 5.6705 | 5.604 | 5.5771 | 5.5535 | 5.5323 | 5.4954 | 5.4465 | 5.3959 | 5.3394 | 5.2165 | 5.1548 | 5.1017 | 5.0571 | 5.0273 | 4.9885 | 4.943 | 3.645 | 3.4038
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | System Transformation | Headroom (MW) | Thermal | 5.709 | 5.6468 | 5.553 | 5.4892 | 5.4199 | 5.3405 | 5.1639 | 4.9888 | 4.7925 | 4.6035 | 4.3962 | 4.2261 | 4.0574 | 3.9087 | 3.7732 | 3.6372 | 1.8306 | -0.0081517 | -2.0349
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | 53.0774 | -0.9412 | WPD Best View | Headroom (MW) | Thermal | 5.6862 | 5.5823 | 5.4363 | 5.2927 | 5.1537 | 4.9266 | 4.5714 | 4.2292 | 3.9084 | 3.5729 | 3.1888 | 2.8351 | 2.4828 | 1.2183 | 0.90104 | 0.56461 | -3.473 | -6.6684 | -11.0733
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Consumer Transformation | Headroom (MW) | Thermal | 3.6767 | 3.6668 | 3.589 | 3.5195 | 3.4359 | 3.3167 | 3.1409 | 2.9742 | 2.8306 | 2.6618 | 2.474 | 2.3074 | 2.1757 | 1.1216 | 1.0144 | 0.87928 | -3.552 | -9.6227 | -17.0566
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Leading the Way | Headroom (MW) | Thermal | 3.7044 | 3.6379 | 3.6105 | 3.5789 | 3.5503 | 3.5325 | 3.4773 | 3.4393 | 3.3814 | 3.3632 | 3.3432 | 3.342 | 3.372 | 2.1217 | 0.47736 | -3.8299 | -10.4713 | -18.5151 | -24.1987
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | Steady Progression | Headroom (MW) | N/A | 3.704 | 3.7042 | 3.6708 | 3.6575 | 3.649 | 3.6258 | 3.6192 | 3.6115 | 3.5909 | 3.5677 | 3.5619 | 3.5485 | 3.5469 | 3.5598 | 3.5801 | 3.594 | 3.8523 | 1.5154 | 1.2857
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | System Transformation | Headroom (MW) | Thermal | 3.7003 | 3.6957 | 3.6598 | 3.6142 | 3.5664 | 3.5202 | 3.4319 | 3.3552 | 3.2558 | 3.1729 | 3.0759 | 3.0107 | 2.9666 | 2.9379 | 2.9266 | 2.9092 | 0.41917 | -3.6708 | -9.2482
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | 53.1675 | -0.7129 | WPD Best View | Headroom (MW) | Thermal | 3.689 | 3.6852 | 3.6252 | 3.578 | 3.5257 | 3.4468 | 3.3419 | 3.2438 | 3.1574 | 3.0559 | 2.968 | 2.8767 | 2.8193 | 2.757 | 2.716 | 2.6452 | 0.94533 | -4.4904 | -7.9344
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Consumer Transformation | Headroom (MW) | Thermal | 5.1486 | 5.0984 | 5.0161 | 4.9381 | 4.8582 | 4.743 | 4.5773 | 4.4165 | 4.2729 | 4.1265 | 3.9788 | 3.8609 | 3.749 | 3.648 | 3.557 | 3.4437 | -0.8929 | -5.998 | -13.3815
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Leading the Way | Headroom (MW) | Thermal | 5.1585 | 5.1325 | 5.0907 | 5.0659 | 5.038 | 5.0223 | 4.9739 | 4.9403 | 4.9144 | 4.9233 | 4.9342 | 4.8518 | 3.7678 | 3.8211 | 2.1832 | 0.51855 | -6.1075 | -15.4463 | -21.491
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | Steady Progression | Headroom (MW) | N/A | 5.1659 | 5.1394 | 5.0993 | 5.0822 | 5.0592 | 5.0477 | 5.0278 | 5.0079 | 4.9888 | 4.9631 | 4.9486 | 4.934 | 4.9347 | 4.937 | 4.9568 | 4.9745 | 5.1995 | 4.1494 | 2.6318
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | System Transformation | Headroom (MW) | Thermal | 5.1539 | 5.1233 | 5.0728 | 5.0339 | 4.9837 | 4.9336 | 4.8412 | 4.7567 | 4.6578 | 4.5762 | 4.4889 | 4.4243 | 4.3866 | 4.354 | 4.3386 | 4.3362 | 1.8684 | -2.2275 | -7.8427
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | 52.9954 | -0.7385 | WPD Best View | Headroom (MW) | Thermal | 5.1471 | 5.0952 | 5.0093 | 4.9271 | 4.8417 | 4.7189 | 4.5437 | 4.371 | 4.2116 | 4.047 | 3.878 | 3.7339 | 3.5937 | 3.4633 | 3.3445 | 3.2151 | -1.0693 | -5.9188 | -11.893
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Consumer Transformation | Headroom (MW) | Thermal | 34.8672 | 34.811 | 31.0362 | 30.3101 | 29.4474 | 28.6705 | 27.4224 | 26.2026 | 25.0065 | 21.9132 | 20.5437 | 19.2783 | 18.0616 | 16.8539 | 15.6694 | 14.3452 | 3.805 | -6.1011 | -17.363
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Leading the Way | Headroom (MW) | N/A | 34.9638 | 35.2542 | 31.7377 | 31.3996 | 30.9039 | 30.9132 | 30.6917 | 30.4632 | 30.1821 | 28.1439 | 27.9884 | 27.8718 | 27.7467 | 19.0987 | 17.2916 | 15.3434 | 11.0552 | 13.4489 | 5.5438
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | Steady Progression | Headroom (MW) | Thermal | 34.9859 | 24.7975 | 15.214 | 15.0311 | -5.6731 | -5.6141 | -6.6561 | -7.7236 | -8.7774 | -9.8405 | -10.9044 | -11.8856 | -12.9925 | -14.0718 | -14.5396 | -14.5814 | -8.3371 | -10.0722 | -11.9935
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | System Transformation | Headroom (MW) | N/A | 34.9497 | 35.0696 | 31.5242 | 31.2095 | 30.7478 | 30.5872 | 30.0942 | 29.6199 | 29.0325 | 28.4969 | 27.9162 | 27.4535 | 27.0417 | 26.632 | 24.4449 | 24.0573 | 20.1319 | 16.3577 | 12.2045
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | 53.3062 | -1.1009 | WPD Best View | Headroom (MW) | Thermal | 34.8672 | 34.811 | 31.0362 | 30.3101 | 29.4474 | 28.6705 | 27.4224 | 26.2026 | 25.0065 | 21.9132 | 20.5437 | 19.2783 | 18.0616 | 16.8539 | 15.6694 | 14.3452 | 3.805 | -6.1011 | -17.363
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Consumer Transformation | Headroom (MW) | Thermal | 11.1402 | 11.1746 | 10.8213 | 10.453 | 10.0518 | 9.4979 | 8.7131 | 7.9229 | 7.1577 | 6.32 | 5.4093 | 4.5464 | 3.6925 | 2.8387 | 1.985 | 1.0373 | -3.8502 | -8.672 | -13.1674
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Leading the Way | Headroom (MW) | N/A | 11.1935 | 11.4262 | 11.222 | 11.0561 | 10.855 | 10.6615 | 10.3617 | 10.0354 | 9.6698 | 9.3211 | 8.9465 | 8.6209 | 8.2958 | 7.9735 | 7.6387 | 7.265 | 5.455 | 7.6814 | 5.0046
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | Steady Progression | Headroom (MW) | N/A | 11.2106 | 11.2859 | 11.1207 | 11.0086 | 10.9112 | 10.8198 | 10.7146 | 10.5851 | 10.4444 | 10.2879 | 9.8948 | 9.5511 | 9.3941 | 9.2455 | 9.1082 | 8.9435 | 8.2347 | 7.7255 | 7.0548
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | System Transformation | Headroom (MW) | N/A | 11.1899 | 11.3082 | 11.0891 | 10.8929 | 10.6548 | 10.4345 | 10.0514 | 9.6626 | 9.2061 | 8.7515 | 8.2604 | 7.817 | 7.3934 | 6.9822 | 6.575 | 6.1266 | 4.1689 | 2.4414 | 1.0375
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | 53.3085 | -1.1111 | WPD Best View | Headroom (MW) | Thermal | 11.1402 | 11.1746 | 10.8213 | 10.453 | 10.0518 | 9.4979 | 8.7131 | 7.9229 | 7.1577 | 6.32 | 5.4093 | 4.5464 | 3.6925 | 2.8387 | 1.985 | 1.0373 | -3.8502 | -8.672 | -13.1674
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Consumer Transformation | Headroom (MW) | Thermal | 11.0499 | 10.9072 | 10.6973 | 10.3826 | 10.0456 | 9.9687 | 9.7051 | 9.4666 | 9.2207 | 7.1633 | 6.9283 | 6.7305 | 6.5685 | 6.4143 | 6.2733 | 6.1202 | 1.6164 | -2.2199 | -7.7766
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Leading the Way | Headroom (MW) | Thermal | 11.0776 | 11.0035 | 10.8734 | 10.6685 | 10.4421 | 10.7081 | 10.8553 | 11.0447 | 11.2192 | 9.6173 | 9.9233 | 10.202 | 10.4694 | 10.7402 | 9.3077 | 7.8168 | 4.9682 | 0.191 | -4.1241
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | Steady Progression | Headroom (MW) | N/A | 11.0869 | 11.0282 | 10.9228 | 10.8536 | 10.7944 | 10.9847 | 11.1211 | 11.2524 | 11.4159 | 11.5842 | 11.7414 | 11.8541 | 11.9732 | 12.1117 | 12.26 | 12.4279 | 10.751 | 10.3813 | 9.1194
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | System Transformation | Headroom (MW) | N/A | 11.0749 | 10.9932 | 10.8513 | 10.7328 | 10.5924 | 10.7261 | 10.7245 | 10.7466 | 10.7493 | 10.7942 | 10.8348 | 10.9298 | 11.0485 | 11.1585 | 9.4718 | 9.6352 | 8.0744 | 6.0327 | 4.195
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | 53.2945 | -1.0958 | WPD Best View | Headroom (MW) | Thermal | 11.0499 | 10.9072 | 10.6973 | 10.3826 | 10.0456 | 9.9687 | 9.7051 | 9.4666 | 9.2207 | 7.1633 | 6.9283 | 6.7305 | 6.5685 | 6.4143 | 6.2733 | 6.1202 | 1.6164 | -2.2199 | -7.7766
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Consumer Transformation | Headroom (MW) | Thermal | 7.5521 | 7.6042 | 4.3926 | 4.3496 | 4.225 | 4.079 | 3.8792 | 3.6881 | 3.503 | 3.3048 | 3.0812 | 2.8764 | 2.6756 | 2.4759 | 2.286 | 2.0627 | 0.91373 | -0.33418 | -1.5441
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Leading the Way | Headroom (MW) | N/A | 7.5677 | 7.6995 | 4.5173 | 4.5499 | 4.4819 | 4.4186 | 4.3497 | 4.2582 | 4.1681 | 4.0805 | 3.9936 | 3.924 | 3.8566 | 3.7468 | 3.7071 | 3.619 | 3.1076 | 8.6075 | 8.0252
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | Steady Progression | Headroom (MW) | Thermal | 7.5634 | 7.6114 | -1.7015 | -1.7031 | -1.7448 | -1.7846 | -2.8577 | -3.9271 | -5.0036 | -6.0786 | -6.9065 | -7.6568 | -8.7258 | -9.795 | -10.2739 | -10.3188 | -12.0209 | -14.1966 | -14.4726
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | System Transformation | Headroom (MW) | N/A | 7.5599 | 7.6431 | 4.4588 | 4.4589 | 4.3756 | 4.3016 | 4.1932 | 4.0857 | 3.9521 | 3.8262 | 3.6961 | 3.5817 | 3.4748 | 3.3662 | 3.2731 | 3.1705 | 2.7452 | 2.2431 | 1.7458
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | 53.3144 | -1.1383 | WPD Best View | Headroom (MW) | Thermal | 7.5521 | 7.6042 | 4.3926 | 4.3496 | 4.225 | 4.079 | 3.8792 | 3.6881 | 3.503 | 3.3048 | 3.0812 | 2.8764 | 2.6756 | 2.4759 | 2.286 | 2.0627 | 0.91373 | -0.33418 | -1.5441
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Consumer Transformation | Headroom (MW) | Thermal | 39.8741 | 39.4644 | 38.7134 | 38.1583 | 37.5326 | 36.0766 | 33.1805 | 31.1463 | 28.7651 | 26.6471 | 23.8478 | 20.7937 | 17.7616 | 13.8101 | 10.7428 | 6.6691 | -3.0028 | -20.5228 | -35.7335
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Leading the Way | Headroom (MW) | N/A | 39.9148 | 39.461 | 38.7895 | 37.9443 | 37.8532 | 37.455 | 34.0574 | 32.6201 | 30.6523 | 28.9067 | 29.0911 | 27.0213 | 24.5465 | 21.8364 | 20.552 | 17.8327 | 8.2759 | 20.0071 | 7.365
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | Steady Progression | Headroom (MW) | Thermal | 40.9151 | 40.5013 | 39.8488 | 39.4785 | 39.2932 | 38.9612 | 34.6719 | 31.2682 | 27.3704 | 23.9455 | 20.6476 | 17.1044 | 12.9033 | 8.7371 | 5.8613 | 5.5039 | 0.27382 | -9.603 | -13.6773
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | System Transformation | Headroom (MW) | N/A | 40.9141 | 40.8038 | 40.1236 | 39.7277 | 39.54 | 39.1389 | 37.5837 | 36.7136 | 35.0027 | 33.7987 | 32.0516 | 30.3257 | 28.6724 | 27.0581 | 25.0878 | 24.1097 | 23.4486 | 16.4656 | 12.5244
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | 52.9655 | -1.1023 | WPD Best View | Headroom (MW) | Thermal | 40.9129 | 40.8287 | 40.0792 | 39.5708 | 39.0552 | 37.9939 | 36.5799 | 35.1477 | 33.4952 | 31.8096 | 29.9571 | 28.1956 | 26.5431 | 23.9542 | 22.3328 | 18.7084 | 13.5424 | -0.56438 | -11.4072
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Consumer Transformation | Headroom (MW) | Thermal | 1.7135 | 1.6599 | 1.5483 | 1.4273 | 1.0275 | 0.45355 | -0.36344 | -1.14 | -1.9064 | -2.7349 | -3.6083 | -4.4394 | -5.2306 | -6.0456 | -6.8299 | -9.5218 | -14.8997 | -17.8795 | -20.4643
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Leading the Way | Headroom (MW) | Thermal | 1.7155 | 1.6377 | 1.53 | 1.4394 | 1.3862 | 1.335 | 0.76458 | 0.72062 | 0.30738 | -0.054809 | 1.7902 | 0.85791 | -0.5727 | -2.0703 | -3.1053 | -3.8745 | -11.3052 | -10.0717 | -16.1347
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | Steady Progression | Headroom (MW) | Thermal | 1.712 | 1.6561 | 1.5417 | 1.4777 | 1.4182 | 1.3599 | -1.8033 | -4.9325 | -8.0764 | -11.2099 | -13.8271 | -16.2818 | -19.5002 | -22.7043 | -24.2964 | -24.4149 | -29.5503 | -37.1958 | -37.9581
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | System Transformation | Headroom (MW) | Thermal | 1.7134 | 1.6598 | 1.548 | 1.4913 | 1.434 | 1.3748 | 0.97483 | 0.58319 | 0.11549 | -0.32452 | -0.78624 | -1.1937 | -1.5616 | -1.9278 | -2.2454 | -2.602 | -4.8973 | -6.2877 | -6.0256
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | 52.9604 | -1.0802 | WPD Best View | Headroom (MW) | Thermal | 1.7135 | 1.66 | 1.5484 | 1.4708 | 1.0918 | 0.55058 | -0.23131 | -0.96329 | -1.6994 | -2.4812 | -3.3118 | -4.1065 | -4.8584 | -5.6249 | -6.3665 | -9.0303 | -12.7489 | -16.9841 | -19.4114
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Consumer Transformation | Headroom (MW) | Thermal | 9.8044 | 9.6786 | 9.4629 | 9.2572 | 9.0375 | 8.7269 | 8.2835 | 7.8858 | 7.4826 | 7.0507 | 6.5793 | 6.1218 | 5.6899 | 4.3431 | 3.9467 | 3.5285 | 1.3356 | -3.3183 | -6.6268
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Leading the Way | Headroom (MW) | Thermal | 9.8295 | 9.767 | 9.6251 | 9.5206 | 9.3997 | 9.2623 | 9.025 | 8.8658 | 8.6458 | 8.4573 | 8.2791 | 8.1507 | 8.0306 | 7.9349 | 7.8352 | 6.0395 | 4.1752 | 1.7191 | -0.51395
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | Steady Progression | Headroom (MW) | N/A | 9.8315 | 9.7666 | 9.6533 | 9.5837 | 9.5146 | 9.4558 | 9.3817 | 9.3083 | 9.2271 | 9.1339 | 9.0305 | 8.9328 | 8.8507 | 8.779 | 8.7085 | 8.6533 | 8.6397 | 8.5989 | 8.0923
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | System Transformation | Headroom (MW) | N/A | 9.8191 | 9.7509 | 9.6063 | 9.4953 | 9.3717 | 9.2328 | 9.0035 | 8.8047 | 8.5483 | 8.3086 | 8.0444 | 7.8306 | 7.6218 | 7.4389 | 7.2606 | 7.1087 | 6.5653 | 4.5051 | 3.6744
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | 52.985 | -1.0908 | WPD Best View | Headroom (MW) | Thermal | 9.8044 | 9.6785 | 9.4626 | 9.2573 | 9.0378 | 8.7274 | 8.2844 | 7.8879 | 7.4865 | 7.0577 | 6.5902 | 6.1369 | 5.7092 | 4.3665 | 3.973 | 3.5526 | 1.3261 | -3.368 | -6.7214
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Consumer Transformation | Headroom (MW) | Fault level | 14.2193 | 14.0885 | 13.913 | 13.6871 | 13.4233 | 13.018 | 12.4169 | 11.8155 | 11.2158 | 10.5581 | 9.8283 | 9.1001 | 8.3855 | 7.6493 | 6.9074 | 6.0745 | 1.9398 | -1.9174 | -5.4331
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Leading the Way | Headroom (MW) | N/A | 14.1665 | 14.1088 | 14.038 | 13.9567 | 13.8467 | 13.7152 | 13.4788 | 13.2422 | 12.9438 | 12.6291 | 12.256 | 11.8774 | 11.4827 | 11.0759 | 10.6595 | 10.2298 | 8.429 | 6.9053 | 5.4913
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | Steady Progression | Headroom (MW) | N/A | 11.809 | 11.7757 | 11.7438 | 11.7133 | 11.6815 | 11.6558 | 11.6048 | 11.5578 | 11.4911 | 11.4159 | 11.3126 | 11.2217 | 11.1314 | 11.0415 | 10.9524 | 10.8531 | 10.286 | 9.7977 | 9.213
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | System Transformation | Headroom (MW) | N/A | 13.7672 | 13.7066 | 13.6274 | 13.5299 | 13.4085 | 13.2651 | 13.0089 | 12.7518 | 12.4376 | 12.1289 | 11.7824 | 11.4588 | 11.1355 | 10.808 | 10.4759 | 10.1097 | 8.4115 | 7.0247 | 6.0217
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | 52.9703 | -1.1309 | WPD Best View | Headroom (MW) | N/A | 13.5431 | 13.4851 | 13.3964 | 13.3 | 13.1619 | 12.9979 | 12.7262 | 12.447 | 12.1238 | 11.778 | 11.3796 | 10.9872 | 10.5864 | 10.1735 | 9.7576 | 9.3098 | 7.29 | 5.5473 | 3.9394
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Consumer Transformation | Headroom (MW) | N/A | 31.4987 | 31.3527 | 31.1506 | 30.899 | 30.6265 | 30.2134 | 29.5967 | 28.9668 | 28.3575 | 27.6872 | 26.965 | 26.2297 | 25.491 | 24.7456 | 24.0086 | 23.2184 | 19.3226 | 15.7064 | 12.4643
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Leading the Way | Headroom (MW) | N/A | 31.3183 | 31.2299 | 31.1251 | 30.9985 | 30.8592 | 30.7033 | 30.4199 | 30.1219 | 29.796 | 29.4552 | 29.098 | 28.7368 | 28.3683 | 28.0005 | 27.6199 | 27.2259 | 25.5034 | 23.6626 | 21.5081
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | Steady Progression | Headroom (MW) | N/A | 26.0968 | 26.0557 | 26.0166 | 25.9829 | 25.9459 | 25.9102 | 25.8621 | 25.8051 | 25.7416 | 25.6627 | 25.566 | 25.473 | 25.379 | 25.2892 | 25.1914 | 25.0822 | 24.5568 | 24.1287 | 23.6969
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | System Transformation | Headroom (MW) | N/A | 30.4414 | 30.3695 | 30.2818 | 30.1803 | 30.0568 | 29.915 | 29.6616 | 29.4078 | 29.1178 | 28.8197 | 28.5061 | 28.1913 | 27.8739 | 27.562 | 27.2421 | 26.8944 | 25.3267 | 24.0801 | 23.2069
Stoke Bardolph 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | 52.957 | -1.1433 | WPD Best View | Headroom (MW) | N/A | 29.9668 | 29.8822 | 29.7819 | 29.6608 | 29.5275 | 29.3783 | 29.1072 | 28.822 | 28.5102 | 28.1841 | 27.8423 | 27.4967 | 27.1441 | 26.7922 | 26.4281 | 26.051 | 24.4029 | 23.1316 | 22.1135
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Consumer Transformation | Headroom (MW) | Fault level | 13.3874 | 13.2859 | 13.1353 | 12.9621 | 12.7688 | 12.4413 | 11.955 | 11.5016 | 11.0629 | 10.5746 | 10.0549 | 9.5413 | 9.0322 | 8.5133 | 7.9782 | 7.3609 | 4.1194 | 1.0327 | -1.7209
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Leading the Way | Headroom (MW) | N/A | 13.3328 | 12.9367 | 12.8909 | 12.8274 | 12.7586 | 12.6569 | 12.5011 | 12.3586 | 12.1923 | 12.0153 | 11.8041 | 11.5726 | 11.3152 | 11.0413 | 10.7391 | 10.4258 | 9.2126 | 8.0635 | 6.9992
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | Steady Progression | Headroom (MW) | N/A | 11.1131 | 7.496 | 7.4715 | 7.4491 | 7.4276 | 7.4081 | 7.3748 | 7.3393 | 7.2928 | 7.2412 | 6.8866 | 6.5763 | 6.5171 | 6.4605 | 6.401 | 6.3338 | 5.9711 | 5.5843 | 5.1488
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | System Transformation | Headroom (MW) | N/A | 12.9575 | 12.9115 | 12.8504 | 12.7693 | 12.6801 | 12.5713 | 12.365 | 12.1666 | 11.9215 | 11.6768 | 11.4112 | 11.164 | 10.9217 | 10.6866 | 10.4416 | 10.1543 | 8.846 | 7.8661 | 7.1014
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | 52.979 | -1.1734 | WPD Best View | Headroom (MW) | N/A | 12.7575 | 12.3785 | 12.3347 | 12.2738 | 12.208 | 12.1107 | 11.9617 | 11.8253 | 11.6662 | 11.4968 | 11.2947 | 11.0732 | 10.8269 | 10.5648 | 10.2756 | 9.9759 | 8.815 | 7.7155 | 6.6972
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Consumer Transformation | Headroom (MW) | N/A | 78.1862 | 77.6316 | 76.5193 | 75.3192 | 74.0935 | 72.3288 | 69.7724 | 67.3128 | 64.8529 | 62.25 | 59.416 | 56.8061 | 54.2941 | 51.8696 | 49.3831 | 46.5014 | 31.2936 | 13.957 | 0.56086
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Leading the Way | Headroom (MW) | N/A | 78.3165 | 77.9107 | 77.275 | 76.6441 | 76.3001 | 75.7902 | 74.061 | 73.4117 | 72.1023 | 71.2918 | 69.9112 | 68.7291 | 67.5957 | 66.453 | 65.8394 | 64.9998 | 59.3722 | 54.3813 | 44.9547
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | Steady Progression | Headroom (MW) | N/A | 78.3015 | 77.9479 | 77.3491 | 76.9412 | 76.609 | 76.2892 | 75.7458 | 75.3968 | 74.8355 | 74.3745 | 73.6547 | 72.9647 | 72.3198 | 71.7693 | 71.4518 | 71.0938 | 69.8466 | 68.8672 | 65.5164
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | System Transformation | Headroom (MW) | N/A | 78.2889 | 77.9658 | 77.1581 | 76.5709 | 75.9456 | 75.1866 | 73.8914 | 72.6928 | 71.2238 | 69.8208 | 68.3053 | 67.0296 | 65.8644 | 64.8087 | 63.8294 | 62.6624 | 58.178 | 52.8992 | 49.7536
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | 52.9784 | -1.1742 | WPD Best View | Headroom (MW) | N/A | 78.2792 | 77.9776 | 77.1511 | 76.3525 | 75.5429 | 74.5304 | 72.938 | 71.4141 | 69.7571 | 68.1295 | 66.3334 | 64.7384 | 63.2373 | 61.8217 | 60.3316 | 58.5727 | 49.4512 | 38.1373 | 29.9016
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Consumer Transformation | Headroom (MW) | Thermal | 14.163 | 14.1128 | 13.9998 | 13.7129 | 13.414 | 13.0054 | 12.4322 | 11.9351 | 11.3888 | 10.8007 | 10.1607 | 9.5515 | 8.9711 | 8.3804 | 7.7924 | 7.1314 | 3.7266 | -0.70818 | -1.6178
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Leading the Way | Headroom (MW) | N/A | 14.1657 | 14.0857 | 13.9817 | 13.8826 | 13.8261 | 13.7268 | 13.4137 | 13.3161 | 13.0376 | 12.7676 | 12.4784 | 12.2376 | 11.9902 | 11.7375 | 11.4903 | 11.1926 | 9.6803 | 10.4602 | 7.7217
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | Steady Progression | Headroom (MW) | N/A | 14.1611 | 14.1082 | 13.9976 | 13.9328 | 13.8728 | 13.8119 | 13.7184 | 13.6818 | 13.6132 | 13.4951 | 13.3282 | 13.1922 | 13.058 | 12.9385 | 12.8304 | 12.7023 | 12.2518 | 11.9542 | 11.1505
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | System Transformation | Headroom (MW) | N/A | 14.163 | 14.1127 | 14.005 | 13.9476 | 13.8466 | 13.6522 | 13.3476 | 13.1264 | 12.7772 | 12.4434 | 12.0936 | 11.7906 | 11.5008 | 11.2174 | 10.9595 | 10.6678 | 9.4576 | 8.1889 | 9.4147
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | 53.0077 | -1.1241 | WPD Best View | Headroom (MW) | Thermal | 14.1634 | 14.1133 | 14.0059 | 13.7626 | 13.4926 | 13.1138 | 12.5893 | 12.147 | 11.6359 | 11.0943 | 10.5013 | 9.9219 | 9.3612 | 8.8023 | 8.2352 | 7.6078 | 4.4467 | 0.25585 | -0.46582
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Consumer Transformation | Headroom (MW) | N/A | 14.766 | 14.684 | 14.5378 | 14.4178 | 14.296 | 14.1412 | 13.9284 | 13.7233 | 13.5403 | 13.3383 | 13.1308 | 12.9534 | 12.8067 | 12.652 | 12.4772 | 12.2579 | 10.8586 | 9.139 | 7.4419
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Leading the Way | Headroom (MW) | N/A | 14.782 | 14.7347 | 14.6353 | 14.578 | 14.5164 | 14.4785 | 14.4254 | 14.3709 | 14.3421 | 14.3159 | 14.2712 | 14.2431 | 14.2118 | 14.1693 | 14.1301 | 14.0282 | 13.4471 | 12.4616 | 11.293
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | Steady Progression | Headroom (MW) | N/A | 14.7766 | 14.7287 | 14.6225 | 14.5715 | 14.5186 | 14.4744 | 14.418 | 14.3616 | 14.3113 | 14.258 | 14.1856 | 14.1351 | 14.0983 | 14.0643 | 14.048 | 14.0216 | 13.9817 | 13.9137 | 13.4557
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | System Transformation | Headroom (MW) | N/A | 14.7753 | 14.7163 | 14.6011 | 14.5274 | 14.4481 | 14.3692 | 14.2424 | 14.1169 | 13.9896 | 13.8635 | 13.7215 | 13.6085 | 13.5187 | 13.4414 | 13.3896 | 13.2919 | 12.9863 | 12.4891 | 11.7722
Stoke Bardolph 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | 52.9619 | -1.2133 | WPD Best View | Headroom (MW) | N/A | 14.7816 | 14.7334 | 14.6329 | 14.5728 | 14.5009 | 14.4593 | 14.4065 | 14.3374 | 14.3001 | 14.2562 | 14.2017 | 14.1572 | 14.1238 | 14.0866 | 14.0347 | 13.9495 | 13.3972 | 12.4613 | 11.3746
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Consumer Transformation | Headroom (MW) | N/A | 24.6414 | 24.5395 | 24.2035 | 23.8952 | 23.6254 | 23.2131 | 22.5571 | 21.9074 | 21.2602 | 20.5968 | 19.8778 | 19.2345 | 18.6056 | 18.0527 | 17.4556 | 16.7596 | 13.0567 | 8.874 | 4.7659
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Leading the Way | Headroom (MW) | N/A | 24.6714 | 24.5525 | 24.4364 | 24.1824 | 24.2055 | 24.0898 | 23.1984 | 23.1457 | 22.6597 | 22.624 | 22.0773 | 21.5976 | 21.1437 | 20.6618 | 20.7226 | 20.7855 | 19.8437 | 18.0487 | 15.8429
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | Steady Progression | Headroom (MW) | N/A | 22.6821 | 22.6551 | 22.6222 | 22.5887 | 22.5552 | 22.5194 | 22.4783 | 22.4267 | 22.3611 | 22.2925 | 22.1937 | 22.1093 | 22.0237 | 21.9368 | 21.8484 | 21.7434 | 21.2134 | 20.7562 | 20.2178
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | System Transformation | Headroom (MW) | N/A | 24.6667 | 24.6409 | 24.4115 | 24.2362 | 24.0974 | 23.9643 | 23.6611 | 23.3588 | 23.0029 | 22.6735 | 22.3096 | 22.0408 | 21.7954 | 21.6076 | 21.4024 | 21.1693 | 20.25 | 18.941 | 17.4397
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | 53.0022 | -1.1988 | WPD Best View | Headroom (MW) | N/A | 24.67 | 24.6969 | 24.4699 | 24.3039 | 24.2026 | 24.0762 | 23.7814 | 23.4711 | 23.098 | 22.795 | 22.4576 | 22.2146 | 22.0097 | 21.8565 | 21.6604 | 21.4179 | 20.0117 | 18.1459 | 16.1193
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Consumer Transformation | Headroom (MW) | Thermal | 13.0207 | 12.8653 | 12.6138 | 12.3903 | 12.1484 | 11.7707 | 11.2497 | 10.7266 | 10.2091 | 9.6727 | 9.0697 | 8.5109 | 7.9604 | 7.4332 | 6.9013 | 6.2617 | 3.0213 | -0.36739 | -3.5772
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Leading the Way | Headroom (MW) | N/A | 13.0568 | 12.9742 | 12.8061 | 12.7088 | 12.5847 | 12.4631 | 12.2517 | 12.0378 | 11.7842 | 11.5601 | 11.3163 | 11.098 | 10.9068 | 10.7373 | 10.556 | 10.3122 | 9.1017 | 7.7241 | 6.1828
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | Steady Progression | Headroom (MW) | N/A | 13.0566 | 12.9696 | 12.8319 | 12.7345 | 12.656 | 12.5767 | 12.4893 | 12.3949 | 12.2866 | 12.1765 | 12.0338 | 11.9247 | 11.8199 | 11.7263 | 11.6313 | 11.5318 | 11.2301 | 11.0941 | 10.483
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | System Transformation | Headroom (MW) | N/A | 13.05 | 12.956 | 12.767 | 12.6408 | 12.4914 | 12.3287 | 12.0789 | 11.8234 | 11.5391 | 11.2644 | 10.954 | 10.6708 | 10.4204 | 10.1846 | 9.9671 | 9.6962 | 8.7096 | 7.6711 | 6.6836
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | 52.9882 | -1.2018 | WPD Best View | Headroom (MW) | N/A | 13.0485 | 12.9435 | 12.757 | 12.6287 | 12.4798 | 12.2908 | 12.0114 | 11.7282 | 11.4142 | 11.118 | 10.777 | 10.4752 | 10.1991 | 9.9408 | 9.6767 | 9.345 | 7.7797 | 6.0729 | 4.294
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Consumer Transformation | Headroom (MW) | Thermal | 14.045 | 13.8801 | 13.6144 | 13.353 | 13.0598 | 12.6484 | 12.0551 | 11.4704 | 10.9045 | 10.2916 | 9.6271 | 9.0058 | 8.4003 | 7.8014 | 7.2067 | 6.5407 | 3.0803 | -0.53039 | -4.0019
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Leading the Way | Headroom (MW) | N/A | 14.0905 | 14.0136 | 13.8655 | 13.7422 | 13.6174 | 13.482 | 13.2219 | 12.9913 | 12.7286 | 12.4741 | 12.2181 | 12.0027 | 11.7932 | 11.5971 | 11.3904 | 11.1313 | 9.7494 | 8.1367 | 6.3643
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | Steady Progression | Headroom (MW) | N/A | 14.0939 | 14.0184 | 13.8972 | 13.8131 | 13.7372 | 13.6602 | 13.5706 | 13.4651 | 13.3688 | 13.2413 | 13.1079 | 12.9933 | 12.8789 | 12.7966 | 12.7121 | 12.6168 | 12.3558 | 12.2301 | 11.5474
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | System Transformation | Headroom (MW) | N/A | 14.0838 | 13.9898 | 13.8236 | 13.669 | 13.5122 | 13.3222 | 13.0113 | 12.7174 | 12.365 | 12.0259 | 11.6767 | 11.369 | 11.0792 | 10.8078 | 10.5608 | 10.2872 | 9.2245 | 8.0591 | 6.8933
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | 52.9902 | -1.1341 | WPD Best View | Headroom (MW) | N/A | 14.0657 | 13.9404 | 13.7355 | 13.5345 | 13.3169 | 13.0403 | 12.5995 | 12.1804 | 11.7589 | 11.316 | 10.8458 | 10.4197 | 9.9935 | 9.5855 | 9.1746 | 8.7024 | 6.2659 | 3.6514 | 1.0295
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Consumer Transformation | Headroom (MW) | Thermal | -15.3438 | -15.9604 | -17.0597 | -19.7467 | -28.7881 | -32.3892 | -37.2452 | -41.6275 | -57.4802 | -63.9325 | -69.7967 | -74.6365 | -79.553 | -84.5388 | -89.947 | -94.6395 | -136.2999 | -176.5005 | -198.0745
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Leading the Way | Headroom (MW) | Thermal | -15.0644 | -15.2706 | -15.8132 | -17.8152 | -26.1589 | -28.5886 | -31.5439 | -37.0291 | -49.8692 | -52.8687 | -57.8248 | -63.2948 | -69.7935 | -77.0479 | -84.7398 | -95.4823 | -123.4563 | -143.8047 | -162.4165
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | Steady Progression | Headroom (MW) | Thermal | -15.0895 | -15.3528 | -15.8604 | -17.0942 | -27.5713 | -28.8542 | -32.6827 | -36.0854 | -39.448 | -42.6498 | -45.9547 | -51.6903 | -54.4189 | -57.2578 | -59.8846 | -62.4649 | -78.3991 | -89.2574 | -96.2053
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | System Transformation | Headroom (MW) | Thermal | -15.0962 | -15.4053 | -16.0675 | -17.9071 | -26.2321 | -28.5575 | -31.2681 | -34.0001 | -36.8082 | -41.6209 | -44.6297 | -47.5314 | -50.3454 | -59.1413 | -61.7674 | -64.5031 | -76.9329 | -83.9747 | -96.648
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | 52.9665 | -0.0142 | WPD Best View | Headroom (MW) | Thermal | -15.0327 | -15.3065 | -15.8293 | -17.2367 | -27.9965 | -29.5864 | -33.2003 | -36.9698 | -40.7433 | -44.2095 | -47.7328 | -53.6837 | -56.5782 | -59.533 | -62.3188 | -65.1033 | -81.0554 | -88.3326 | -96.0754
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Consumer Transformation | Headroom (MW) | Thermal | 6.0001 | 5.8796 | 5.7096 | 5.209 | 4.6758 | 4.032 | 3.2909 | 2.5373 | 1.7822 | 1.1111 | 0.33789 | -0.41975 | -1.1509 | -1.8832 | -2.6041 | -3.333 | -11.5496 | -13.7645 | -16.524
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Leading the Way | Headroom (MW) | Thermal | 6.0218 | 5.9716 | 5.8805 | 5.4793 | 5.056 | 4.5878 | 4.0754 | 3.5512 | 2.9931 | 2.6033 | 2.1304 | 1.6845 | 1.2636 | 0.067703 | -1.2642 | -2.5667 | -12.8843 | -21.3118 | -29.7503
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | Steady Progression | Headroom (MW) | Thermal | 6.04 | 5.9841 | 5.9116 | 5.5621 | 5.2214 | 4.8666 | 4.5462 | 4.2137 | 3.8711 | 3.556 | 3.1883 | 2.8369 | 2.4901 | 2.1528 | 1.821 | 1.5205 | 0.228 | -2.6135 | -3.0532
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | System Transformation | Headroom (MW) | Thermal | 6.0166 | 5.9598 | 5.8585 | 5.4515 | 5.0275 | 4.5753 | 4.0696 | 3.5792 | 3.0333 | 2.5636 | 2.0217 | 1.4925 | 0.98209 | 0.49068 | 0.0075944 | -0.47063 | -2.4113 | -3.5057 | -4.4174
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | 52.9155 | -0.189 | WPD Best View | Headroom (MW) | Thermal | 6.0278 | 5.966 | 5.8812 | 5.5003 | 5.1118 | 4.7017 | 4.2767 | 3.8546 | 3.3917 | 2.9987 | 2.5343 | 2.0834 | 1.642 | 1.2196 | 0.79408 | 0.39392 | -1.2857 | -1.8943 | -2.5287
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Consumer Transformation | Headroom (MW) | Thermal | 3.008 | 3.0264 | 2.986 | 2.6675 | 2.337 | 1.9491 | 1.5116 | 1.0622 | 0.59631 | 0.13709 | -0.35119 | -0.81945 | -1.2787 | -1.7234 | -2.1733 | -2.6318 | -5.4239 | -7.0623 | -7.6799
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Leading the Way | Headroom (MW) | Thermal | 3.0218 | 3.1042 | 3.1297 | 2.8711 | 2.595 | 2.3086 | 2.0028 | 1.685 | 1.327 | 0.99757 | 0.66577 | 0.39371 | 0.12194 | -0.13814 | -0.40247 | -0.66576 | -1.8699 | -2.9042 | -4.0733
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | Steady Progression | Headroom (MW) | N/A | 3.0218 | 3.0578 | 3.0518 | 3.025 | 2.9935 | 2.9753 | 2.9445 | 2.832 | 2.7067 | 2.568 | 2.4295 | 2.2159 | 2.0028 | 1.7862 | 1.5786 | 1.3879 | 1.4565 | 1.4027 | 1.1146
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | System Transformation | Headroom (MW) | Thermal | 3.0184 | 3.0654 | 3.0665 | 2.9132 | 2.654 | 2.3879 | 2.105 | 1.8129 | 1.4966 | 1.1808 | 0.84504 | 0.52751 | 0.22744 | -0.081541 | -0.37775 | -0.67574 | -1.3164 | -1.8538 | -1.3783
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | 52.9216 | -0.0575 | WPD Best View | Headroom (MW) | N/A | 3.0218 | 3.0581 | 3.0521 | 3.0258 | 2.8996 | 2.7859 | 2.6684 | 2.4683 | 2.2552 | 2.0291 | 1.8028 | 1.5836 | 1.369 | 1.1471 | 0.93845 | 0.74225 | 0.61483 | 0.51073 | 0.18518
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Consumer Transformation | Headroom (MW) | Thermal | 1.647 | 1.6143 | 1.5564 | 1.1751 | 0.77501 | 0.34863 | -0.076371 | -0.51896 | -0.9757 | -3.977 | -4.4031 | -4.8263 | -5.2403 | -5.6663 | -6.0847 | -6.4912 | -8.6578 | -10.7811 | -13.5173
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Leading the Way | Headroom (MW) | Thermal | 1.6526 | 1.6385 | 1.6072 | 1.2587 | 0.90698 | 0.5299 | 0.1737 | -2.7741 | -3.1579 | -3.5244 | -3.8725 | -4.213 | -4.5553 | -4.8978 | -5.2315 | -5.5665 | -7.4003 | -9.7667 | -11.6683
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | Steady Progression | Headroom (MW) | Thermal | 1.6606 | 1.6355 | 1.6055 | 1.2855 | 0.9565 | 0.63632 | 0.34325 | 0.047287 | -0.24935 | -0.55914 | -0.8602 | -3.7229 | -4.0141 | -4.3133 | -4.5948 | -4.8495 | -5.9533 | -6.2888 | -6.84
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | System Transformation | Headroom (MW) | Thermal | 1.6502 | 1.6306 | 1.5868 | 1.2385 | 0.88226 | 0.51723 | 0.15466 | -0.2168 | -0.58572 | -3.5296 | -3.8913 | -4.2623 | -4.616 | -4.9749 | -5.3071 | -5.6271 | -6.9197 | -7.7932 | -8.9544
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | 53.0121 | -0.1246 | WPD Best View | Headroom (MW) | Thermal | 1.6601 | 1.6336 | 1.6012 | 1.2654 | 0.92659 | 0.58603 | 0.27538 | -0.055807 | -0.37859 | -0.71348 | -1.0393 | -3.9273 | -4.2386 | -4.562 | -4.8609 | -5.1413 | -6.3038 | -6.8034 | -7.7309
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Consumer Transformation | Headroom (MW) | Thermal | -2.6387 | -2.7664 | -2.8905 | -3.1482 | -9.5864 | -10.0468 | -10.626 | -11.2187 | -11.659 | -11.9631 | -12.6486 | -13.3655 | -14.0666 | -14.7261 | -15.3707 | -16.0709 | -19.4865 | -20.9842 | -23.5613
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Leading the Way | Headroom (MW) | Thermal | -2.6033 | -2.6848 | -2.6975 | -2.8261 | -9.136 | -9.4149 | -9.7544 | -10.1281 | -10.3369 | -10.2798 | -10.6995 | -11.121 | -11.5243 | -11.9249 | -12.3305 | -12.7461 | -13.4836 | -1.6331 | -2.7943
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | Steady Progression | Headroom (MW) | Thermal | -2.6039 | -2.6643 | -2.7084 | -2.7391 | -11.9887 | -12.0502 | -14.1499 | -16.2709 | -18.2949 | -20.2188 | -21.9167 | -23.5437 | -24.7377 | -25.9183 | -27.0025 | -28.1954 | -32.5058 | -36.7729 | -40.243
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | System Transformation | Headroom (MW) | Thermal | -2.6078 | -2.6927 | -2.7457 | -2.8975 | -9.2205 | -9.4671 | -9.7627 | -10.0705 | -10.2485 | -10.2412 | -10.5841 | -10.9332 | -11.2684 | -11.5865 | -11.8791 | -12.2247 | -13.6186 | -13.3373 | -14.2076
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | 52.9617 | -0.0136 | WPD Best View | Headroom (MW) | Thermal | -2.6039 | -2.6643 | -2.7084 | -2.7391 | -11.9887 | -12.0502 | -14.1499 | -16.2709 | -18.2949 | -20.2188 | -21.9167 | -23.5437 | -24.7377 | -25.9183 | -27.0025 | -28.1954 | -32.5058 | -36.7729 | -40.483
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Consumer Transformation | Headroom (MW) | Thermal | 11.2134 | 11.0674 | 10.8323 | 10.369 | 9.8783 | 9.2536 | 8.4405 | 7.6385 | 6.8346 | 5.9956 | 4.162 | 3.2929 | 2.4208 | 1.5524 | -0.18193 | -1.0607 | -7.254 | -12.9298 | -18.4069
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Leading the Way | Headroom (MW) | Thermal | 11.2543 | 11.1839 | 11.0477 | 10.7165 | 10.3507 | 9.9703 | 9.4793 | 8.9576 | 8.4001 | 7.8668 | 7.3508 | 6.8863 | 5.5165 | 5.0818 | 4.6677 | 4.2088 | 1.0119 | -2.6014 | -5.136
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | Steady Progression | Headroom (MW) | N/A | 11.2759 | 11.1989 | 11.0953 | 10.9243 | 10.7523 | 10.5851 | 10.422 | 10.241 | 10.0508 | 9.8511 | 9.6266 | 9.4061 | 9.2069 | 8.9256 | 8.6548 | 8.4521 | 7.7142 | 7.2114 | 6.4358
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | System Transformation | Headroom (MW) | Thermal | 11.249 | 11.1645 | 11.0145 | 10.7794 | 10.4268 | 10.06 | 9.5974 | 9.1233 | 8.6148 | 8.103 | 7.559 | 7.0441 | 6.5603 | 6.0781 | 5.6167 | 5.1154 | 2.3519 | 0.90622 | -0.39748
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | 52.9693 | -0.0146 | WPD Best View | Headroom (MW) | N/A | 11.2672 | 11.1987 | 11.095 | 10.9193 | 10.7417 | 10.5678 | 10.3966 | 10.2069 | 10.0129 | 9.8068 | 9.5634 | 9.338 | 9.1355 | 8.8509 | 8.5799 | 8.3642 | 7.6483 | 7.0401 | 6.169
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Consumer Transformation | Headroom (MW) | Thermal | 14.7889 | 14.6592 | 14.3069 | 13.8334 | 13.3099 | 12.6067 | 11.6615 | 10.7166 | 9.7735 | 8.9821 | 7.9321 | 6.8406 | 5.736 | 4.6445 | 3.5667 | 2.4209 | -3.137 | -8.3844 | -13.2042
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Leading the Way | Headroom (MW) | N/A | 14.8505 | 14.8311 | 14.6262 | 14.3352 | 13.999 | 13.641 | 13.1455 | 12.6311 | 12.0584 | 11.9078 | 11.3261 | 10.8061 | 10.2479 | 9.6992 | 9.1138 | 8.5724 | 5.8189 | 3.456 | 1.5406
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | Steady Progression | Headroom (MW) | N/A | 14.8609 | 14.8236 | 14.6633 | 14.4589 | 14.259 | 14.0518 | 13.8538 | 13.6396 | 13.3931 | 13.3086 | 13.0457 | 12.8066 | 12.5583 | 12.3229 | 12.0882 | 11.8426 | 10.7751 | 10.0766 | 9.1077
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | System Transformation | Headroom (MW) | N/A | 14.8445 | 14.7905 | 14.5767 | 14.2826 | 13.9457 | 13.6034 | 13.1101 | 12.6101 | 12.0454 | 11.7703 | 11.2043 | 10.6892 | 10.148 | 9.6335 | 9.1494 | 8.6168 | 6.257 | 4.1607 | 2.3985
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | 52.9778 | -0.033 | WPD Best View | Headroom (MW) | N/A | 14.8609 | 14.8239 | 14.6636 | 14.4554 | 14.2505 | 14.0376 | 13.8335 | 13.6118 | 13.3606 | 13.2713 | 13.0008 | 12.7543 | 12.5033 | 12.2604 | 12.0231 | 11.7695 | 10.7115 | 9.9389 | 8.9133
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Consumer Transformation | Headroom (MW) | Thermal | -1.708 | -1.7863 | -1.9059 | -2.1979 | -2.5231 | -2.8779 | -3.2657 | -3.6628 | -4.0616 | -4.4478 | -4.8674 | -5.2411 | -5.61 | -5.9957 | -6.3579 | -6.7318 | -9.4365 | -11.091 | -13.6779
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Leading the Way | Headroom (MW) | Thermal | -1.6872 | -1.7402 | -1.832 | -2.0749 | -2.3557 | -2.6364 | -2.9305 | -3.2161 | -3.5221 | -3.7838 | -4.0554 | -4.3276 | -4.5753 | -4.8334 | -5.0891 | -5.3378 | -6.4852 | -8.8785 | -10.3701
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | Steady Progression | Headroom (MW) | Thermal | -1.6903 | -1.7338 | -1.8249 | -1.9564 | -2.1108 | -2.2647 | -2.3957 | -2.5413 | -2.6788 | -2.909 | -3.1494 | -3.3706 | -3.6068 | -3.8248 | -4.041 | -4.2343 | -4.6638 | -4.7951 | -5.113
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | System Transformation | Headroom (MW) | Thermal | -1.6921 | -1.7485 | -1.8499 | -2.0998 | -2.373 | -2.6593 | -2.9671 | -3.2633 | -3.589 | -3.8929 | -4.2095 | -4.5143 | -4.8039 | -5.095 | -5.3715 | -5.6313 | -6.4661 | -7.0551 | -7.6792
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 53.0887 | 0.0197 | WPD Best View | Headroom (MW) | Thermal | -1.6916 | -1.7476 | -1.8391 | -2.0889 | -2.363 | -2.6403 | -2.9259 | -3.2098 | -3.5153 | -3.8082 | -4.1032 | -4.397 | -4.6767 | -4.9558 | -5.216 | -5.4615 | -6.3289 | -6.7459 | -7.2344
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Consumer Transformation | Headroom (MW) | Thermal | 37.5873 | 37.3227 | 36.8562 | 35.742 | 34.5715 | 33.227 | 31.5929 | 29.9359 | 27.3259 | 25.667 | 23.8966 | 21.2424 | 19.5455 | 16.9597 | 15.3511 | 11.0959 | -0.98762 | -20.3657 | -38.5725
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Leading the Way | Headroom (MW) | Thermal | 37.6795 | 37.5697 | 37.2846 | 36.4417 | 35.5445 | 34.6725 | 33.659 | 32.6205 | 31.4829 | 30.505 | 28.5759 | 27.599 | 25.4124 | 24.4757 | 20.0967 | 16.6404 | 3.0214 | -12.3299 | -28.2972
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | Steady Progression | Headroom (MW) | N/A | 37.6649 | 37.5573 | 37.3397 | 36.699 | 36.0573 | 35.4332 | 34.8494 | 34.2356 | 33.5915 | 32.9428 | 32.2461 | 31.4956 | 30.7652 | 30.0582 | 29.3762 | 28.7601 | 25.2224 | 23.6323 | 22.6807
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | System Transformation | Headroom (MW) | Thermal | 37.6519 | 37.5151 | 37.2061 | 36.4322 | 35.5046 | 34.5806 | 33.4809 | 32.3687 | 31.1426 | 29.9648 | 28.7556 | 27.6026 | 25.5697 | 24.4761 | 23.4484 | 20.7302 | 16.1278 | 6.4103 | -2.1061
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | 52.7656 | -0.3838 | WPD Best View | Headroom (MW) | Thermal | 37.5956 | 37.3238 | 36.865 | 35.7776 | 34.6253 | 33.3149 | 31.7201 | 30.1247 | 27.5701 | 25.9372 | 24.1838 | 21.5269 | 19.8366 | 17.2443 | 15.6532 | 11.4336 | -0.10575 | -17.6782 | -34.0821
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Consumer Transformation | Headroom (MW) | Thermal | 12.5035 | 12.285 | 11.9483 | 11.5683 | 11.1572 | 10.5766 | 9.7164 | 8.8859 | 7.1053 | 6.2251 | 5.2245 | 3.3041 | 2.3179 | 0.43846 | -0.45357 | -4.0301 | -13.2295 | -29.1219 | -42.4128
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Leading the Way | Headroom (MW) | Thermal | 12.5624 | 12.4543 | 12.2644 | 12.0885 | 11.8942 | 11.6783 | 11.307 | 10.9588 | 10.5316 | 10.159 | 8.8173 | 8.4339 | 6.7875 | 6.4301 | 2.6459 | -0.26653 | -10.3239 | -22.57 | -35.4262
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Steady Progression | Headroom (MW) | N/A | 12.5703 | 12.4907 | 12.3589 | 12.2613 | 12.1722 | 12.0775 | 11.9683 | 11.8479 | 11.7111 | 11.5537 | 11.3607 | 11.1938 | 11.0269 | 10.8794 | 10.7398 | 10.5849 | 8.7079 | 7.0158 | 6.4768
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | System Transformation | Headroom (MW) | Thermal | 12.5531 | 12.4392 | 12.2436 | 12.0534 | 11.835 | 11.5885 | 11.1634 | 10.7456 | 10.2444 | 9.7616 | 9.2486 | 8.7894 | 7.4042 | 6.9822 | 6.573 | 4.4287 | 1.2599 | -7.6043 | -13.8884
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | WPD Best View | Headroom (MW) | Thermal | 12.5035 | 12.285 | 11.9483 | 11.5683 | 11.1572 | 10.5766 | 9.7164 | 8.8859 | 7.1053 | 6.2251 | 5.2245 | 3.3041 | 2.3179 | 0.43846 | -0.45357 | -4.0301 | -13.2295 | -29.1219 | -42.4128
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Consumer Transformation | Headroom (MW) | Thermal | 2.9796 | 2.9447 | 2.8913 | 2.4271 | 1.9487 | 1.4477 | 0.94707 | 0.42844 | -0.09511 | -0.57957 | -1.0648 | -1.5245 | -1.9686 | -2.4038 | -2.8511 | -3.2718 | -4.816 | -6.8974 | -10.3725
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Leading the Way | Headroom (MW) | Thermal | 2.996 | 2.9763 | 2.9442 | 2.5234 | 2.0767 | 1.6401 | 1.2107 | 0.77716 | 0.32734 | -0.045331 | -0.42251 | -0.79778 | -1.1256 | -1.4913 | -1.8706 | -2.2094 | -4.6857 | -6.5793 | -8.5803
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | Steady Progression | Headroom (MW) | Thermal | 2.9955 | 2.9729 | 2.9464 | 2.6339 | 2.311 | 1.9983 | 1.7173 | 1.4292 | 1.1407 | 0.85681 | 0.56792 | 0.19735 | -0.16141 | -0.51423 | -0.85177 | -1.1447 | -2.0583 | -1.9779 | -2.1801
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | System Transformation | Headroom (MW) | Thermal | 2.9923 | 2.9669 | 2.9244 | 2.588 | 2.1396 | 1.6941 | 1.2494 | 0.81431 | 0.35487 | -0.08093 | -0.52694 | -0.96713 | -1.3715 | -1.7953 | -2.1797 | -2.5369 | -3.1366 | -3.6198 | -5.4795
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | 52.8488 | -0.2762 | WPD Best View | Headroom (MW) | Thermal | 2.9886 | 2.9471 | 2.9032 | 2.4648 | 2.0045 | 1.5369 | 1.0755 | 0.61498 | 0.13887 | -0.31844 | -0.77867 | -1.231 | -1.6604 | -2.0917 | -2.5149 | -2.8942 | -3.9732 | -4.5986 | -6.6437
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Consumer Transformation | Headroom (MW) | N/A | 9.1042 | 9.093 | 9.0165 | 8.7465 | 8.4656 | 8.2027 | 7.9294 | 7.6215 | 7.3157 | 7.0215 | 6.737 | 6.4627 | 6.1963 | 5.9251 | 5.6557 | 5.3978 | 4.0579 | 2.6537 | 1.2127
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Leading the Way | Headroom (MW) | N/A | 9.1211 | 9.1391 | 9.0761 | 8.8298 | 8.5736 | 8.3541 | 8.1413 | 7.8846 | 7.624 | 7.3914 | 7.181 | 6.9629 | 6.7505 | 6.5369 | 6.3214 | 6.1163 | 5.031 | 3.8194 | 2.7094
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | Steady Progression | Headroom (MW) | N/A | 9.0991 | 9.0937 | 9.0345 | 8.8038 | 8.5741 | 8.3573 | 8.1638 | 7.9585 | 7.7396 | 7.5323 | 7.3176 | 7.1044 | 6.8998 | 6.693 | 6.4882 | 6.3199 | 5.5727 | 5.5944 | 5.3839
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | System Transformation | Headroom (MW) | N/A | 9.1066 | 9.109 | 9.0381 | 8.7908 | 8.53 | 8.298 | 8.0681 | 7.8088 | 7.5433 | 7.2841 | 7.034 | 6.7803 | 6.5369 | 6.2892 | 6.055 | 5.8384 | 5.0045 | 4.6344 | 4.2618
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | 52.7586 | -0.3646 | WPD Best View | Headroom (MW) | N/A | 9.1035 | 9.0917 | 9.0135 | 8.7445 | 8.4636 | 8.2014 | 7.9281 | 7.6238 | 7.3259 | 7.0306 | 6.738 | 6.4537 | 6.1791 | 5.8975 | 5.6216 | 5.3579 | 4.097 | 3.0423 | 1.9744
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Consumer Transformation | Headroom (MW) | Thermal | -22.691 | -23.4942 | -24.9773 | -32.8147 | -35.6738 | -39.3389 | -56.8697 | -62.3626 | -67.2137 | -71.8864 | -77.9284 | -86.2607 | -95.5159 | -92.9934 | -101.538 | -110.2404 | -166.4313 | -208.9909 | -239.2734
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Leading the Way | Headroom (MW) | Thermal | -22.4474 | -22.7975 | -23.7279 | -25.8051 | -32.9626 | -35.2578 | -48.586 | -51.4508 | -53.9518 | -57.674 | -62.9234 | -70.6023 | -76.1411 | -71.3079 | -76.9476 | -82.5576 | -125.1291 | -160.5448 | -194.8609
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | Steady Progression | Headroom (MW) | Thermal | -22.4479 | -22.7922 | -23.5099 | -24.4229 | -30.4325 | -31.423 | -32.5874 | -33.7864 | -34.6323 | -35.9886 | -37.6774 | -40.9512 | -44.6846 | -48.4144 | -52.1475 | -55.7657 | -78.9815 | -97.396 | -105.1177
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | System Transformation | Headroom (MW) | Thermal | -22.5039 | -22.9243 | -23.8722 | -44.2616 | -46.2906 | -48.6253 | -51.4882 | -54.3479 | -56.7073 | -59.7121 | -63.8101 | -74.1918 | -77.105 | -62.4856 | -65.1561 | -68.9019 | -92.2688 | -104.917 | -113.448
Walpole 132kV | Spalding & South Holland | Spalding & South Holland | Bulk Supply Point | 33 | 52.7567 | 0.0316 | WPD Best View | Headroom (MW) | Thermal | -22.5034 | -22.9356 | -23.8841 | -43.994 | -45.7394 | -47.6932 | -50.2215 | -52.754 | -54.7775 | -57.4303 | -61.41 | -71.7439 | -74.6297 | -60.0467 | -62.801 | -66.5238 | -85.2866 | -94.4756 | -103.5602
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Consumer Transformation | Headroom (MW) | Thermal | 1.8442 | 1.7723 | 1.6678 | 1.4339 | 1.1918 | 0.89539 | 0.51311 | 0.13222 | -0.24689 | -0.63315 | -1.0387 | -1.5005 | -1.9618 | -2.3978 | -2.8485 | -3.2947 | -5.1694 | -7.0909 | -8.9866
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Leading the Way | Headroom (MW) | Thermal | 1.8715 | 1.8435 | 1.7818 | 1.6146 | 1.4405 | 1.2681 | 1.0404 | 0.82404 | 0.58088 | 0.36448 | 0.088664 | -0.182 | -0.43786 | -0.67963 | -0.92604 | -1.1809 | -2.231 | -4.7532 | -6.0573
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | Steady Progression | Headroom (MW) | Thermal | 1.8641 | 1.847 | 1.8024 | 1.77 | 1.6488 | 1.512 | 1.3918 | 1.2709 | 1.1438 | 1.0162 | 0.86733 | 0.7422 | 0.60728 | 0.49564 | 0.40013 | 0.28832 | 0.098601 | 0.18279 | -0.080862
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | System Transformation | Headroom (MW) | Thermal | 1.8629 | 1.8327 | 1.7747 | 1.6026 | 1.4302 | 1.2434 | 1.0107 | 0.794 | 0.54111 | 0.29707 | 0.047502 | -0.18225 | -0.39404 | -0.5934 | -0.77355 | -0.97428 | -1.5722 | -2.1171 | -2.7627
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | 52.6835 | -0.164 | WPD Best View | Headroom (MW) | Thermal | 1.8618 | 1.8202 | 1.7583 | 1.5806 | 1.3956 | 1.2005 | 0.94745 | 0.70445 | 0.4432 | 0.192 | -0.068839 | -0.38492 | -0.67933 | -0.96739 | -1.2531 | -1.5496 | -2.4972 | -3.4127 | -4.3377
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Consumer Transformation | Headroom (MW) | Thermal | 10.4455 | 10.2597 | 9.9629 | 9.4533 | 8.9008 | 8.2315 | 7.3208 | 6.4072 | 4.5174 | 3.5487 | 2.455 | 0.41991 | -1.6211 | -2.6851 | -4.5862 | -6.5188 | -16.2933 | -24.2466 | -31.9942
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Leading the Way | Headroom (MW) | Thermal | 10.5125 | 10.4164 | 10.2325 | 9.8852 | 9.4943 | 9.1165 | 8.5652 | 7.997 | 7.3487 | 6.7357 | 5.143 | 4.5102 | 3.8705 | 2.3632 | 1.846 | 0.41989 | -5.1098 | -9.9897 | -14.6372
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | Steady Progression | Headroom (MW) | N/A | 10.4933 | 10.4157 | 10.2889 | 10.2091 | 10.1239 | 10.0616 | 9.8792 | 9.6905 | 9.4769 | 9.2525 | 9.0068 | 8.764 | 8.5374 | 8.2422 | 7.9641 | 7.7423 | 7.0393 | 6.7248 | 6.1748
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | System Transformation | Headroom (MW) | Thermal | 10.49 | 10.3912 | 10.2096 | 9.9561 | 9.5736 | 9.1985 | 8.6559 | 8.1314 | 7.5455 | 6.9642 | 6.3652 | 4.8533 | 4.2746 | 3.7506 | 3.239 | 2.687 | -0.31505 | -1.6578 | -3.7261
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 52.8169 | 0.0295 | WPD Best View | Headroom (MW) | Thermal | 10.4901 | 10.3909 | 10.2093 | 9.9552 | 9.666 | 9.3848 | 8.9274 | 8.489 | 7.9894 | 7.494 | 6.9812 | 5.5569 | 5.0629 | 4.544 | 4.0333 | 3.5578 | 0.74761 | -0.54481 | -2.5755
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Consumer Transformation | Headroom (MW) | Thermal | 8.48 | 8.3182 | 8.0577 | 7.5317 | 6.9439 | 6.2363 | 5.3718 | 3.599 | 2.7017 | 1.8509 | -0.091579 | -1.9824 | -3.85 | -5.7742 | -7.5429 | -9.3773 | -20.5463 | -31.9203 | -42.3871
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Leading the Way | Headroom (MW) | Thermal | 8.5253 | 8.4274 | 8.2762 | 7.8758 | 7.4428 | 6.9787 | 6.4483 | 5.9127 | 5.3297 | 3.8909 | 3.3041 | 1.8768 | 1.3805 | -0.13543 | -1.5184 | -2.0164 | -9.1979 | -16.7188 | -24.225
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | Steady Progression | Headroom (MW) | N/A | 8.5264 | 8.4516 | 8.3219 | 8.1574 | 7.9821 | 7.8006 | 7.6281 | 7.4444 | 7.2486 | 7.0529 | 6.6354 | 6.2745 | 5.9157 | 5.5384 | 5.1755 | 4.8359 | 3.6542 | 2.799 | 1.639
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | System Transformation | Headroom (MW) | Thermal | 8.5197 | 8.415 | 8.2501 | 7.8356 | 7.3736 | 6.8937 | 6.3356 | 5.7694 | 5.1621 | 4.5745 | 3.0018 | 2.4331 | 1.8974 | 1.3074 | 0.75937 | -0.73578 | -2.6626 | -5.4802 | -8.2019
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 52.7784 | 0.1137 | WPD Best View | Headroom (MW) | Thermal | 8.5197 | 8.4144 | 8.2495 | 8.0226 | 7.7527 | 7.4666 | 7.0842 | 6.6955 | 6.2664 | 5.856 | 4.2967 | 3.7412 | 3.2099 | 2.6329 | 2.0888 | 0.60928 | -1.3374 | -4.0072 | -6.6144
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Consumer Transformation | Headroom (MW) | N/A | 11.8015 | 11.7301 | 11.5258 | 11.2846 | 11.0192 | 10.6645 | 10.1578 | 9.6401 | 9.7834 | 9.2894 | 8.7352 | 8.1823 | 7.6698 | 9.2417 | 8.7697 | 8.2624 | 5.483 | 3.0895 | 0.80785
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Leading the Way | Headroom (MW) | N/A | 11.8256 | 11.8309 | 11.7 | 11.5729 | 11.4277 | 11.2669 | 10.9934 | 10.6978 | 11.2976 | 11.0949 | 10.8387 | 10.5904 | 10.3482 | 12.0984 | 11.8499 | 11.6159 | 10.1892 | 8.8783 | 7.7083
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | Steady Progression | Headroom (MW) | N/A | 11.8347 | 11.8115 | 11.7086 | 11.6826 | 11.6603 | 11.6482 | 11.5062 | 11.3474 | 11.5844 | 11.4471 | 11.2942 | 11.1487 | 11.0056 | 10.8763 | 10.766 | 10.6606 | 10.187 | 10.2198 | 9.9445
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | System Transformation | Headroom (MW) | N/A | 11.8206 | 11.8015 | 11.6677 | 11.5141 | 11.3469 | 11.1697 | 10.8815 | 10.58 | 10.9015 | 10.6167 | 10.3047 | 9.9936 | 9.7258 | 11.5441 | 11.3282 | 11.0807 | 9.816 | 8.9567 | 8.2073
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | 52.7733 | -0.1429 | WPD Best View | Headroom (MW) | N/A | 11.8206 | 11.8015 | 11.6677 | 11.5141 | 11.3469 | 11.1697 | 10.8815 | 10.58 | 10.9015 | 10.6167 | 10.3047 | 9.9936 | 9.7258 | 11.5441 | 11.3282 | 11.0807 | 9.816 | 8.9567 | 8.2073
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Consumer Transformation | Headroom (MW) | Thermal | 15.3649 | 15.1875 | 14.9357 | 14.3055 | 13.6259 | 12.7738 | 11.7206 | 10.6346 | 9.5145 | 8.3441 | 7.1031 | 5.8369 | 4.5682 | 3.2834 | 2.0231 | 0.77859 | -5.779 | -11.5229 | -16.911
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Leading the Way | Headroom (MW) | Fault level | 15.2774 | 15.1859 | 15.0535 | 14.5881 | 14.0721 | 13.5276 | 12.8488 | 12.1356 | 11.3291 | 10.5319 | 9.7128 | 8.9014 | 8.0857 | 7.2599 | 6.4675 | 5.7873 | 2.6807 | 0.33647 | -1.63
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | Steady Progression | Headroom (MW) | N/A | 12.1099 | 12.0633 | 12.0201 | 11.8557 | 11.6893 | 11.5172 | 11.3493 | 11.1685 | 10.9651 | 10.6433 | 10.4094 | 10.0695 | 9.724 | 9.3829 | 9.0337 | 8.7057 | 7.5919 | 6.9619 | 6.6166
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | System Transformation | Headroom (MW) | N/A | 14.7154 | 14.6337 | 14.521 | 14.0923 | 13.6225 | 13.1269 | 12.5145 | 11.8966 | 11.21 | 10.5215 | 9.8065 | 9.0966 | 8.3869 | 7.6601 | 6.9441 | 6.2367 | 3.345 | 1.5657 | 0.16383
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | 52.7957 | -0.1543 | WPD Best View | Headroom (MW) | Fault level | 14.4186 | 14.3386 | 14.2282 | 13.8042 | 13.3402 | 12.8492 | 12.2432 | 11.6252 | 10.9319 | 10.249 | 9.5487 | 8.8547 | 8.1584 | 7.4495 | 6.7482 | 6.0611 | 3.1738 | 1.3178 | -0.08552
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Consumer Transformation | Headroom (MW) | Thermal | 14.5191 | 14.5114 | 14.3916 | 14.1041 | 13.9643 | 13.6491 | 13.3622 | 13.0818 | 12.8135 | 12.5041 | 12.1971 | 10.5001 | 7.8969 | 5.299 | 3.0233 | 0.77388 | -17.5353 | -29.1026 | -29.7246
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Leading the Way | Headroom (MW) | Thermal | 14.5252 | 14.5574 | 14.4561 | 14.1836 | 14.1238 | 13.8545 | 13.6509 | 13.4544 | 13.2591 | 13.049 | 12.8066 | 10.3299 | 7.4823 | 4.6216 | 2.3291 | 0.068825 | -18.6671 | -33.4105 | -48.914
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | Steady Progression | Headroom (MW) | Thermal | 14.5227 | 14.5164 | 14.4282 | 14.1758 | 14.0452 | 13.8015 | 13.5972 | 13.4118 | 13.215 | 13.0059 | 12.7821 | 11.0073 | 8.8107 | 6.6073 | 4.34 | 2.099 | -9.4403 | -21.4294 | -21.6475
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | System Transformation | Headroom (MW) | N/A | 14.522 | 14.529 | 14.4335 | 14.1627 | 14.044 | 13.7689 | 13.5407 | 13.3133 | 13.1064 | 12.8472 | 12.5745 | 12.3184 | 12.0705 | 11.8088 | 11.5695 | 11.3411 | 2.0492 | 1.7385 | 2.112
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | 52.8136 | -0.1342 | WPD Best View | Headroom (MW) | N/A | 14.522 | 14.5287 | 14.4332 | 14.1659 | 14.0521 | 13.7824 | 13.5599 | 13.3397 | 13.1373 | 12.8827 | 12.6169 | 12.3677 | 12.1222 | 11.8672 | 11.6302 | 11.4091 | 11.0288 | 10.6513 | 10.879
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Consumer Transformation | Headroom (MW) | Thermal | 2.9594 | 2.9309 | 2.8822 | 2.6413 | 2.298 | 1.9209 | 1.5522 | 1.1675 | 0.78083 | 0.40397 | 0.03217 | -0.32869 | -0.6859 | -1.0366 | -1.3932 | -1.7403 | -3.57 | -5.176 | -7.0569
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Leading the Way | Headroom (MW) | Thermal | 2.9647 | 2.9544 | 2.9276 | 2.6145 | 2.2936 | 1.9738 | 1.6609 | 1.3449 | 1.0111 | 0.72441 | 0.42877 | 0.14974 | -0.12964 | -0.40202 | -0.68854 | -0.95705 | -2.4842 | -4.1157 | -5.8779
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | Steady Progression | Headroom (MW) | Thermal | 2.9641 | 2.9525 | 2.9317 | 2.812 | 2.7017 | 2.5925 | 2.4856 | 2.3876 | 2.2783 | 2.1797 | 1.9807 | 1.7033 | 1.4269 | 1.1581 | 0.89203 | 0.66469 | -0.23924 | -0.45162 | -0.97851
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | System Transformation | Headroom (MW) | Thermal | 2.9623 | 2.9482 | 2.9135 | 2.688 | 2.457 | 2.1322 | 1.812 | 1.4918 | 1.159 | 0.84002 | 0.49283 | 0.16109 | -0.16169 | -0.4821 | -0.79208 | -1.085 | -2.198 | -2.8299 | -3.5906
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | 52.6979 | -0.052 | WPD Best View | Headroom (MW) | Thermal | 2.9631 | 2.9493 | 2.9162 | 2.7862 | 2.5614 | 2.3333 | 2.1015 | 1.8678 | 1.6183 | 1.3899 | 1.0575 | 0.74223 | 0.4299 | 0.12624 | -0.17535 | -0.45487 | -1.7215 | -2.4188 | -3.4243
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Consumer Transformation | Headroom (MW) | Thermal | 53.6382 | 52.7931 | 51.4902 | 49.8908 | 48.0626 | 45.3947 | 39.0254 | 35.2875 | 31.576 | 27.7467 | 23.6008 | 19.5589 | 14.673 | 9.9015 | 6.0866 | 0.066966 | -27.6563 | -68.1599 | -108.5797
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Leading the Way | Headroom (MW) | Thermal | 53.8775 | 53.6108 | 53.0193 | 52.4313 | 48.9091 | 47.9179 | 46.3145 | 44.8036 | 42.9631 | 41.3699 | 39.8209 | 38.4097 | 36.9328 | 35.4711 | 27.3491 | 14.1771 | -14.5805 | -43.564 | -68.5536
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | Steady Progression | Headroom (MW) | N/A | 53.9374 | 53.6274 | 53.1312 | 52.6933 | 52.2005 | 51.7451 | 51.2515 | 50.6989 | 47.5517 | 46.9103 | 46.202 | 45.5762 | 44.9778 | 44.515 | 44.0996 | 43.6658 | 42.6644 | 42.2846 | 38.059
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | System Transformation | Headroom (MW) | Thermal | 53.834 | 53.4423 | 52.667 | 51.8834 | 50.8071 | 49.6473 | 45.1594 | 43.2556 | 41.0158 | 38.8802 | 36.7743 | 34.8428 | 32.9747 | 31.2674 | 29.7485 | 28.2004 | 21.1598 | 0.27265 | -21.6764
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | 52.6512 | -0.4714 | WPD Best View | Headroom (MW) | Thermal | 53.6535 | 52.8844 | 51.6032 | 50.112 | 48.3616 | 45.8291 | 39.6792 | 36.1448 | 32.5967 | 28.8862 | 24.9398 | 21.0897 | 17.3141 | 12.7309 | 9.1507 | 3.4249 | -16.6982 | -52.9307 | -87.7165
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Consumer Transformation | Headroom (MW) | Thermal | 12.3536 | 12.2108 | 11.9922 | 11.6789 | 11.3086 | 10.7333 | 10.0231 | 9.3203 | 8.6144 | 7.9111 | 7.1365 | 6.3897 | 5.664 | 4.9921 | 4.3083 | 3.5627 | 0.32715 | -2.9293 | -6.1335
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Leading the Way | Headroom (MW) | N/A | 12.3905 | 12.3207 | 12.1953 | 12.0309 | 11.6904 | 11.3555 | 10.9442 | 10.5269 | 10.0663 | 9.6916 | 9.2804 | 8.8996 | 8.549 | 8.2484 | 7.9623 | 7.5749 | 5.7866 | 2.8267 | 1.1779
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | Steady Progression | Headroom (MW) | N/A | 12.3986 | 12.3323 | 12.2406 | 12.1132 | 11.9467 | 11.7911 | 11.6337 | 11.472 | 11.2967 | 11.1323 | 10.9332 | 10.7586 | 10.5822 | 10.4429 | 10.3246 | 10.1781 | 9.757 | 9.7887 | 9.4113
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | System Transformation | Headroom (MW) | N/A | 12.383 | 12.3044 | 12.1696 | 11.9914 | 11.7391 | 11.4758 | 11.0374 | 10.6035 | 10.1151 | 9.6721 | 9.1946 | 8.7441 | 8.3122 | 7.939 | 7.5871 | 7.2701 | 6.1478 | 5.1995 | 4.2306
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | 52.6782 | -0.3012 | WPD Best View | Headroom (MW) | Thermal | 12.3529 | 12.2094 | 11.9892 | 11.6768 | 11.3066 | 10.7319 | 10.0219 | 9.3226 | 8.6246 | 7.9201 | 7.1376 | 6.3807 | 5.6448 | 4.9624 | 4.2721 | 3.5205 | 0.36528 | -2.5415 | -5.3727
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Consumer Transformation | Headroom (MW) | Thermal | 15.5717 | 15.3039 | 14.9005 | 14.3867 | 13.7959 | 12.9289 | 11.6462 | 10.3823 | 9.1175 | 7.7741 | 6.3415 | 4.9013 | 3.4715 | 2.0507 | 0.63689 | -1.8048 | -10.5188 | -22.8631 | -35.8872
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Leading the Way | Headroom (MW) | Thermal | 15.6511 | 15.5916 | 15.4436 | 15.282 | 15.0143 | 14.7322 | 14.2195 | 13.7268 | 13.1011 | 12.5022 | 11.9287 | 11.3641 | 10.8001 | 10.2473 | 7.9979 | 3.9464 | -5.0077 | -11.9257 | -18.3941
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | Steady Progression | Headroom (MW) | N/A | 15.6766 | 15.6024 | 15.4699 | 15.3651 | 15.2441 | 15.1272 | 14.9976 | 14.8374 | 14.6625 | 14.4636 | 14.2437 | 14.046 | 13.8386 | 13.6749 | 13.5026 | 13.3279 | 12.802 | 12.5217 | 11.6086
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | System Transformation | Headroom (MW) | Thermal | 15.6414 | 15.5352 | 15.3209 | 15.0956 | 14.7666 | 14.4076 | 13.8042 | 13.2053 | 12.4904 | 11.7881 | 11.1165 | 10.4635 | 9.824 | 9.2098 | 8.6383 | 8.0317 | 5.6206 | -0.6593 | -7.8703
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | 52.6516 | -0.4717 | WPD Best View | Headroom (MW) | Thermal | 15.5764 | 15.333 | 14.9287 | 14.4459 | 13.8745 | 13.0402 | 11.8154 | 10.6095 | 9.3858 | 8.072 | 6.6946 | 5.301 | 3.9261 | 2.558 | 1.2109 | -1.1498 | -8.1825 | -19.7744 | -31.2324
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Consumer Transformation | Headroom (MW) | Thermal | 5.0416 | 5.0111 | 4.9581 | 4.897 | 4.8408 | 4.756 | 4.6174 | 4.5037 | 4.3936 | 4.3064 | 4.1999 | 4.1288 | 3.1515 | 3.1161 | 3.1065 | 3.0524 | 0.44102 | -4.4745 | -7
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Leading the Way | Headroom (MW) | Thermal | 5.0518 | 5.0475 | 5.0281 | 5.0224 | 5.0201 | 5.0195 | 5.0075 | 5.0156 | 5.0352 | 5.0965 | 5.1588 | 5.2802 | 5.2946 | 5.2259 | 5.2667 | 2.3334 | 1.155 | -4.2456 | -8.0397
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | Steady Progression | Headroom (MW) | N/A | 5.0588 | 5.041 | 5.0265 | 5.0193 | 5.0074 | 5.008 | 5.0019 | 5.0007 | 5.006 | 5.0012 | 5.0162 | 5.0265 | 5.057 | 5.0991 | 5.1484 | 5.2219 | 5.5215 | 5.5266 | 5.3331
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | System Transformation | Headroom (MW) | N/A | 5.0461 | 5.033 | 5.0004 | 4.9713 | 4.9401 | 4.906 | 4.833 | 4.7739 | 4.7016 | 4.6489 | 4.5969 | 4.5904 | 4.5923 | 4.615 | 4.6714 | 4.7293 | 5.1285 | 2.3833 | 0.81296
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | 52.6377 | -0.5431 | WPD Best View | Headroom (MW) | N/A | 5.0483 | 5.0369 | 5.0093 | 4.9854 | 4.9618 | 4.9369 | 4.8764 | 4.8333 | 4.7809 | 4.7518 | 4.7271 | 4.7517 | 4.7862 | 4.8381 | 4.9163 | 4.9736 | 5.1788 | 2.1752 | 0.46784
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Consumer Transformation | Headroom (MW) | Thermal | 11.3455 | 11.2506 | 11.0858 | 10.9444 | 10.7959 | 10.6014 | 10.3209 | 10.0562 | 9.8035 | 9.5557 | 9.2851 | 9.0471 | 8.8186 | 8.6027 | 8.3794 | 8.1298 | 6.6988 | 2.4685 | -0.46122
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Leading the Way | Headroom (MW) | Thermal | 11.3673 | 11.3062 | 11.1934 | 11.1202 | 11.0506 | 10.9751 | 10.8544 | 10.7692 | 10.6612 | 10.5739 | 10.5046 | 10.4637 | 10.4375 | 10.4067 | 8.6761 | 6.9173 | 5.0546 | 1.6154 | -1.8657
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | Steady Progression | Headroom (MW) | N/A | 11.3691 | 11.3068 | 11.2105 | 11.1476 | 11.0876 | 11.0303 | 10.9721 | 10.9124 | 10.8529 | 10.785 | 10.715 | 10.6601 | 10.6104 | 10.5719 | 10.5489 | 10.5157 | 10.4969 | 10.4761 | 10.1448
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | System Transformation | Headroom (MW) | N/A | 11.3644 | 11.2947 | 11.1676 | 11.0753 | 10.9789 | 10.871 | 10.7085 | 10.5634 | 10.391 | 10.2162 | 10.0489 | 9.9192 | 9.7994 | 9.6902 | 9.6014 | 9.5193 | 9.2051 | 6.1031 | 4.168
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | 52.6715 | -0.356 | WPD Best View | Headroom (MW) | Thermal | 11.3455 | 11.2506 | 11.0858 | 10.9444 | 10.7959 | 10.6014 | 10.3209 | 10.0562 | 9.8035 | 9.5557 | 9.2851 | 9.0471 | 8.8186 | 8.6027 | 8.3794 | 8.1298 | 6.6988 | 2.4685 | -0.46122
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Consumer Transformation | Headroom (MW) | Thermal | 6.0041 | 5.9626 | 5.9031 | 5.8472 | 5.7756 | 5.6962 | 3.0217 | 2.8927 | 2.7795 | 2.6753 | 2.5462 | 2.4407 | 2.3459 | 1.3392 | 1.2686 | 1.1816 | -1.8357 | -5.2484 | -10.9608
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Leading the Way | Headroom (MW) | Thermal | 6.0156 | 6.0031 | 5.9651 | 5.9438 | 3.3694 | 3.3534 | 3.3194 | 3.2884 | 3.2483 | 3.2534 | 3.2698 | 3.288 | 3.3016 | 3.3455 | 1.6982 | 1.7088 | -4.3112 | -7.6591 | -10.7878
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | Steady Progression | Headroom (MW) | N/A | 6.0077 | 5.9924 | 5.9638 | 5.9329 | 5.9205 | 5.9112 | 5.8986 | 5.889 | 3.321 | 3.3145 | 3.3 | 3.289 | 3.301 | 3.3014 | 3.3225 | 3.3443 | 3.535 | 3.6998 | 2.2026
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | System Transformation | Headroom (MW) | Thermal | 6.0077 | 5.9898 | 5.9376 | 5.9041 | 5.8658 | 5.8294 | 3.2222 | 3.1543 | 3.0773 | 3.0168 | 2.9509 | 2.9121 | 2.8729 | 2.8536 | 2.8619 | 2.8683 | 1.6872 | 0.15532 | -2.8973
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | 52.6116 | -0.4394 | WPD Best View | Headroom (MW) | Thermal | 6.0041 | 5.9714 | 5.9116 | 5.8635 | 5.7983 | 5.7284 | 3.0793 | 2.9638 | 2.8662 | 2.7647 | 2.6508 | 2.5582 | 2.4623 | 1.4619 | 1.4111 | 1.3504 | -0.32606 | -3.2341 | -7.6357
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Consumer Transformation | Headroom (MW) | Fault level | 11.4579 | 11.2394 | 10.9159 | 10.3592 | 9.7618 | 8.8974 | 7.7213 | 6.4914 | 5.19 | 3.7968 | 2.2713 | 0.67828 | -0.95267 | -2.5927 | -4.2328 | -5.9315 | -14.731 | -21.7922 | -22.4072
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Leading the Way | Headroom (MW) | Fault level | 11.4431 | 11.3418 | 11.1776 | 10.8549 | 10.4675 | 10.0291 | 9.3782 | 8.6328 | 7.7276 | 6.7477 | 5.6956 | 4.6221 | 3.5399 | 2.4275 | 1.3635 | 0.27201 | 0.4485 | -3.514 | -7.7025
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | Steady Progression | Headroom (MW) | Fault level | 9.5499 | 9.492 | 7.0387 | 6.9817 | 6.9242 | 6.8585 | 6.7764 | 3.0827 | 2.9463 | 2.7974 | 1.1488 | -0.47362 | -0.76555 | -1.0696 | -1.3786 | -1.7109 | -2.8454 | -3.6406 | -4.319
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | System Transformation | Headroom (MW) | Fault level | 11.1218 | 11.0179 | 10.8726 | 10.6942 | 10.3419 | 9.9526 | 9.3826 | 8.7919 | 8.1072 | 7.4139 | 6.6877 | 5.9617 | 5.207 | 4.4353 | 3.6664 | 2.8509 | -0.61268 | -2.8352 | 1.1957
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | 53.2282 | -0.5216 | WPD Best View | Headroom (MW) | Fault level | 10.9535 | 10.8555 | 10.7204 | 10.5571 | 10.361 | 10.128 | 9.7206 | 6.5514 | 6.0437 | 5.5349 | 3.875 | 2.2021 | 1.5367 | 0.86347 | 0.18279 | -0.53506 | -3.3004 | -5.3367 | -1.2904
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Consumer Transformation | Headroom (MW) | Thermal | 90.36 | 89.2653 | 87.2364 | 85.2116 | 82.8141 | 79.0796 | 73.6065 | 67.9471 | 61.3513 | 53.6122 | 46.9579 | 39.6124 | 30.5403 | 23.3479 | -1.2086 | -8.6253 | -66.8833 | -136.4237 | -194.607
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Leading the Way | Headroom (MW) | Thermal | 90.606 | 90.0083 | 88.9357 | 87.9923 | 87.0394 | 85.6685 | 82.8162 | 80.7279 | 78.0072 | 75.6688 | 70.9244 | 67.4114 | 48.0032 | 36.8679 | 24.4963 | 9.0747 | -46.2684 | -81.2404 | -134.347
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | Steady Progression | Headroom (MW) | N/A | 90.5784 | 90.1075 | 89.1971 | 88.6612 | 88.1419 | 87.5219 | 86.7007 | 83.9034 | 83.0695 | 82.1999 | 80.0289 | 78.0537 | 77.1503 | 76.3048 | 75.5028 | 74.7187 | 72.3667 | 62.6701 | 53.6587
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | System Transformation | Headroom (MW) | Thermal | 90.5414 | 89.9993 | 88.7258 | 87.7608 | 86.6698 | 85.1386 | 82.5496 | 79.9915 | 77.0274 | 74.1518 | 70.8921 | 67.9262 | 64.16 | 60.5009 | 40.3056 | 37.5806 | 14.0257 | -10.0445 | -37.3057
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | 53.2284 | -0.5186 | WPD Best View | Headroom (MW) | N/A | 101.4313 | 100.9177 | 99.7835 | 99.0458 | 98.2826 | 97.2316 | 95.8031 | 94.365 | 92.7356 | 91.0974 | 88.677 | 86.537 | 84.77 | 83.041 | 64.4036 | 62.6673 | 54.5901 | 36.2165 | 20.4752
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Consumer Transformation | Headroom (MW) | Thermal | 15.8212 | 15.6782 | 15.3378 | 14.903 | 14.4148 | 13.7309 | 12.8176 | 11.8948 | 10.9885 | 10.0431 | 9.0399 | 8.0832 | 7.1378 | 6.2044 | 5.2935 | 4.2808 | -1.6374 | -6.7548 | -12.5031
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Leading the Way | Headroom (MW) | N/A | 15.8297 | 15.794 | 15.658 | 15.4239 | 15.1343 | 14.8173 | 14.3801 | 13.947 | 13.4712 | 13.0386 | 12.6431 | 12.2875 | 11.9513 | 11.6258 | 11.3042 | 10.9542 | 8.2525 | 6.1923 | 4.5894
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | Steady Progression | Headroom (MW) | N/A | 15.8151 | 15.7913 | 15.7127 | 15.6389 | 15.5321 | 15.4491 | 15.3572 | 15.2299 | 15.105 | 14.972 | 14.7945 | 14.6448 | 14.5077 | 14.3744 | 14.18 | 14.0447 | 13.7445 | 13.3941 | 12.7475
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | System Transformation | Headroom (MW) | N/A | 15.8212 | 15.8047 | 15.6251 | 15.4677 | 15.2502 | 14.9362 | 14.477 | 14.0165 | 13.4889 | 12.9823 | 12.4358 | 11.9289 | 11.439 | 10.9574 | 10.5189 | 10.0388 | 8.3742 | 6.7132 | 5.2403
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2426 | -0.5393 | WPD Best View | Headroom (MW) | N/A | 15.8203 | 15.803 | 15.6424 | 15.4947 | 15.2906 | 15.0952 | 14.7618 | 14.4254 | 14.0365 | 13.6543 | 13.2303 | 12.8476 | 12.4873 | 12.1318 | 11.7213 | 11.3466 | 10.0178 | 8.5911 | 7.287
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Consumer Transformation | Headroom (MW) | N/A | 16.3507 | 16.3747 | 16.2968 | 16.2668 | 16.2215 | 16.1802 | 15.9355 | 15.3689 | 14.7955 | 14.1762 | 13.4884 | 12.7859 | 12.0633 | 11.3578 | 10.6593 | 9.9206 | 6.3846 | 3.3558 | 0.68361
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Leading the Way | Headroom (MW) | N/A | 16.3608 | 16.4008 | 16.3259 | 16.2894 | 16.2457 | 16.2081 | 15.7986 | 15.7662 | 15.5527 | 15.5196 | 15.1499 | 14.7335 | 14.3046 | 13.8752 | 13.4184 | 12.9393 | 10.7279 | 9.1506 | 7.98
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | Steady Progression | Headroom (MW) | N/A | 16.3433 | 16.3484 | 16.2658 | 16.2303 | 16.1848 | 16.1439 | 16.0085 | 15.9687 | 15.9269 | 15.8893 | 15.8493 | 15.7208 | 15.6841 | 15.6519 | 15.6221 | 15.5927 | 15.4238 | 15.065 | 14.4866
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | System Transformation | Headroom (MW) | N/A | 16.3507 | 16.3749 | 16.2971 | 16.2672 | 16.2218 | 16.1806 | 16.1494 | 16.1166 | 16.0805 | 16.0462 | 15.7814 | 15.4839 | 15.1814 | 14.8876 | 14.5867 | 14.2703 | 12.8734 | 11.6582 | 10.6247
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | 53.2253 | -0.5526 | WPD Best View | Headroom (MW) | N/A | 16.3507 | 16.3749 | 16.2971 | 16.2672 | 16.2218 | 16.1806 | 16.1533 | 16.1205 | 16.0867 | 16.0523 | 15.7814 | 15.4839 | 15.1814 | 14.8876 | 14.5867 | 14.2703 | 12.8734 | 11.6582 | 10.6247
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Consumer Transformation | Headroom (MW) | Thermal | 14.7697 | 14.7242 | 14.632 | 14.5832 | 14.2907 | 13.8608 | 13.2654 | 12.6907 | 12.1082 | 11.5106 | 10.8142 | 10.2075 | 8.656 | 8.0476 | 7.4583 | 6.7747 | 0.91423 | -6.3547 | -12.1992
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Leading the Way | Headroom (MW) | Thermal | 14.7698 | 14.6915 | 14.6008 | 14.5085 | 14.4634 | 14.4214 | 14.0683 | 14.0311 | 13.8278 | 13.5597 | 13.2731 | 13.0637 | 12.8384 | 12.5192 | 9.7898 | 9.5074 | 4.0404 | -0.04227 | -6.4384
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | Steady Progression | Headroom (MW) | N/A | 14.7697 | 14.7231 | 14.6298 | 14.574 | 14.5253 | 14.4782 | 14.3987 | 12.3023 | 12.2463 | 12.2031 | 11.0564 | 10.0164 | 9.921 | 9.8176 | 9.7351 | 9.6487 | 9.3358 | 9.114 | 7.2221
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | System Transformation | Headroom (MW) | N/A | 14.7697 | 14.7239 | 14.6315 | 14.5824 | 14.5347 | 14.4887 | 14.2192 | 13.9241 | 13.5839 | 13.2533 | 12.9075 | 12.6126 | 12.331 | 12.0575 | 11.831 | 11.5459 | 9.145 | 5.3327 | 1.8534
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | 53.2061 | -0.6155 | WPD Best View | Headroom (MW) | N/A | 15.3582 | 15.2507 | 15.0663 | 14.9273 | 14.7729 | 14.5991 | 14.3549 | 14.1004 | 13.8249 | 13.5501 | 12.9422 | 12.4048 | 12.1745 | 11.9371 | 11.734 | 11.4858 | 10.3479 | 7.8515 | 5.3335
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Consumer Transformation | Headroom (MW) | Thermal | 9.7263 | 9.6028 | 9.4119 | 9.1901 | 8.9366 | 8.5902 | 8.0069 | 7.4497 | 6.8939 | 6.3093 | 5.6695 | 5.0627 | 4.4956 | 3.9052 | 3.3197 | 2.6902 | -2.6041 | -10.1529 | -14.0748
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Leading the Way | Headroom (MW) | Thermal | 9.772 | 9.6645 | 9.5866 | 9.4904 | 9.3665 | 9.2226 | 8.9333 | 8.6483 | 8.3343 | 8.038 | 7.7278 | 7.4969 | 7.2805 | 5.7606 | 3.8095 | 1.825 | -5.8853 | -8.4189 | -16.8078
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | Steady Progression | Headroom (MW) | N/A | 9.7749 | 9.7079 | 9.6389 | 9.5813 | 9.5182 | 9.4627 | 9.4055 | 9.336 | 9.2549 | 9.171 | 9.055 | 8.97 | 8.8965 | 8.8168 | 8.7599 | 8.6908 | 8.5426 | 7.1655 | 6.771
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | System Transformation | Headroom (MW) | Thermal | 9.7675 | 9.6836 | 9.5815 | 9.4714 | 9.3303 | 9.1749 | 8.9321 | 8.6911 | 8.4002 | 8.117 | 7.8222 | 7.5612 | 7.3266 | 7.0995 | 6.8885 | 6.6587 | 3.2706 | -1.4876 | -3.6512
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | 53.2382 | -0.4154 | WPD Best View | Headroom (MW) | N/A | 9.7749 | 9.7079 | 9.6389 | 9.5813 | 9.5182 | 9.4627 | 9.4055 | 9.336 | 9.2549 | 9.171 | 9.055 | 8.97 | 8.8965 | 8.8168 | 8.7599 | 8.6908 | 8.5426 | 7.1655 | 6.771
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Consumer Transformation | Headroom (MW) | Thermal | 8.4077 | 8.289 | 8.0774 | 7.8639 | 7.6412 | 7.3298 | 6.885 | 6.4524 | 5.0824 | 4.6438 | 4.101 | 2.5662 | 1.9867 | 0.47043 | -0.95648 | -1.4879 | -10.1843 | -19.6941 | -28.7353
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Leading the Way | Headroom (MW) | Thermal | 8.4476 | 8.3764 | 8.2398 | 8.1326 | 8.0203 | 7.8984 | 7.708 | 7.5315 | 7.3085 | 7.133 | 5.9009 | 5.6101 | 5.3631 | 2.9014 | 1.0254 | -1.8306 | -9.7908 | -18.1221 | -25.9554
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | Steady Progression | Headroom (MW) | N/A | 8.4493 | 8.3858 | 8.2735 | 8.2033 | 8.1345 | 8.0607 | 7.9951 | 7.9149 | 7.83 | 7.7332 | 7.6255 | 7.5428 | 7.4482 | 7.368 | 7.3003 | 7.2267 | 6.9644 | 5.4895 | 5.0648
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | System Transformation | Headroom (MW) | Thermal | 8.442 | 8.3603 | 8.2084 | 8.0872 | 7.9562 | 7.8147 | 7.5835 | 7.3508 | 7.0827 | 6.8354 | 6.5601 | 6.3153 | 5.1667 | 4.9484 | 4.7636 | 4.5524 | 2.407 | -3.247 | -6.6414
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | 53.1352 | -0.4092 | WPD Best View | Headroom (MW) | N/A | 8.4493 | 8.3858 | 8.2735 | 8.2033 | 8.1345 | 8.0607 | 7.9951 | 7.9149 | 7.83 | 7.7332 | 7.6255 | 7.5428 | 7.4482 | 7.368 | 7.3003 | 7.2267 | 6.9644 | 5.4895 | 5.0648
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Consumer Transformation | Headroom (MW) | Thermal | 13.0581 | 12.8345 | 12.4506 | 12.0515 | 11.6179 | 10.9978 | 10.1422 | 9.2845 | 8.4066 | 7.4493 | 6.3798 | 5.3199 | 4.2992 | 3.292 | 2.3098 | 1.3073 | -4.7595 | -11.8589 | -15.349
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Leading the Way | Headroom (MW) | Thermal | 13.1144 | 12.9535 | 12.725 | 12.5179 | 12.2822 | 12.016 | 11.5851 | 11.1385 | 10.597 | 10.0358 | 9.4434 | 8.8513 | 8.352 | 6.634 | 6.206 | 4.1359 | -0.49115 | -2.9533 | -7.0729
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | Steady Progression | Headroom (MW) | N/A | 13.1254 | 13.019 | 12.8341 | 12.7227 | 12.6129 | 12.4982 | 12.3647 | 12.2287 | 12.0829 | 11.9031 | 11.7038 | 11.5304 | 11.3564 | 11.1848 | 11.0166 | 10.8493 | 10.3121 | 8.6414 | 7.9521
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | System Transformation | Headroom (MW) | Thermal | 13.1056 | 12.9699 | 12.7284 | 12.5155 | 12.2832 | 12.0094 | 11.5865 | 11.1722 | 10.6771 | 10.1871 | 9.6842 | 9.2169 | 8.7577 | 8.3133 | 7.8803 | 7.439 | 4.3797 | 0.19155 | -0.45991
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | 53.1926 | -0.5996 | WPD Best View | Headroom (MW) | N/A | 13.1232 | 13.0189 | 12.8261 | 12.6968 | 12.5743 | 12.4352 | 12.2725 | 12.1048 | 11.9194 | 11.7087 | 11.4694 | 11.2708 | 11.0756 | 10.8793 | 10.6898 | 10.4986 | 9.8612 | 7.9805 | 7.1591
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Consumer Transformation | Headroom (MW) | Thermal | 13.1956 | 13.0318 | 12.8564 | 12.7289 | 12.654 | 12.1511 | 11.4672 | 10.79 | 10.1407 | 9.4626 | 8.694 | 7.9634 | 7.2344 | 6.5029 | 5.7862 | 4.9744 | 0.60552 | -3.8823 | -8.1252
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Leading the Way | Headroom (MW) | N/A | 13.1971 | 13.1486 | 13.1726 | 13.283 | 13.4842 | 13.3401 | 13.0931 | 12.8542 | 12.5571 | 12.3196 | 12.0371 | 11.7896 | 11.5422 | 11.2926 | 11.0331 | 10.72 | 9.0522 | 5.9569 | 3.2236
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | Steady Progression | Headroom (MW) | N/A | 13.1947 | 13.1648 | 13.1454 | 13.2003 | 13.2915 | 13.2516 | 13.1854 | 13.1133 | 13.0294 | 12.9341 | 12.8067 | 12.6939 | 12.5902 | 12.4973 | 12.4188 | 12.3225 | 11.8807 | 11.6214 | 11.0328
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | System Transformation | Headroom (MW) | N/A | 13.1956 | 13.1546 | 13.095 | 13.1181 | 13.198 | 12.9999 | 12.6759 | 12.3704 | 12.0115 | 11.6601 | 11.2753 | 10.9269 | 10.5819 | 10.2565 | 9.9452 | 9.6005 | 8.0436 | 6.515 | 5.1669
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | 53.2103 | -0.5613 | WPD Best View | Headroom (MW) | N/A | 13.1953 | 13.1558 | 13.0987 | 13.1256 | 13.2103 | 13.0182 | 12.7063 | 12.4111 | 12.0735 | 11.7326 | 11.3555 | 11.0099 | 10.6675 | 10.3426 | 10.0319 | 9.6848 | 8.131 | 6.7232 | 5.4727
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Consumer Transformation | Headroom (MW) | N/A | 10.6478 | 10.6386 | 10.6274 | 10.6176 | 10.6079 | 10.5985 | 10.5902 | 10.5819 | 10.5739 | 10.5664 | 10.5592 | 10.5528 | 10.5472 | 10.5423 | 10.5377 | 10.5335 | 10.5112 | 10.4636 | 10.3948
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Leading the Way | Headroom (MW) | N/A | 10.6478 | 10.6386 | 10.6298 | 10.62 | 10.6104 | 10.6012 | 10.5926 | 10.585 | 10.5769 | 10.5695 | 10.5629 | 10.5573 | 10.5526 | 10.5485 | 10.5447 | 10.5411 | 10.508 | 10.4552 | 10.3919
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | Steady Progression | Headroom (MW) | N/A | 10.6478 | 10.6385 | 10.6253 | 10.6154 | 10.6056 | 10.5963 | 10.5872 | 10.5781 | 10.5691 | 10.5603 | 10.5516 | 10.5432 | 10.5349 | 10.5269 | 10.5191 | 10.5116 | 10.4826 | 10.4582 | 10.4115
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | System Transformation | Headroom (MW) | N/A | 10.6478 | 10.6385 | 10.6272 | 10.6173 | 10.6075 | 10.5979 | 10.5891 | 10.5804 | 10.5716 | 10.563 | 10.5545 | 10.5463 | 10.5386 | 10.5314 | 10.5246 | 10.5187 | 10.5003 | 10.4724 | 10.4319
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | 53.2252 | -0.5525 | WPD Best View | Headroom (MW) | N/A | 10.6478 | 10.6385 | 10.6272 | 10.6173 | 10.6075 | 10.5979 | 10.5891 | 10.5804 | 10.5716 | 10.563 | 10.5545 | 10.5463 | 10.5386 | 10.5314 | 10.5246 | 10.5187 | 10.5003 | 10.4735 | 10.4378
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Consumer Transformation | Headroom (MW) | Thermal | 5.8394 | 5.754 | 5.5942 | 5.4137 | 5.2247 | 4.9529 | 4.5368 | 4.1611 | 3.7858 | 2.4916 | 2.0441 | 1.6463 | 0.34587 | -0.037873 | -0.35086 | -1.6281 | -8.4295 | -20.1321 | -30.9256
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Leading the Way | Headroom (MW) | Thermal | 5.8746 | 5.8476 | 5.7769 | 5.6942 | 5.6151 | 5.5399 | 5.3908 | 5.2561 | 5.1138 | 5.0363 | 4.9433 | 3.9868 | 3.9537 | 2.6565 | 0.95625 | -2.4934 | -12.9441 | -22.732 | -33.4671
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | Steady Progression | Headroom (MW) | N/A | 5.8666 | 5.841 | 5.7905 | 5.7554 | 5.7222 | 5.6928 | 5.6496 | 5.6194 | 5.5693 | 5.5269 | 5.4582 | 5.4193 | 5.3851 | 5.3693 | 5.3585 | 5.3589 | 5.5357 | 4.3817 | 2.7193
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | System Transformation | Headroom (MW) | Thermal | 5.8638 | 5.8232 | 5.7443 | 5.6511 | 5.5476 | 5.4437 | 5.2398 | 5.0429 | 4.8311 | 4.6184 | 4.4061 | 4.2518 | 4.0957 | 3.9675 | 2.9388 | 2.8391 | -0.040287 | -5.8868 | -12.8666
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | 53.2728 | -0.576 | WPD Best View | Headroom (MW) | Thermal | 5.8668 | 5.8426 | 5.7932 | 5.7596 | 5.721 | 5.6949 | 5.6462 | 5.6219 | 5.5739 | 5.5456 | 5.4851 | 5.4617 | 5.463 | 5.4561 | 5.4611 | 5.4768 | 5.5574 | 2.8238 | -0.32705
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Consumer Transformation | Headroom (MW) | Thermal | 17.1182 | 16.9561 | 16.6529 | 16.3751 | 16.0675 | 15.6696 | 15.1128 | 14.5804 | 14.0365 | 12.5622 | 11.9274 | 11.3231 | 9.7901 | 9.2036 | 7.9628 | 7.3881 | -0.80305 | -9.4176 | -16.6015
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Leading the Way | Headroom (MW) | Thermal | 17.1573 | 17.0709 | 16.8526 | 16.6996 | 16.5208 | 16.3436 | 16.0633 | 15.8231 | 15.5632 | 15.3311 | 14.1775 | 13.964 | 13.7599 | 12.2804 | 11.3978 | 9.4944 | 3.7541 | -3.4967 | -8.8996
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | Steady Progression | Headroom (MW) | N/A | 17.1607 | 17.0717 | 16.9016 | 16.7949 | 16.6889 | 16.5782 | 16.4704 | 16.3493 | 16.222 | 16.0963 | 15.9397 | 15.8071 | 15.6739 | 15.5459 | 15.4424 | 15.3246 | 14.8982 | 13.2858 | 12.7305
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | System Transformation | Headroom (MW) | N/A | 17.1472 | 17.0532 | 16.8361 | 16.6771 | 16.4863 | 16.29 | 15.979 | 15.6905 | 15.3596 | 15.0268 | 14.6957 | 14.3793 | 14.0954 | 12.8813 | 12.8337 | 12.557 | 10.1381 | 5.5228 | 3.2004
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | 53.1752 | -0.5358 | WPD Best View | Headroom (MW) | N/A | 17.1606 | 17.072 | 16.902 | 16.7957 | 16.69 | 16.5801 | 16.4731 | 16.353 | 16.2274 | 16.1065 | 15.9498 | 15.8215 | 15.6936 | 15.574 | 15.4781 | 15.3696 | 14.9699 | 13.3072 | 12.7119
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Consumer Transformation | Headroom (MW) | Thermal | 1.7007 | 1.6571 | 1.5745 | 1.4934 | 1.4129 | 1.2933 | 1.1224 | 0.9681 | 0.81492 | 0.6727 | 0.5159 | 0.37686 | 0.25971 | 0.13509 | 0.020764 | -0.12969 | -3.6318 | -8.7464 | -13.9225
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Leading the Way | Headroom (MW) | Thermal | 1.7105 | 1.6975 | 1.6432 | 1.6084 | 1.5719 | 1.5356 | 1.4786 | 1.4223 | 1.3801 | 1.3632 | 1.3408 | 1.3461 | 1.3542 | 0.023167 | -1.7396 | -3.4693 | -10.2429 | -17.4123 | -22.0727
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | Steady Progression | Headroom (MW) | Thermal | 1.7067 | 1.6914 | 1.6549 | 1.6202 | 1.6012 | 1.5857 | 1.554 | 1.5384 | 1.5093 | 1.4862 | 1.4636 | 1.4406 | 1.4279 | 1.4276 | 1.4255 | 1.4237 | 1.5218 | 0.32881 | -1.2039
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | System Transformation | Headroom (MW) | Thermal | 1.706 | 1.6879 | 1.6268 | 1.5812 | 1.5296 | 1.4782 | 1.3936 | 1.3115 | 1.2159 | 1.1377 | 1.0447 | 0.97872 | 0.92156 | 0.87612 | 0.84373 | 0.8097 | -1.8166 | -6.0111 | -10.3863
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | 53.2867 | -0.3076 | WPD Best View | Headroom (MW) | Thermal | 1.7066 | 1.69 | 1.6407 | 1.5995 | 1.5638 | 1.5294 | 1.4678 | 1.4192 | 1.3593 | 1.3024 | 1.2508 | 1.2002 | 1.1661 | 1.1389 | 1.1122 | 1.095 | -0.17937 | -2.8513 | -7.064
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Consumer Transformation | Headroom (MW) | N/A | 36.114 | 35.9296 | 35.6994 | 35.4005 | 35.0543 | 34.5458 | 33.8022 | 33.0429 | 32.3162 | 31.5292 | 30.6747 | 29.8091 | 28.9517 | 28.1042 | 27.2476 | 26.3415 | 21.9229 | 17.8764 | 14.2665
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Leading the Way | Headroom (MW) | N/A | 35.9182 | 35.8085 | 35.6985 | 35.5569 | 35.3784 | 35.1749 | 34.8155 | 34.4464 | 34.0711 | 33.6992 | 33.3152 | 32.9486 | 32.571 | 32.1781 | 31.8114 | 31.4243 | 29.7712 | 28.2186 | 26.8198
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | Steady Progression | Headroom (MW) | N/A | 29.9172 | 29.8727 | 29.8275 | 29.7876 | 29.7415 | 29.7005 | 29.6407 | 29.569 | 29.4888 | 29.3964 | 29.2803 | 29.1678 | 29.0553 | 28.9482 | 28.834 | 28.7122 | 28.1753 | 27.6591 | 27.0902
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | System Transformation | Headroom (MW) | N/A | 34.907 | 34.8167 | 34.717 | 34.5912 | 34.4322 | 34.2538 | 33.9342 | 33.6133 | 33.2463 | 32.8794 | 32.4863 | 32.11 | 31.7336 | 31.3509 | 30.977 | 30.5713 | 28.774 | 27.4344 | 26.3839
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | 52.9261 | -1.4762 | WPD Best View | Headroom (MW) | N/A | 34.3298 | 34.1546 | 33.9358 | 33.6516 | 33.3226 | 32.8392 | 32.1323 | 31.4105 | 30.7197 | 29.9716 | 29.1593 | 28.3365 | 27.5214 | 26.7158 | 25.9015 | 25.0401 | 20.8399 | 16.9933 | 13.5617
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Consumer Transformation | Headroom (MW) | N/A | 72.3561 | 72.0566 | 71.3241 | 70.7183 | 69.972 | 68.8601 | 67.2388 | 65.7066 | 61.6758 | 60.117 | 58.4596 | 56.9298 | 55.4537 | 48.4437 | 47.0804 | 45.5354 | 35.3439 | 23.2469 | 10.3673
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Leading the Way | Headroom (MW) | N/A | 72.4042 | 72.2726 | 71.9195 | 71.5598 | 71.1629 | 70.7616 | 67.2464 | 66.7977 | 66.206 | 65.6583 | 65.1085 | 64.6432 | 64.0352 | 58.3973 | 56.886 | 56.4725 | 49.3686 | 42.1508 | 30.5319
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | Steady Progression | Headroom (MW) | N/A | 72.3777 | 72.2399 | 71.844 | 71.6053 | 71.3543 | 71.128 | 70.8631 | 70.5639 | 70.2621 | 69.9624 | 67.0259 | 66.7367 | 66.487 | 66.2778 | 66.1142 | 65.926 | 65.8469 | 60.724 | 57.2764
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | System Transformation | Headroom (MW) | N/A | 72.3759 | 72.2569 | 71.7429 | 71.386 | 70.9732 | 70.5349 | 69.7344 | 68.9572 | 65.4545 | 64.5212 | 63.5393 | 62.702 | 61.9572 | 61.2599 | 60.6453 | 60.0954 | 52.5189 | 48.6301 | 43.7481
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | 52.9256 | -1.4763 | WPD Best View | Headroom (MW) | N/A | 72.3561 | 72.0566 | 71.3241 | 70.7183 | 69.972 | 68.8601 | 67.2388 | 65.7066 | 61.6758 | 60.117 | 58.4596 | 56.9298 | 55.4537 | 48.4437 | 47.0804 | 45.5354 | 35.3439 | 23.2469 | 10.3673
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Consumer Transformation | Headroom (MW) | Thermal | 13.7353 | 13.6908 | 13.5107 | 13.3645 | 13.1431 | 12.8419 | 12.4292 | 12.033 | 11.6437 | 11.2166 | 10.7623 | 10.3414 | 9.9346 | 4.8802 | 4.4731 | 4.0049 | 1.6016 | -0.85991 | -3.2058
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Leading the Way | Headroom (MW) | N/A | 13.7365 | 13.7547 | 13.7293 | 13.7169 | 13.6 | 13.4923 | 13.2357 | 13.1818 | 13.0101 | 12.8417 | 12.6701 | 12.5193 | 12.3693 | 7.5869 | 7.4631 | 7.2955 | 6.5412 | 5.2824 | 3.8604
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | Steady Progression | Headroom (MW) | N/A | 13.7344 | 13.7324 | 13.6469 | 13.6022 | 13.5089 | 13.4225 | 13.3375 | 13.2411 | 13.1383 | 13.0331 | 12.9007 | 12.7938 | 12.6985 | 12.6057 | 12.5243 | 12.4327 | 12.1785 | 7.3551 | 6.723
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | System Transformation | Headroom (MW) | N/A | 13.7353 | 13.7545 | 13.6384 | 13.5699 | 13.413 | 13.2609 | 13.0367 | 12.8221 | 12.5714 | 12.3198 | 12.055 | 11.8232 | 11.5949 | 11.3915 | 11.2026 | 10.9855 | 5.5702 | 4.7873 | 3.8491
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | 52.925 | -1.4409 | WPD Best View | Headroom (MW) | Thermal | 13.7353 | 13.6908 | 13.5107 | 13.3645 | 13.1431 | 12.8419 | 12.4292 | 12.033 | 11.6437 | 11.2166 | 10.7623 | 10.3414 | 9.9346 | 4.8802 | 4.4731 | 4.0049 | 1.6016 | -0.85991 | -3.2058
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Consumer Transformation | Headroom (MW) | N/A | 16.136 | 16.0416 | 15.8148 | 15.6295 | 15.4356 | 15.1598 | 14.7969 | 14.4474 | 11.5623 | 11.2187 | 10.8557 | 10.5471 | 10.2483 | 9.9661 | 9.6933 | 9.3785 | 7.5285 | 4.3876 | 2.169
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Leading the Way | Headroom (MW) | N/A | 16.1373 | 16.0751 | 15.9826 | 15.8922 | 15.7954 | 15.704 | 13.0067 | 12.8952 | 12.778 | 12.6937 | 12.6273 | 12.5755 | 12.3761 | 12.1489 | 12.156 | 12.1611 | 11.6385 | 10.694 | 8.1493
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | Steady Progression | Headroom (MW) | N/A | 16.1348 | 16.0902 | 15.9844 | 15.9061 | 15.8321 | 15.7672 | 15.6919 | 15.6089 | 15.5366 | 15.4552 | 12.8011 | 12.7307 | 12.6767 | 12.6384 | 12.6135 | 12.593 | 12.6536 | 12.4356 | 11.9241
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | System Transformation | Headroom (MW) | N/A | 16.1358 | 16.0921 | 15.9306 | 15.8127 | 15.6857 | 15.5505 | 15.3416 | 15.139 | 12.3344 | 12.1197 | 11.908 | 11.7289 | 11.5841 | 11.4545 | 11.351 | 11.2627 | 11.0478 | 10.4436 | 9.5081
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | 52.9441 | -1.4857 | WPD Best View | Headroom (MW) | N/A | 16.136 | 16.0416 | 15.8148 | 15.6295 | 15.4356 | 15.1598 | 14.7969 | 14.4474 | 11.5623 | 11.2187 | 10.8557 | 10.5471 | 10.2483 | 9.9661 | 9.6933 | 9.3785 | 7.5285 | 4.3876 | 2.169
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Consumer Transformation | Headroom (MW) | N/A | 15.1015 | 15.0735 | 15.008 | 14.9751 | 14.9831 | 14.8512 | 14.6032 | 14.3702 | 14.1487 | 13.9053 | 13.6527 | 13.4035 | 13.143 | 12.902 | 12.6648 | 12.4099 | 11.1156 | 9.7459 | 8.4112
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Leading the Way | Headroom (MW) | N/A | 15.1045 | 15.0756 | 15.0121 | 14.9748 | 14.9994 | 14.9696 | 14.722 | 14.6986 | 14.6433 | 14.5583 | 14.4321 | 14.3248 | 14.2145 | 14.107 | 13.9876 | 13.867 | 13.2146 | 12.4415 | 11.6516
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | Steady Progression | Headroom (MW) | N/A | 15.0993 | 15.0692 | 15.0022 | 14.9671 | 14.9624 | 14.9291 | 14.8916 | 14.8626 | 14.8286 | 14.7964 | 14.7621 | 14.7298 | 14.6971 | 14.6658 | 14.6352 | 14.6051 | 14.4532 | 14.2601 | 13.8812
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | System Transformation | Headroom (MW) | N/A | 15.1015 | 15.0735 | 15.008 | 14.9752 | 14.9831 | 14.9513 | 14.9178 | 14.8894 | 14.7872 | 14.6679 | 14.5317 | 14.4119 | 14.2948 | 14.1813 | 14.0648 | 13.9557 | 13.4716 | 12.9383 | 12.3537
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | 52.9198 | -1.4715 | WPD Best View | Headroom (MW) | N/A | 15.1015 | 15.0735 | 15.008 | 14.9751 | 14.9831 | 14.8512 | 14.6032 | 14.3702 | 14.1487 | 13.9053 | 13.6527 | 13.4035 | 13.143 | 12.902 | 12.6648 | 12.4099 | 11.1156 | 9.7459 | 8.4112
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Consumer Transformation | Headroom (MW) | Thermal | 13.5833 | 13.4508 | 13.1906 | 12.9492 | 12.6103 | 12.2073 | 11.6096 | 11.056 | 10.5211 | 9.9764 | 9.3889 | 8.8378 | 8.3278 | 6.8954 | 6.4492 | 5.9421 | 1.2981 | -3.8268 | -10.807
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Leading the Way | Headroom (MW) | Thermal | 13.6258 | 13.5672 | 13.3954 | 13.1759 | 12.9681 | 12.7958 | 12.482 | 12.2221 | 11.9747 | 11.7647 | 11.5789 | 11.4236 | 11.2752 | 10.7544 | 9.4793 | 9.3489 | 4.1744 | -0.067178 | -6.9294
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | Steady Progression | Headroom (MW) | N/A | 13.6092 | 13.5481 | 13.4105 | 13.3299 | 13.251 | 13.2092 | 13.1421 | 13.0512 | 12.9586 | 12.8777 | 12.762 | 12.6825 | 12.6147 | 12.5678 | 12.5412 | 12.4952 | 12.7616 | 12.8732 | 10.948
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | System Transformation | Headroom (MW) | N/A | 13.6033 | 13.5368 | 13.3659 | 13.2281 | 13.0914 | 12.9722 | 12.6383 | 12.3067 | 11.9615 | 11.6138 | 11.2446 | 10.9379 | 10.6834 | 10.4326 | 10.2269 | 10.0915 | 8.6294 | 6.6609 | 4.2372
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | 52.9211 | -1.5199 | WPD Best View | Headroom (MW) | Thermal | 13.5833 | 13.4508 | 13.1906 | 12.9492 | 12.6103 | 12.2073 | 11.6096 | 11.056 | 10.5211 | 9.9764 | 9.3889 | 8.8378 | 8.3278 | 6.8954 | 6.4492 | 5.9421 | 1.2981 | -3.8268 | -10.807
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Consumer Transformation | Headroom (MW) | N/A | 77.8879 | 77.7476 | 77.3051 | 76.8479 | 76.1648 | 75.1512 | 73.7514 | 72.3697 | 71.0343 | 69.5253 | 67.8888 | 66.3328 | 64.8423 | 63.4607 | 62.1157 | 60.5959 | 53.2829 | 38.189 | 30.5075
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Leading the Way | Headroom (MW) | N/A | 77.9385 | 77.7797 | 77.4122 | 77.0783 | 76.8621 | 76.6791 | 75.7017 | 75.5986 | 75.0597 | 74.3379 | 73.6022 | 72.9728 | 72.2281 | 71.4945 | 71.3467 | 69.408 | 65.9672 | 71.0863 | 63.823
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | Steady Progression | Headroom (MW) | N/A | 77.8889 | 77.7562 | 77.3639 | 77.1464 | 76.9432 | 76.7727 | 76.5533 | 76.4138 | 76.2551 | 76.0348 | 75.7249 | 75.433 | 75.1138 | 74.8311 | 74.5987 | 74.3176 | 73.9492 | 73.3774 | 71.3644
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | System Transformation | Headroom (MW) | N/A | 77.9062 | 77.7894 | 77.3909 | 77.1431 | 76.9098 | 76.5834 | 76.0078 | 75.3524 | 74.5856 | 73.7636 | 72.8948 | 72.1447 | 71.4157 | 70.8071 | 70.2514 | 69.6244 | 67.6309 | 62.5243 | 57.5314
Willington 132kV | Derby South | Derby South | Bulk Supply Point | 33 | 52.8863 | -1.4619 | WPD Best View | Headroom (MW) | N/A | 77.8879 | 77.7476 | 77.3051 | 76.8479 | 76.1648 | 75.1512 | 73.7514 | 72.3697 | 71.0343 | 69.5253 | 67.8888 | 66.3328 | 64.8423 | 63.4607 | 62.1157 | 60.5959 | 53.2829 | 38.189 | 30.5075
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Consumer Transformation | Headroom (MW) | N/A | 31.7727 | 31.704 | 31.5548 | 31.4759 | 31.2575 | 30.8533 | 30.2996 | 29.7421 | 29.2167 | 28.6705 | 28.0736 | 27.51 | 26.9587 | 26.4229 | 25.9049 | 25.309 | 22.3355 | 19.3824 | 16.6209
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Leading the Way | Headroom (MW) | N/A | 31.7766 | 31.6729 | 31.5257 | 31.3991 | 31.3236 | 31.2497 | 30.8464 | 30.7768 | 30.594 | 30.3869 | 30.1434 | 29.9489 | 29.5862 | 29.1787 | 29.1323 | 29.0852 | 28.1021 | 26.6281 | 25.011
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | Steady Progression | Headroom (MW) | N/A | 31.7698 | 31.6983 | 31.5473 | 31.4604 | 31.3806 | 31.3019 | 31.1864 | 31.1099 | 31.0194 | 30.9424 | 30.8541 | 30.7634 | 30.6238 | 30.4803 | 30.3548 | 30.2153 | 29.7791 | 29.4237 | 28.6244
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | System Transformation | Headroom (MW) | N/A | 31.7727 | 31.7039 | 31.5546 | 31.4756 | 31.3974 | 31.3203 | 31.1269 | 30.8373 | 30.5048 | 30.1872 | 29.8469 | 29.5465 | 29.2518 | 28.9822 | 28.7318 | 28.4516 | 27.3502 | 26.3416 | 25.2156
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | 52.8939 | -1.4531 | WPD Best View | Headroom (MW) | N/A | 31.7727 | 31.704 | 31.5548 | 31.4759 | 31.2575 | 30.8533 | 30.2996 | 29.7421 | 29.2167 | 28.6705 | 28.0736 | 27.51 | 26.9587 | 26.4229 | 25.9049 | 25.309 | 22.3355 | 19.3824 | 16.6209
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Consumer Transformation | Headroom (MW) | N/A | 25.4208 | 25.3801 | 25.2653 | 25.0321 | 24.7353 | 24.3196 | 23.7081 | 23.087 | 22.4714 | 21.7955 | 21.059 | 20.3507 | 19.673 | 19.0356 | 18.411 | 17.7445 | 14.5327 | 10.0532 | 7.0271
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Leading the Way | Headroom (MW) | N/A | 25.4441 | 25.3689 | 25.2587 | 25.1424 | 25.0856 | 25.0259 | 24.489 | 24.4399 | 24.0826 | 23.6654 | 23.2679 | 22.9054 | 22.615 | 22.4095 | 22.2371 | 22.0428 | 19.5851 | 17.991 | 14.924
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | Steady Progression | Headroom (MW) | N/A | 25.4033 | 25.3565 | 25.2372 | 25.1683 | 25.1071 | 25.0477 | 24.9519 | 24.897 | 24.8288 | 24.7432 | 24.5917 | 24.4519 | 24.3207 | 24.1896 | 24.0824 | 23.9499 | 23.712 | 23.4723 | 22.6767
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | System Transformation | Headroom (MW) | N/A | 25.4207 | 25.38 | 25.265 | 25.2011 | 25.1389 | 24.9536 | 24.6433 | 24.3331 | 23.9852 | 23.6381 | 23.2818 | 22.9596 | 22.6463 | 22.3622 | 22.0921 | 21.8087 | 20.7788 | 18.4837 | 17.3048
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | 52.8992 | -1.4924 | WPD Best View | Headroom (MW) | N/A | 25.4208 | 25.3801 | 25.2653 | 25.0321 | 24.7353 | 24.3196 | 23.7081 | 23.087 | 22.4714 | 21.7955 | 21.059 | 20.3507 | 19.673 | 19.0356 | 18.411 | 17.7445 | 14.5327 | 10.0532 | 7.0271
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Consumer Transformation | Headroom (MW) | Thermal | 11.6548 | 11.6239 | 11.4454 | 11.3003 | 11.1324 | 10.9387 | 10.7042 | 10.501 | 10.3066 | 10.0198 | 9.7166 | 9.4324 | 9.171 | 8.9627 | 8.7602 | 8.5028 | 7.3751 | -0.28609 | -2.1801
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Leading the Way | Headroom (MW) | N/A | 11.6782 | 11.6984 | 11.5882 | 11.4972 | 11.4134 | 11.3639 | 11.3267 | 11.3423 | 11.3435 | 11.2461 | 11.1513 | 11.0789 | 10.9873 | 10.8667 | 10.9377 | 9.2405 | 9.2404 | 3.0733 | 0.49421
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | Steady Progression | Headroom (MW) | N/A | 11.6762 | 11.6618 | 11.5397 | 11.4781 | 11.4159 | 11.3835 | 11.3754 | 11.3673 | 11.3673 | 11.3095 | 11.2395 | 11.178 | 11.1296 | 11.1216 | 11.1218 | 11.1128 | 11.4185 | 11.4418 | 11.0237
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | System Transformation | Headroom (MW) | N/A | 11.6732 | 11.6659 | 11.5317 | 11.4267 | 11.3339 | 11.2699 | 11.198 | 11.1424 | 11.0559 | 10.8988 | 10.7265 | 10.599 | 10.478 | 10.4232 | 10.3879 | 10.3245 | 10.4623 | 8.6593 | 5.9715
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | 52.8877 | -1.4745 | WPD Best View | Headroom (MW) | Thermal | 11.6548 | 11.6239 | 11.4454 | 11.3003 | 11.1324 | 10.9387 | 10.7042 | 10.501 | 10.3066 | 10.0198 | 9.7166 | 9.4324 | 9.171 | 8.9627 | 8.7602 | 8.5028 | 7.3751 | -0.28609 | -2.1801
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Consumer Transformation | Headroom (MW) | Thermal | 61.3682 | 60.9614 | 60.2022 | 59.4878 | 58.6047 | 57.4012 | 55.6694 | 53.9177 | 52.2256 | 50.4904 | 48.5788 | 46.7747 | 44.1711 | 38.3151 | 36.7636 | 34.9787 | 20.0724 | -2.3998 | -24.0976
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Leading the Way | Headroom (MW) | N/A | 61.428 | 61.069 | 60.5191 | 60.0705 | 59.6954 | 59.3147 | 58.0949 | 57.7057 | 56.9719 | 56.5716 | 55.9327 | 55.1509 | 54.2999 | 50.9418 | 50.7553 | 43.0948 | 36.0027 | 24.1454 | 7.94
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | Steady Progression | Headroom (MW) | N/A | 61.4165 | 61.1109 | 60.5443 | 60.198 | 59.8697 | 59.5438 | 58.1355 | 54.7542 | 53.3952 | 52.0405 | 50.303 | 48.7014 | 48.3593 | 48.0456 | 47.7636 | 47.46 | 46.5499 | 43.3264 | 40.5603
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | System Transformation | Headroom (MW) | N/A | 61.4084 | 61.0916 | 60.4706 | 60.0364 | 59.5872 | 59.0492 | 58.0863 | 57.2311 | 56.204 | 55.2371 | 54.158 | 53.1875 | 52.3894 | 51.6747 | 51.0373 | 50.316 | 45.3477 | 33.3152 | 21.1817
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | 53.0213 | -1.3627 | WPD Best View | Headroom (MW) | Thermal | 61.3682 | 60.9614 | 60.2022 | 59.4878 | 58.6047 | 57.4012 | 55.6703 | 53.9199 | 52.2295 | 50.4973 | 48.5898 | 46.7898 | 44.1904 | 38.3385 | 36.7899 | 35.0029 | 20.0629 | -2.4494 | -24.1922
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Consumer Transformation | Headroom (MW) | N/A | 14.8354 | 14.7858 | 14.6978 | 14.6107 | 14.5133 | 14.3864 | 14.2171 | 14.0995 | 13.9811 | 13.8688 | 13.7288 | 13.5636 | 13.4143 | 13.2747 | 13.1665 | 13.0194 | 11.1999 | 8.9629 | 5.7973
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Leading the Way | Headroom (MW) | N/A | 14.8366 | 14.7963 | 14.7755 | 14.7185 | 14.6639 | 14.6065 | 14.5226 | 14.5209 | 14.4912 | 14.4952 | 14.5105 | 14.4747 | 14.4183 | 14.2929 | 14.3139 | 12.6818 | 11.38 | 9.5282 | 7.5947
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | Steady Progression | Headroom (MW) | N/A | 14.8344 | 14.8024 | 14.7531 | 14.7092 | 14.6666 | 14.6276 | 14.5783 | 14.5649 | 14.5472 | 14.5361 | 14.5147 | 14.4751 | 14.4396 | 14.4182 | 14.4072 | 14.3801 | 14.3178 | 14.2487 | 13.9872
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | System Transformation | Headroom (MW) | N/A | 14.8354 | 14.804 | 14.7498 | 14.6853 | 14.6178 | 14.5471 | 14.4518 | 14.4104 | 14.3527 | 14.2991 | 14.2424 | 14.1597 | 14.0939 | 14.0227 | 13.999 | 13.9467 | 13.713 | 12.1247 | 10.4284
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | 53.0157 | -1.4299 | WPD Best View | Headroom (MW) | N/A | 14.8354 | 14.7858 | 14.6978 | 14.6107 | 14.5133 | 14.3864 | 14.2171 | 14.0995 | 13.9811 | 13.8688 | 13.7288 | 13.5636 | 13.4143 | 13.2747 | 13.1665 | 13.0194 | 11.1999 | 8.9629 | 5.7973
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Consumer Transformation | Headroom (MW) | Thermal | 12.4408 | 12.2814 | 12.0027 | 11.7609 | 11.5098 | 11.1522 | 10.6544 | 10.1643 | 9.6836 | 9.1796 | 8.643 | 8.12 | 7.6111 | 7.1154 | 6.6212 | 6.0811 | 3.305 | -0.73661 | -3.3358
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Leading the Way | Headroom (MW) | N/A | 12.4751 | 12.3786 | 12.1949 | 12.0629 | 11.9305 | 11.801 | 11.5748 | 11.3712 | 11.1259 | 10.9167 | 10.6986 | 10.5142 | 10.3411 | 10.1704 | 10.0264 | 9.8301 | 7.5613 | 12.1404 | 10.76
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | Steady Progression | Headroom (MW) | N/A | 12.4761 | 12.3864 | 12.2181 | 12.114 | 12.0208 | 11.9224 | 10.7976 | 8.6419 | 7.4973 | 6.3542 | 5.2975 | 4.3323 | 4.214 | 4.1075 | 4.0123 | 3.9089 | 3.5843 | 3.3146 | 2.6878
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | System Transformation | Headroom (MW) | N/A | 12.4666 | 12.3613 | 12.163 | 12.0044 | 11.8376 | 11.6687 | 11.3899 | 11.1319 | 10.817 | 10.525 | 10.2136 | 9.9298 | 9.6727 | 9.4203 | 9.1903 | 8.9353 | 7.9612 | 5.7667 | 4.7869
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | 53.0211 | -1.3625 | WPD Best View | Headroom (MW) | Thermal | 12.4408 | 12.2814 | 12.0027 | 11.7609 | 11.5098 | 11.1522 | 10.6544 | 10.1643 | 9.6836 | 9.1796 | 8.643 | 8.12 | 7.6111 | 7.1154 | 6.6212 | 6.0811 | 3.305 | -0.73661 | -3.3358
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Consumer Transformation | Headroom (MW) | Thermal | 13.1542 | 13.1229 | 13.05 | 12.9664 | 12.8074 | 12.5845 | 12.2603 | 11.9505 | 11.6657 | 11.3724 | 11.0488 | 10.7695 | 10.5022 | 7.8409 | 7.5836 | 7.2823 | 5.6024 | 2.2777 | -0.70429
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Leading the Way | Headroom (MW) | N/A | 13.1571 | 13.1059 | 13.0349 | 12.9659 | 12.9273 | 12.8892 | 12.6632 | 12.6279 | 12.5345 | 12.5068 | 12.4101 | 12.2197 | 12.0304 | 9.5077 | 9.5074 | 9.5065 | 8.0388 | 5.5335 | 4.0751
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | Steady Progression | Headroom (MW) | N/A | 13.1519 | 13.1182 | 13.0434 | 12.9985 | 12.9575 | 12.9168 | 12.8545 | 12.8146 | 12.7677 | 12.729 | 12.6839 | 12.647 | 12.6071 | 12.5669 | 12.5307 | 12.5004 | 12.3498 | 9.8298 | 9.3587
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | System Transformation | Headroom (MW) | N/A | 13.1541 | 13.1226 | 13.0494 | 13.0088 | 12.9683 | 12.9142 | 12.7374 | 12.5747 | 12.3738 | 12.1886 | 12.0091 | 11.8434 | 11.7169 | 11.5988 | 11.4986 | 11.402 | 8.6844 | 6.8519 | 5.9647
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | 53.0231 | -1.2954 | WPD Best View | Headroom (MW) | Thermal | 13.1542 | 13.1229 | 13.05 | 12.9664 | 12.8074 | 12.5845 | 12.2603 | 11.9505 | 11.6657 | 11.3724 | 11.0488 | 10.7695 | 10.5022 | 7.8409 | 7.5836 | 7.2823 | 5.6024 | 2.2777 | -0.70429
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Consumer Transformation | Headroom (MW) | Thermal | 8.3891 | 8.3641 | 8.3152 | 8.2906 | 8.2671 | 8.2436 | 8.1752 | 8.1019 | 8.0341 | 7.9867 | 7.9121 | 7.8584 | 6.892 | 5.9354 | 5.931 | 5.9132 | 3.5388 | -0.90521 | -5.467
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Leading the Way | Headroom (MW) | Thermal | 8.3894 | 8.3586 | 8.3096 | 8.2782 | 8.2554 | 8.2326 | 8.1572 | 8.1367 | 8.0931 | 8.0804 | 8.0412 | 7.9696 | 7.8976 | 7.8215 | 7.8322 | 5.309 | 1.932 | -2.0034 | -5.5914
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | Steady Progression | Headroom (MW) | N/A | 8.3886 | 8.3634 | 8.3139 | 8.2872 | 8.262 | 8.2366 | 8.2051 | 8.1801 | 8.1537 | 8.1299 | 8.1048 | 8.0825 | 8.0603 | 8.0402 | 8.0216 | 8.0047 | 7.9408 | 7.8574 | 7.6471
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | System Transformation | Headroom (MW) | N/A | 8.3889 | 8.3638 | 8.3143 | 8.2892 | 8.2647 | 8.2398 | 8.2125 | 8.1878 | 8.1459 | 8.1012 | 8.0405 | 8.0146 | 8.0076 | 8.033 | 8.0374 | 8.0306 | 8.0148 | 5.6009 | 1.6109
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | 52.9685 | -1.4137 | WPD Best View | Headroom (MW) | Thermal | 8.3891 | 8.3641 | 8.3152 | 8.2906 | 8.2671 | 8.2436 | 8.1752 | 8.1019 | 8.0341 | 7.9867 | 7.9121 | 7.8584 | 6.892 | 5.9354 | 5.931 | 5.9132 | 3.5388 | -0.90521 | -5.467
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Consumer Transformation | Headroom (MW) | Thermal | 7.8699 | 7.7973 | 7.6998 | 7.565 | 7.426 | 7.214 | 6.9022 | 6.588 | 6.2598 | 5.9082 | 5.5339 | 5.1549 | 4.7825 | 4.4107 | 4.0374 | 3.644 | 0.7373 | -2.6105 | -5.8907
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Leading the Way | Headroom (MW) | N/A | 7.8383 | 7.8109 | 7.768 | 7.7131 | 7.6568 | 7.5887 | 7.4481 | 7.3119 | 7.1384 | 6.9717 | 6.7979 | 6.6373 | 6.4653 | 6.3016 | 6.1509 | 4.5491 | 8.2028 | 4.9819 | 2.6542
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | Steady Progression | Headroom (MW) | N/A | 6.534 | 6.5134 | 6.4983 | 6.4832 | 6.4628 | 6.4486 | 6.4247 | 5.1995 | 5.1616 | 5.1208 | 4.612 | 4.149 | 4.106 | 4.0573 | 4.0091 | 3.9598 | 3.7278 | 3.5032 | 3.259
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | System Transformation | Headroom (MW) | N/A | 7.6162 | 7.586 | 7.5411 | 7.483 | 7.4198 | 7.3436 | 7.1961 | 7.0543 | 6.8806 | 6.7081 | 6.5266 | 6.3577 | 6.1892 | 6.0207 | 5.852 | 5.6706 | 4.8707 | 3.2529 | 1.4896
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | 53.0575 | -1.4065 | WPD Best View | Headroom (MW) | Thermal | 7.4812 | 7.4121 | 7.3194 | 7.1913 | 7.0592 | 6.8576 | 6.5613 | 6.2625 | 5.9505 | 5.6163 | 5.2605 | 4.9002 | 4.5463 | 4.1928 | 3.8379 | 3.464 | 0.70087 | -2.6105 | -5.8907
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Consumer Transformation | Headroom (MW) | N/A | 14.2905 | 14.2665 | 14.2132 | 14.1864 | 14.1591 | 14.1335 | 14.0771 | 13.9136 | 13.7688 | 13.6121 | 13.4344 | 13.2639 | 13.1453 | 12.1163 | 12.0011 | 11.8564 | 10.9617 | 8.8579 | 6.6829
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Leading the Way | Headroom (MW) | N/A | 14.2916 | 14.2572 | 14.2046 | 14.1634 | 14.1368 | 14.1127 | 13.9808 | 13.9565 | 13.8896 | 13.8699 | 13.8011 | 13.6833 | 13.5835 | 13.4919 | 13.4956 | 13.4972 | 12.3045 | 11.9125 | 8.9252
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | Steady Progression | Headroom (MW) | N/A | 14.2895 | 14.2641 | 14.2098 | 14.1797 | 14.151 | 14.1236 | 14.0846 | 14.0567 | 14.0252 | 13.9981 | 13.9678 | 13.9419 | 13.9281 | 13.9198 | 13.8993 | 13.88 | 13.793 | 13.676 | 13.3907
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | System Transformation | Headroom (MW) | N/A | 14.2904 | 14.2663 | 14.2127 | 14.1856 | 14.1576 | 14.1312 | 14.1012 | 14.0737 | 14.0448 | 14.0185 | 13.9288 | 13.8411 | 13.7977 | 13.7727 | 13.7334 | 13.6856 | 13.6196 | 13.3066 | 12.7547
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | 53.008 | -1.2505 | WPD Best View | Headroom (MW) | N/A | 14.2905 | 14.2665 | 14.2132 | 14.1865 | 14.1591 | 14.1336 | 14.078 | 13.9158 | 13.7727 | 13.6191 | 13.4454 | 13.279 | 13.1646 | 12.1398 | 12.0274 | 11.8806 | 10.9522 | 8.8082 | 6.5883
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Consumer Transformation | Headroom (MW) | N/A | 15.2146 | 15.1392 | 15.0049 | 14.8818 | 14.7643 | 14.6019 | 14.3839 | 14.1777 | 13.9783 | 13.777 | 13.5569 | 13.3725 | 13.19 | 13.0259 | 12.8595 | 12.6581 | 10.4397 | 7.5564 | 4.6224
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Leading the Way | Headroom (MW) | N/A | 15.2344 | 15.1869 | 15.0964 | 15.0444 | 14.9884 | 14.923 | 14.8429 | 14.7799 | 14.718 | 14.6724 | 14.6293 | 14.6071 | 14.5189 | 14.3417 | 14.3372 | 12.8832 | 12.3857 | 7.8547 | 5.3246
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | Steady Progression | Headroom (MW) | N/A | 15.2326 | 15.1756 | 15.0889 | 15.0405 | 14.9882 | 14.938 | 14.8977 | 14.847 | 14.8035 | 14.7476 | 14.6889 | 14.6376 | 14.6161 | 14.587 | 14.5735 | 14.5469 | 14.6061 | 14.6802 | 14.248
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | System Transformation | Headroom (MW) | N/A | 15.2293 | 15.1721 | 15.0632 | 14.9899 | 14.913 | 14.821 | 14.6941 | 14.5663 | 14.4339 | 14.3063 | 14.1729 | 14.0698 | 13.9835 | 13.9133 | 13.8555 | 13.7939 | 13.6425 | 11.9545 | 9.9488
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | 53.0564 | -1.315 | WPD Best View | Headroom (MW) | N/A | 15.2146 | 15.1392 | 15.0049 | 14.8818 | 14.7643 | 14.6019 | 14.3839 | 14.1777 | 13.9783 | 13.777 | 13.5569 | 13.3725 | 13.19 | 13.0259 | 12.8595 | 12.6581 | 10.4397 | 7.5564 | 4.6224
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Consumer Transformation | Headroom (MW) | Thermal | 41.8231 | 41.7652 | 41.2238 | 40.6527 | 39.8041 | 38.9686 | 35.7986 | 32.1313 | 28.8318 | 25.2292 | 21.9714 | 16.0676 | 12.0741 | 8.0683 | 3.892 | -0.57589 | -33.628 | -66.5863 | -98.5063
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Leading the Way | Headroom (MW) | Thermal | 41.6054 | 41.6172 | 41.2076 | 41.1672 | 40.9809 | 41.1275 | 38.1821 | 35.5614 | 32.8304 | 30.1608 | 27.7412 | 23.6342 | 20.3245 | 15.723 | 10.1064 | 0.7576 | -34.4955 | -22.4876 | -56.5636
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | Steady Progression | Headroom (MW) | Thermal | 41.7471 | 41.6587 | 41.1947 | 41.105 | 40.9077 | 40.9727 | 40.161 | 38.9176 | 37.9981 | 36.6441 | 35.6955 | 33.3666 | 30.9665 | 28.591 | 26.4199 | 24.1312 | 12.0884 | -3.0737 | -14.8855
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | System Transformation | Headroom (MW) | Thermal | 41.8224 | 41.7932 | 41.3526 | 41.2936 | 40.9088 | 40.7219 | 39.6858 | 38.8088 | 37.4813 | 36.5582 | 35.5035 | 32.6518 | 29.6867 | 26.7924 | 24.3941 | 21.7956 | 7.5072 | -16.0773 | -40.3311
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | 52.9065 | -1.3983 | WPD Best View | Headroom (MW) | Thermal | 41.8277 | 41.8041 | 41.3286 | 40.8247 | 40.0418 | 39.3021 | 37.7635 | 36.2619 | 34.7725 | 33.3287 | 31.9256 | 29.718 | 28.359 | 27.017 | 25.0672 | 23.7844 | 9.9002 | -11.1838 | -31.8052
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Consumer Transformation | Headroom (MW) | Thermal | 15.534 | 15.4886 | 15.3999 | 15.188 | 14.9423 | 14.5967 | 14.106 | 13.6193 | 13.1466 | 12.6532 | 12.2811 | 11.9598 | 11.4947 | 11.0224 | 10.7625 | 10.3064 | 6.1452 | 2.2477 | -2.4975
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Leading the Way | Headroom (MW) | N/A | 15.5341 | 15.4651 | 15.3767 | 15.298 | 15.2509 | 15.205 | 14.8278 | 14.7852 | 14.6805 | 14.5237 | 14.5915 | 14.664 | 14.4725 | 14.2441 | 14.4451 | 12.9535 | 9.8381 | 8.5233 | 5.8173
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | Steady Progression | Headroom (MW) | N/A | 15.5339 | 15.4885 | 15.3996 | 15.3468 | 15.2986 | 15.2511 | 15.1805 | 15.1343 | 15.0809 | 15.0038 | 14.9803 | 14.9826 | 14.9089 | 14.8376 | 14.8928 | 14.8443 | 14.6472 | 14.6577 | 14.2319
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | System Transformation | Headroom (MW) | N/A | 15.534 | 15.4886 | 15.3996 | 15.3507 | 15.28 | 15.1169 | 14.8372 | 14.5696 | 14.2627 | 13.9636 | 13.8312 | 13.7481 | 13.5116 | 13.2906 | 13.2958 | 13.1268 | 12.2703 | 10.2648 | 8.0548
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | 53.0154 | -1.4767 | WPD Best View | Headroom (MW) | Thermal | 15.534 | 15.4886 | 15.3999 | 15.188 | 14.9423 | 14.5967 | 14.106 | 13.6193 | 13.1466 | 12.6532 | 12.2811 | 11.9598 | 11.4947 | 11.0224 | 10.7625 | 10.3064 | 6.1452 | 2.2477 | -2.4975
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Consumer Transformation | Headroom (MW) | Thermal | 10.6115 | 10.582 | 10.4448 | 10.3465 | 10.2408 | 10.1881 | 10.0263 | 9.8552 | 9.6866 | 9.5217 | 9.3417 | 8.1423 | 7.9886 | 7.8436 | 7.7147 | 6.6542 | 5.7983 | 2.4592 | -0.0084582
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Leading the Way | Headroom (MW) | N/A | 10.6193 | 10.6189 | 10.5135 | 10.4375 | 10.3716 | 10.3951 | 10.3129 | 10.2062 | 10.0847 | 9.9879 | 9.889 | 8.7938 | 8.7473 | 8.7204 | 7.0237 | 6.9875 | 4.7008 | 2.5779 | 0.32706
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | Steady Progression | Headroom (MW) | N/A | 10.6123 | 10.5939 | 10.489 | 10.4396 | 10.3837 | 10.3896 | 10.345 | 10.2915 | 10.2468 | 10.192 | 10.1476 | 10.0985 | 10.0632 | 10.0258 | 9.9991 | 9.9704 | 9.96 | 8.9245 | 8.5362
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | System Transformation | Headroom (MW) | N/A | 10.613 | 10.5967 | 10.4878 | 10.4215 | 10.3546 | 10.3489 | 10.2611 | 10.1627 | 10.0577 | 9.973 | 9.8801 | 9.8078 | 9.7248 | 9.6618 | 9.6185 | 9.5711 | 8.4317 | 6.7831 | 4.8927
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | 52.841 | -1.3617 | WPD Best View | Headroom (MW) | N/A | 10.6145 | 10.5994 | 10.4939 | 10.4309 | 10.3689 | 10.3692 | 10.2893 | 10.2009 | 10.108 | 10.0369 | 9.9597 | 9.9053 | 9.8419 | 9.7956 | 9.7649 | 9.7186 | 8.4719 | 6.6778 | 4.726
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Consumer Transformation | Headroom (MW) | N/A | 15.5553 | 15.5136 | 15.4323 | 15.3892 | 15.3246 | 15.2189 | 15.08 | 14.9549 | 14.8429 | 14.737 | 14.6088 | 14.5046 | 14.4253 | 14.3469 | 13.3446 | 13.2519 | 12.5186 | 7.0558 | 5.908
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Leading the Way | Headroom (MW) | N/A | 15.5554 | 15.5065 | 15.4254 | 15.3737 | 15.3306 | 15.2887 | 15.1901 | 15.1518 | 15.0889 | 15.0578 | 14.99 | 14.9151 | 14.8306 | 14.7326 | 14.7239 | 13.5963 | 11.0597 | 8.9962 | 3.6384
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | Steady Progression | Headroom (MW) | N/A | 15.5552 | 15.5132 | 15.4315 | 15.3862 | 15.342 | 15.2982 | 15.248 | 15.2057 | 15.1617 | 15.1209 | 15.0785 | 15.0396 | 15.0006 | 14.964 | 14.9289 | 14.8955 | 14.7368 | 14.5834 | 14.2982
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | System Transformation | Headroom (MW) | N/A | 15.5552 | 15.5132 | 15.4316 | 15.388 | 15.344 | 15.3004 | 15.2301 | 15.1468 | 15.0428 | 14.9576 | 14.885 | 14.8261 | 14.7669 | 14.7366 | 14.7259 | 14.7121 | 14.7372 | 11.8799 | 11.3378
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | 52.8092 | -1.4337 | WPD Best View | Headroom (MW) | N/A | 15.5553 | 15.5134 | 15.4319 | 15.3886 | 15.3122 | 15.2011 | 15.0639 | 14.9282 | 14.8037 | 14.6831 | 14.5478 | 14.433 | 14.3324 | 14.2417 | 13.2393 | 13.156 | 12.5851 | 8.2279 | 7.1838
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Consumer Transformation | Headroom (MW) | Thermal | 5.8763 | 5.9071 | 5.8675 | 5.8473 | 5.8237 | 6.0539 | 4.5472 | 2.4946 | 0.76192 | -1.2586 | -2.9514 | -5.4485 | -7.9232 | -10.4239 | -12.4451 | -14.4635 | -34.1244 | -45.7053 | -57.9222
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Leading the Way | Headroom (MW) | Thermal | 5.8799 | 5.929 | 5.9122 | 5.9024 | 5.8952 | 6.2362 | 4.3004 | 2.2476 | 0.21692 | -1.8089 | -3.8119 | -6.5866 | -9.3793 | -12.1774 | -15.2219 | -18.2759 | -37.6849 | -54.1839 | -69.8385
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | Steady Progression | Headroom (MW) | Thermal | 5.8742 | 5.8921 | 5.8681 | 5.8623 | 5.8608 | 6.0455 | 5.5136 | 4.4806 | 3.8401 | 2.8219 | 2.1819 | 0.093895 | -1.9936 | -4.0894 | -6.133 | -8.1761 | -19.7876 | -32.3049 | -41.6616
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | System Transformation | Headroom (MW) | Thermal | 5.874 | 5.9033 | 5.8777 | 5.8616 | 5.8457 | 6.0891 | 5.9334 | 5.9272 | 5.6039 | 5.6259 | 5.3266 | 3.1137 | 0.91274 | -1.304 | -3.3428 | -5.3751 | -15.3808 | -27.3131 | -40.365
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | 52.8613 | -1.2615 | WPD Best View | Headroom (MW) | N/A | 5.877 | 5.9097 | 5.8823 | 5.868 | 5.8552 | 6.0903 | 6.073 | 6.0495 | 6.0232 | 6.0338 | 6.041 | 6.0537 | 6.0843 | 6.103 | 6.1327 | 6.1829 | 5.2767 | 2.228 | 0.12454
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Consumer Transformation | Headroom (MW) | Thermal | 26.7855 | 26.8432 | 26.74 | 26.4416 | 26.1152 | 25.658 | 24.9271 | 24.2211 | 23.5241 | 22.8326 | 22.0649 | 20.406 | 19.703 | 19.0096 | 18.3694 | 17.6678 | 10.8523 | 3.2693 | -5.6907
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Leading the Way | Headroom (MW) | Thermal | 26.8056 | 26.8645 | 26.8339 | 26.7854 | 26.8164 | 26.7427 | 26.3559 | 26.0236 | 25.646 | 25.3411 | 25.0684 | 24.8756 | 24.7035 | 23.276 | 22.2343 | 18.6416 | 12.4314 | 6.1369 | -1.1867
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | Steady Progression | Headroom (MW) | N/A | 26.7703 | 26.7891 | 26.6939 | 26.6559 | 26.637 | 26.6251 | 26.5182 | 26.4614 | 26.3475 | 26.2044 | 26.0336 | 25.8904 | 25.754 | 25.6372 | 25.5365 | 25.4256 | 25.4115 | 23.9965 | 22.9709
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | System Transformation | Headroom (MW) | N/A | 26.7854 | 26.8429 | 26.7754 | 26.764 | 26.6367 | 26.4796 | 26.12 | 25.7594 | 25.3473 | 24.9491 | 24.5493 | 24.196 | 23.8681 | 23.5627 | 23.2982 | 23.0081 | 20.8799 | 16.1425 | 11.3999
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | 52.9065 | -1.3985 | WPD Best View | Headroom (MW) | Thermal | 26.7855 | 26.8431 | 26.7369 | 26.4369 | 26.1081 | 25.6478 | 24.9129 | 24.202 | 23.4989 | 22.8007 | 22.0251 | 20.3573 | 19.6454 | 18.9437 | 18.2972 | 17.5952 | 10.8326 | 3.3224 | -5.6069
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Consumer Transformation | Headroom (MW) | N/A | 14.8224 | 14.7927 | 14.7013 | 14.8022 | 14.7194 | 14.6152 | 14.474 | 14.3482 | 14.2317 | 14.1052 | 13.9884 | 13.8654 | 13.7476 | 13.6317 | 13.5079 | 13.3692 | 12.544 | 11.4489 | 9.0666
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Leading the Way | Headroom (MW) | N/A | 14.573 | 14.5952 | 14.5079 | 14.7321 | 14.6782 | 14.6218 | 14.557 | 14.509 | 14.4755 | 14.4212 | 14.3761 | 14.3343 | 14.3118 | 14.2892 | 14.2633 | 14.2167 | 12.5214 | 11.812 | 11.0288
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | Steady Progression | Headroom (MW) | N/A | 14.7633 | 14.7439 | 14.6746 | 14.7762 | 14.7476 | 14.7252 | 14.7178 | 14.7061 | 14.6832 | 14.6631 | 14.6356 | 14.6236 | 14.5954 | 14.5778 | 14.5577 | 14.5336 | 14.4826 | 14.431 | 14.1009
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | System Transformation | Headroom (MW) | N/A | 14.8228 | 14.8105 | 14.7425 | 14.8697 | 14.8099 | 14.7489 | 14.6661 | 14.6051 | 14.5289 | 14.451 | 14.3932 | 14.3221 | 14.2646 | 14.2067 | 14.1605 | 14.1146 | 13.9309 | 13.5275 | 11.7107
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | 52.8503 | -1.3453 | WPD Best View | Headroom (MW) | N/A | 14.8236 | 14.8118 | 14.7456 | 14.8744 | 14.8171 | 14.759 | 14.6802 | 14.6241 | 14.554 | 14.4829 | 14.433 | 14.3708 | 14.3221 | 14.2726 | 14.2327 | 14.1873 | 13.9506 | 13.4744 | 11.6268
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Consumer Transformation | Headroom (MW) | Thermal | 39.3339 | 38.9745 | 38.3157 | 37.7143 | 37.1135 | 36.2764 | 35.1011 | 33.9379 | 32.8121 | 31.5788 | 30.2746 | 29.0252 | 27.8011 | 26.65 | 25.5971 | 24.3753 | 17.0674 | 4.6047 | -5.0226
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Leading the Way | Headroom (MW) | N/A | 39.4412 | 39.1727 | 38.7284 | 38.4298 | 38.1141 | 37.8222 | 37.2973 | 36.7908 | 36.2243 | 35.6467 | 35.0323 | 34.5153 | 34.0684 | 33.6605 | 33.5008 | 33.1315 | 25.6209 | 33.7056 | 22.3832
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | Steady Progression | Headroom (MW) | Thermal | 39.4173 | 39.205 | 38.8046 | 38.5862 | 38.3576 | 38.1628 | 34.872 | 29.4738 | 26.141 | 22.7881 | 19.5725 | 16.6599 | 13.3601 | 10.0846 | 8.3113 | 6.0888 | 0.1604 | -8.308 | -12.1409
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | System Transformation | Headroom (MW) | N/A | 39.4108 | 39.1569 | 38.6873 | 38.3568 | 37.9534 | 37.5699 | 36.9221 | 36.2885 | 35.5821 | 34.8979 | 34.2159 | 33.6039 | 33.0519 | 32.5726 | 32.2167 | 31.7505 | 30.2633 | 25.5427 | 20.035
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | 52.948 | -1.3129 | WPD Best View | Headroom (MW) | Thermal | 39.3366 | 38.9774 | 38.3233 | 37.7347 | 37.137 | 36.3101 | 35.128 | 33.9797 | 32.8586 | 31.6363 | 30.3189 | 29.0623 | 27.8239 | 26.6464 | 25.5655 | 24.3139 | 16.9804 | 4.4635 | -5.2363
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Consumer Transformation | Headroom (MW) | Fault level | -25.0497 | -25.1562 | -25.2985 | -25.4702 | -25.6394 | -25.8967 | -26.2715 | -26.6509 | -27.035 | -27.4771 | -27.9658 | -28.4491 | -28.9474 | -29.4165 | -29.8866 | -30.3871 | -32.7525 | -37.9116 | -40.9338
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Leading the Way | Headroom (MW) | Fault level | -24.8646 | -24.974 | -25.0549 | -25.1503 | -25.2251 | -25.3185 | -25.4787 | -25.6409 | -25.8435 | -26.0897 | -26.3868 | -26.6547 | -26.8817 | -27.1275 | -27.3061 | -27.512 | -30.5794 | -11.3693 | -15.2969
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | Steady Progression | Headroom (MW) | Fault level | -20.6901 | -20.7172 | -20.7501 | -20.7759 | -20.791 | -20.8124 | -24.4311 | -30.4609 | -34.095 | -37.7428 | -41.2012 | -44.3658 | -48.0189 | -51.6727 | -53.673 | -56.1471 | -63.2295 | -73.1144 | -75.889
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | System Transformation | Headroom (MW) | Fault level | -24.1611 | -24.2205 | -24.2825 | -24.3587 | -24.4346 | -24.5269 | -24.6903 | -24.855 | -25.0579 | -25.2677 | -25.4876 | -25.7011 | -25.9031 | -26.1142 | -26.3169 | -26.5489 | -27.508 | -29.2905 | -30.945
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | 52.9758 | -1.3249 | WPD Best View | Headroom (MW) | Fault level | -23.8122 | -23.9135 | -24.0487 | -24.2119 | -24.3728 | -24.6173 | -24.9736 | -25.3343 | -25.6994 | -26.1197 | -26.5842 | -27.0436 | -27.5174 | -27.9632 | -28.4101 | -28.8859 | -31.1345 | -36.0386 | -38.9116
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Consumer Transformation | Headroom (MW) | N/A | 17.9833 | 17.8649 | 17.6351 | 17.4202 | 17.211 | 16.9067 | 16.4929 | 16.0602 | 15.6501 | 15.2004 | 14.7152 | 14.2342 | 13.7493 | 13.3214 | 12.9842 | 12.5329 | 9.3178 | 4.5194 | 0.59449
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Leading the Way | Headroom (MW) | N/A | 18.0169 | 17.9484 | 17.8041 | 17.6998 | 17.5808 | 17.4651 | 17.2568 | 17.0447 | 16.805 | 16.5562 | 16.2825 | 16.0443 | 15.7902 | 15.6063 | 15.5894 | 15.4211 | 11.94 | 9.4165 | 4.1156
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | Steady Progression | Headroom (MW) | N/A | 18.011 | 17.9362 | 17.8084 | 17.732 | 17.6552 | 17.5904 | 17.521 | 17.4266 | 17.3398 | 17.2548 | 17.1331 | 17.0418 | 16.961 | 16.9089 | 16.9064 | 16.8519 | 16.8611 | 16.7605 | 16.1043
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | System Transformation | Headroom (MW) | N/A | 18.0068 | 17.9282 | 17.7681 | 17.6626 | 17.5201 | 17.3859 | 17.1494 | 16.9318 | 16.6927 | 16.4551 | 16.2106 | 15.997 | 15.7914 | 15.6429 | 15.5731 | 15.4065 | 14.9354 | 12.8542 | 10.4311
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | 52.9598 | -1.3091 | WPD Best View | Headroom (MW) | N/A | 17.9861 | 17.8678 | 17.6427 | 17.4407 | 17.2344 | 16.9404 | 16.5198 | 16.102 | 15.6967 | 15.2579 | 14.7596 | 14.2713 | 13.7721 | 13.3179 | 12.9526 | 12.4715 | 9.2309 | 4.3782 | 0.38087
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Consumer Transformation | Headroom (MW) | N/A | 15.0961 | 15 | 14.8374 | 14.6848 | 14.5323 | 14.3167 | 14.0136 | 13.7305 | 13.4528 | 13.1508 | 12.838 | 12.5552 | 12.3021 | 12.0246 | 11.7506 | 11.4611 | 9.8022 | 7.9036 | 6.024
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Leading the Way | Headroom (MW) | N/A | 15.1315 | 15.0687 | 14.9548 | 14.8958 | 14.8257 | 14.7653 | 14.6506 | 14.5434 | 14.4309 | 14.3317 | 14.2366 | 14.1612 | 14.1068 | 14.0347 | 13.9733 | 13.9054 | 13.3401 | 10.9975 | 9.7288
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | Steady Progression | Headroom (MW) | N/A | 15.1292 | 15.0676 | 14.9624 | 14.9111 | 14.8434 | 14.7947 | 14.7365 | 14.67 | 14.609 | 14.5322 | 14.455 | 14.3991 | 14.3549 | 14.2966 | 14.2618 | 14.2387 | 14.2074 | 14.1524 | 13.6939
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | System Transformation | Headroom (MW) | N/A | 15.1259 | 15.049 | 14.9267 | 14.8412 | 14.733 | 14.6319 | 14.463 | 14.2897 | 14.1 | 13.9225 | 13.7398 | 13.5849 | 13.4569 | 13.3337 | 13.2268 | 13.1231 | 12.7429 | 12.1915 | 11.4163
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | 52.9228 | -1.2964 | WPD Best View | Headroom (MW) | N/A | 15.0961 | 15 | 14.8374 | 14.6848 | 14.5323 | 14.3167 | 14.0136 | 13.7305 | 13.4528 | 13.1508 | 12.838 | 12.5552 | 12.3021 | 12.0246 | 11.7506 | 11.4611 | 9.8022 | 7.9036 | 6.024
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Consumer Transformation | Headroom (MW) | Thermal | 9.8115 | 9.6339 | 9.3779 | 9.168 | 9.0042 | 8.6542 | 8.2465 | 7.8694 | 7.5224 | 7.1535 | 5.8007 | 5.4557 | 4.1822 | 2.0336 | 0.90343 | 6.2389 | -5.0516 | -21.3092 | -36.7293
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Leading the Way | Headroom (MW) | Thermal | 9.86 | 9.7231 | 9.5596 | 9.4988 | 9.4602 | 9.2811 | 9.1628 | 9.0441 | 8.9436 | 8.8874 | 8.8097 | 8.8546 | 7.9971 | 5.5475 | 1.3853 | -2.4038 | -14.6228 | -33.8965 | -50.3206
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | Steady Progression | Headroom (MW) | N/A | 9.8494 | 9.7139 | 9.5149 | 9.4333 | 9.3853 | 9.2704 | 9.2006 | 9.1086 | 9.0056 | 8.9035 | 8.7988 | 8.7287 | 8.6687 | 8.657 | 8.6611 | 8.6787 | 9.2111 | 7.0017 | 4.6953
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | System Transformation | Headroom (MW) | Thermal | 9.8456 | 9.6874 | 9.4775 | 9.3779 | 9.2944 | 9.0895 | 8.8967 | 8.6599 | 8.4311 | 8.1886 | 7.9545 | 7.7894 | 7.682 | 7.6189 | 7.6173 | 13.2168 | 7.5054 | -1.2778 | -11.6692
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | 52.9087 | -1.8577 | WPD Best View | Headroom (MW) | Thermal | 9.8481 | 9.6861 | 9.492 | 9.3936 | 9.3258 | 9.1368 | 8.9432 | 8.7249 | 8.5235 | 8.3146 | 8.1139 | 7.9736 | 6.9375 | 5.939 | 5.9531 | 11.535 | 3.232 | -8.1044 | -18.9481
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Consumer Transformation | Headroom (MW) | Thermal | 12.9771 | 12.8685 | 12.7306 | 12.5542 | 12.3762 | 12.1026 | 11.8094 | 11.5064 | 11.2041 | 10.864 | 10.5016 | 10.1742 | 9.8363 | 8.6013 | 8.3063 | 7.9853 | 4.9856 | -0.38859 | -4.4825
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Leading the Way | Headroom (MW) | Thermal | 13.0027 | 12.9275 | 12.8757 | 12.7687 | 12.6597 | 12.5023 | 12.3919 | 12.2521 | 12.0759 | 11.921 | 11.7627 | 11.6713 | 11.5984 | 10.2532 | 10.205 | 8.4285 | 4.1886 | -0.73962 | -5.4704
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | Steady Progression | Headroom (MW) | N/A | 12.9981 | 12.9305 | 12.8555 | 12.7874 | 12.7382 | 12.6757 | 12.6403 | 12.5781 | 12.4992 | 12.425 | 12.3293 | 12.2625 | 12.1888 | 12.1344 | 12.0848 | 12.0299 | 11.9698 | 10.6266 | 10.1265
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | System Transformation | Headroom (MW) | N/A | 12.9964 | 12.9163 | 12.8408 | 12.7435 | 12.6548 | 12.5283 | 12.4178 | 12.2495 | 12.0657 | 11.8743 | 11.6857 | 11.5215 | 11.379 | 11.2399 | 11.1252 | 11.0081 | 9.3103 | 6.1611 | 4.0934
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | 52.8996 | -1.8608 | WPD Best View | Headroom (MW) | N/A | 12.9965 | 12.9158 | 12.8409 | 12.7457 | 12.6593 | 12.5341 | 12.4127 | 12.2498 | 12.077 | 11.8963 | 11.7177 | 11.5676 | 11.4317 | 11.3007 | 11.1901 | 11.0674 | 9.1972 | 5.8627 | 3.6862
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Consumer Transformation | Headroom (MW) | Thermal | 1.9339 | 1.9014 | 1.8462 | 1.8534 | 1.8789 | 1.8257 | 1.7428 | 1.6948 | 1.6405 | 1.6083 | 0.6082 | 0.54554 | -0.42956 | -0.47298 | -1.3763 | -1.383 | -8.6179 | -15.2886 | -24.4106
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Leading the Way | Headroom (MW) | Thermal | 1.9459 | 1.9173 | 1.8724 | 1.94 | 2.0094 | 1.9863 | 1.975 | 1.9799 | 2.0078 | 2.0434 | 2.062 | 2.1009 | 1.2039 | -0.021084 | -4.2588 | -7.6246 | -14.2451 | -25.5867 | -34.9266
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | Steady Progression | Headroom (MW) | Thermal | 1.9434 | 1.9086 | 1.8598 | 1.8766 | 1.8998 | 1.8727 | 1.8595 | 1.8472 | 1.8453 | 1.8261 | 1.8221 | 1.8132 | 1.8237 | 1.8398 | 1.859 | 1.8948 | 2.1279 | 1.0175 | -0.52066
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | System Transformation | Headroom (MW) | Thermal | 1.9424 | 1.9064 | 1.8485 | 1.878 | 1.9046 | 1.8547 | 1.8115 | 1.7733 | 1.745 | 1.7083 | 1.687 | 1.6717 | 1.6771 | 1.703 | 1.7433 | 1.7831 | -2.7039 | -5.7005 | -12.2112
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | 52.8789 | -1.8028 | WPD Best View | Headroom (MW) | Thermal | 1.9436 | 1.9106 | 1.856 | 1.8817 | 1.9144 | 1.8724 | 1.8308 | 1.8023 | 1.7751 | 1.7531 | 1.7297 | 1.7136 | 0.79177 | 0.80739 | 0.8628 | 0.88929 | -4.8434 | -9.1082 | -15.8648
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Consumer Transformation | Headroom (MW) | N/A | 11.2062 | 11.1697 | 11.1069 | 11.0662 | 11.0548 | 11.0317 | 11 | 10.974 | 10.9835 | 10.9868 | 10.9967 | 11.0418 | 11.0812 | 10.211 | 10.2792 | 10.3339 | 9.2781 | 5.0654 | 2.8612
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Leading the Way | Headroom (MW) | N/A | 11.2172 | 11.1841 | 11.1172 | 11.0959 | 11.0969 | 11.0983 | 11.1017 | 11.1179 | 11.1656 | 11.2288 | 11.2909 | 11.3882 | 11.5005 | 11.6212 | 11.7448 | 7.4896 | 6.131 | 3.1273 | 0.77384
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | Steady Progression | Headroom (MW) | N/A | 11.2137 | 11.1805 | 11.1054 | 11.0751 | 11.0531 | 11.0278 | 11.0065 | 10.9891 | 10.967 | 10.9582 | 10.9533 | 10.9587 | 10.962 | 10.9885 | 11.0231 | 11.0598 | 11.4192 | 11.6634 | 11.3953
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | System Transformation | Headroom (MW) | N/A | 11.2126 | 11.1705 | 11.094 | 11.0621 | 11.0408 | 11.0122 | 10.9731 | 10.9429 | 10.9262 | 10.9118 | 10.8876 | 10.902 | 10.9316 | 10.9818 | 11.0546 | 11.123 | 11.5965 | 8.959 | 7.146
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | 52.9501 | -1.8506 | WPD Best View | Headroom (MW) | N/A | 11.2138 | 11.1655 | 11.1009 | 11.0719 | 11.0578 | 11.036 | 11.0055 | 10.9786 | 10.9772 | 10.9711 | 10.9723 | 10.9982 | 11.0198 | 10.1367 | 10.206 | 10.2757 | 9.5756 | 5.8384 | 3.9278
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Consumer Transformation | Headroom (MW) | Thermal | 38.9608 | 38.4946 | 37.8848 | 37.2251 | 36.5682 | 35.5272 | 34.1492 | 32.8655 | 31.5687 | 30.3032 | 26.9626 | 25.6066 | 21.9955 | 18.893 | 13.1824 | 8.2259 | -13.1867 | -39.3249 | -69.1543
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Leading the Way | Headroom (MW) | Thermal | 39.0385 | 38.7698 | 38.4285 | 38.1292 | 37.8127 | 37.3488 | 36.7338 | 36.1637 | 35.5705 | 35.081 | 34.4972 | 33.1819 | 32.8928 | 30.2615 | 22.2594 | 11.3733 | -14.1506 | -38.823 | -60.3002
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | Steady Progression | Headroom (MW) | N/A | 39.0384 | 38.7533 | 38.3184 | 37.9949 | 37.7104 | 37.3388 | 37.0177 | 36.6846 | 36.3732 | 36.016 | 35.6138 | 35.2937 | 35.0554 | 34.833 | 34.6446 | 34.4825 | 34.4923 | 26.4808 | 22.9704
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | System Transformation | Headroom (MW) | Thermal | 39.008 | 38.6836 | 38.2144 | 37.7865 | 37.3267 | 36.7561 | 36.0277 | 35.2484 | 34.5219 | 33.7505 | 32.9265 | 32.2983 | 31.7632 | 31.3353 | 30.9664 | 29.6979 | 18.2066 | 4.8019 | -11.3811
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | 53.1264 | -1.6398 | WPD Best View | Headroom (MW) | Thermal | 38.9593 | 38.4996 | 37.8753 | 37.2108 | 36.5466 | 35.505 | 34.1245 | 32.8172 | 31.5048 | 30.2247 | 26.859 | 25.4772 | 21.8198 | 18.7032 | 12.9715 | 8.0053 | -13.1703 | -37.931 | -67.4955
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Consumer Transformation | Headroom (MW) | Thermal | 13.5365 | 13.4284 | 13.3976 | 13.2383 | 13.0637 | 12.7524 | 12.3723 | 12.0124 | 11.6382 | 11.2634 | 9.9009 | 9.4884 | 9.1556 | 7.8237 | 7.4807 | 7.0795 | -0.73741 | -8.8481 | -17.6923
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Leading the Way | Headroom (MW) | Thermal | 13.5585 | 13.4909 | 13.5605 | 13.5208 | 13.4308 | 13.2606 | 13.0653 | 12.8837 | 12.6525 | 12.4411 | 12.1712 | 11.0344 | 10.8979 | 9.4497 | 7.6107 | 5.6839 | -3.0354 | -14.7151 | -21.767
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | Steady Progression | Headroom (MW) | N/A | 13.5509 | 13.4834 | 13.4625 | 13.3512 | 13.2433 | 13.0982 | 12.9672 | 12.8379 | 12.7036 | 12.5713 | 12.4159 | 12.292 | 12.2086 | 12.1017 | 12.0116 | 11.9236 | 11.8009 | 10.6634 | 10.1038
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | System Transformation | Headroom (MW) | Thermal | 13.5493 | 13.4685 | 13.46 | 13.3602 | 13.2189 | 13.0174 | 12.7811 | 12.546 | 12.3083 | 12.0764 | 11.8033 | 11.5976 | 11.4425 | 11.2717 | 11.1336 | 10.0455 | 7.0213 | 3.7648 | -1.1351
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | 53.014 | -1.7116 | WPD Best View | Headroom (MW) | Thermal | 13.5357 | 13.435 | 13.3914 | 13.2295 | 13.0503 | 12.7423 | 12.3644 | 11.9868 | 11.605 | 11.2247 | 9.8477 | 9.4225 | 9.0574 | 7.7262 | 7.376 | 6.9732 | -0.63278 | -7.4891 | -16.1365
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Consumer Transformation | Headroom (MW) | N/A | 7.2967 | 7.2441 | 7.1661 | 7.089 | 7.0067 | 6.8866 | 6.715 | 6.5487 | 6.392 | 6.2306 | 6.0535 | 5.8967 | 5.7395 | 5.5897 | 5.4348 | 5.2729 | 4.3324 | 3.2603 | 1.7093
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Leading the Way | Headroom (MW) | N/A | 7.3088 | 7.284 | 7.2344 | 7.1976 | 7.1751 | 7.1317 | 7.0595 | 7.0144 | 6.9547 | 6.9118 | 6.8658 | 6.8398 | 6.8138 | 6.7947 | 6.7737 | 6.7363 | 6.4034 | 5.852 | 5.2508
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | Steady Progression | Headroom (MW) | N/A | 7.3094 | 7.2914 | 7.2483 | 7.2218 | 7.1965 | 7.1724 | 7.1512 | 7.1202 | 7.1007 | 7.0642 | 7.0354 | 7.011 | 6.9843 | 6.9708 | 6.9661 | 6.9504 | 6.9906 | 6.9744 | 6.8156
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | System Transformation | Headroom (MW) | N/A | 7.3068 | 7.2767 | 7.2191 | 7.1672 | 7.1224 | 7.0644 | 6.9761 | 6.8914 | 6.7906 | 6.697 | 6.6018 | 6.5215 | 6.4543 | 6.3911 | 6.3413 | 6.2899 | 6.1149 | 5.8205 | 5.4372
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | 53.2165 | -1.6893 | WPD Best View | Headroom (MW) | N/A | 7.2967 | 7.2441 | 7.1661 | 7.089 | 7.0067 | 6.8866 | 6.715 | 6.5487 | 6.392 | 6.2306 | 6.0535 | 5.8967 | 5.7395 | 5.5897 | 5.4348 | 5.2729 | 4.3324 | 3.2603 | 1.7093
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Consumer Transformation | Headroom (MW) | Thermal | 7.5046 | 7.4719 | 7.4402 | 7.4093 | 7.3917 | 7.3117 | 7.2027 | 7.1084 | 7.011 | 6.9232 | 6.8212 | 6.7457 | 6.6729 | 6.6286 | 6.5909 | 6.5244 | 4.029 | 0.51282 | -2.9103
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Leading the Way | Headroom (MW) | Thermal | 7.511 | 7.5025 | 7.4978 | 7.5114 | 7.5409 | 7.5174 | 7.4955 | 7.478 | 7.4715 | 7.4834 | 7.5054 | 7.5219 | 7.5469 | 7.5049 | 7.5232 | 6.0283 | 2.6598 | 0.71689 | -1.4032
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | Steady Progression | Headroom (MW) | N/A | 7.5167 | 7.4948 | 7.4805 | 7.4789 | 7.4884 | 7.4742 | 7.466 | 7.4673 | 7.4573 | 7.4444 | 7.4372 | 7.4402 | 7.4539 | 7.4779 | 7.4964 | 7.535 | 7.677 | 7.6507 | 7.486
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | System Transformation | Headroom (MW) | N/A | 7.5069 | 7.4919 | 7.4701 | 7.4605 | 7.4607 | 7.422 | 7.3713 | 7.3123 | 7.2711 | 7.2184 | 7.1766 | 7.145 | 7.1263 | 7.1347 | 7.1465 | 7.1786 | 7.3432 | 4.6265 | 4.1989
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | 53.1022 | -1.565 | WPD Best View | Headroom (MW) | Thermal | 7.5046 | 7.4719 | 7.4402 | 7.4093 | 7.3917 | 7.3117 | 7.2027 | 7.1084 | 7.011 | 6.9232 | 6.8212 | 6.7457 | 6.6729 | 6.6286 | 6.5909 | 6.5244 | 4.029 | 0.51282 | -2.9103
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Consumer Transformation | Headroom (MW) | Thermal | 0.31856 | 0.2309 | 0.080524 | -0.023653 | -0.11574 | -0.22031 | -0.36648 | -0.49405 | -0.57774 | -0.70029 | -1.7808 | -1.9231 | -2.0639 | -2.1916 | -6.9415 | -10.7806 | -14.0438 | -19.6957 | -25.3231
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Leading the Way | Headroom (MW) | Thermal | 0.32307 | 0.24955 | 0.12159 | 0.049721 | -0.027431 | -0.078316 | -0.15531 | -0.22887 | -0.23026 | -0.29434 | -0.37254 | -0.43046 | -0.48282 | -1.4847 | -6.0156 | -11.5054 | -17.1013 | -21.6463 | -27.1741
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | Steady Progression | Headroom (MW) | Thermal | 0.3215 | 0.25247 | 0.10547 | 0.032842 | -0.036928 | -0.097295 | -0.15312 | -0.21943 | -0.2476 | -0.30728 | -0.3683 | -0.43444 | -0.49142 | -0.54474 | -0.59687 | -0.64688 | -0.9 | -7.667 | -8.0716
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | System Transformation | Headroom (MW) | Thermal | 0.31975 | 0.2391 | 0.096628 | 0.0099599 | -0.083997 | -0.14888 | -0.23529 | -0.32733 | -0.35912 | -0.44194 | -0.52164 | -0.58445 | -0.65511 | -0.68491 | -0.71468 | -0.7392 | -8.7946 | -11.7566 | -14.9523
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | 53.0887 | -1.6098 | WPD Best View | Headroom (MW) | Thermal | 0.31856 | 0.2309 | 0.080524 | -0.023653 | -0.11574 | -0.22031 | -0.36648 | -0.49405 | -0.57774 | -0.70029 | -1.7808 | -1.9231 | -2.0639 | -2.1916 | -6.9415 | -10.7806 | -14.0438 | -19.6957 | -25.3231
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Consumer Transformation | Headroom (MW) | N/A | 12.4624 | 12.4256 | 12.3593 | 12.3215 | 12.2801 | 12.2388 | 12.1686 | 12.1253 | 12.0514 | 12.0244 | 11.9607 | 11.9031 | 10.4152 | 10.3757 | 10.3778 | 10.3578 | 7.6397 | 4.855 | 1.9992
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Leading the Way | Headroom (MW) | N/A | 12.4637 | 12.4364 | 12.3723 | 12.3478 | 12.3175 | 12.2968 | 12.2571 | 12.2371 | 12.2125 | 12.2101 | 12.1839 | 12.1712 | 12.1421 | 12.0744 | 10.4928 | 9.5676 | 6.6123 | 3.3684 | 1.4503
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | Steady Progression | Headroom (MW) | N/A | 12.463 | 12.4339 | 12.375 | 12.3441 | 12.3153 | 12.2791 | 12.2517 | 12.2262 | 12.1974 | 12.1762 | 12.1497 | 12.1305 | 12.1223 | 12.1091 | 12.1112 | 12.1098 | 12.1478 | 12.0434 | 10.538
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | System Transformation | Headroom (MW) | N/A | 12.4619 | 12.4313 | 12.362 | 12.3297 | 12.2899 | 12.2519 | 12.2198 | 12.1766 | 12.1419 | 12.1056 | 12.0746 | 12.0502 | 12.0385 | 12.0399 | 12.0428 | 12.0484 | 12.1085 | 8.7709 | 6.209
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | 53.0948 | -1.6592 | WPD Best View | Headroom (MW) | N/A | 12.4617 | 12.424 | 12.356 | 12.316 | 12.2718 | 12.2268 | 12.1518 | 12.1025 | 12.0208 | 11.9846 | 11.9103 | 11.8396 | 10.3376 | 10.2834 | 10.2716 | 10.2435 | 7.5515 | 4.8899 | 2.1023
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Consumer Transformation | Headroom (MW) | Thermal | 14.1085 | 14.0271 | 13.8864 | 13.7323 | 13.5916 | 13.3568 | 13.0609 | 12.7603 | 12.4397 | 12.1368 | 11.7904 | 11.466 | 10.2365 | 9.003 | 8.7571 | 8.4804 | 5.8476 | 1.9883 | -4.4385
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Leading the Way | Headroom (MW) | N/A | 14.132 | 14.0991 | 14.0128 | 13.9285 | 13.862 | 13.7727 | 13.6602 | 13.5163 | 13.3304 | 13.2295 | 13.1172 | 13.0712 | 13.0346 | 13.0224 | 13.0169 | 12.0536 | 7.9071 | 5.804 | 3.4948
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | Steady Progression | Headroom (MW) | N/A | 14.1271 | 14.09 | 14.0155 | 13.9696 | 13.9502 | 13.9 | 13.8629 | 13.8233 | 13.7729 | 13.7223 | 13.656 | 13.6136 | 13.5735 | 13.5516 | 13.5183 | 13.5039 | 13.6924 | 13.78 | 13.3426
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | System Transformation | Headroom (MW) | N/A | 14.1242 | 14.0763 | 13.9888 | 13.9063 | 13.8326 | 13.7377 | 13.6131 | 13.457 | 13.2875 | 13.1341 | 12.9487 | 12.8268 | 12.702 | 12.6116 | 12.522 | 12.4494 | 12.2556 | 11.7741 | 7.5106
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | 53.1388 | -1.5509 | WPD Best View | Headroom (MW) | Thermal | 14.1085 | 14.0271 | 13.8864 | 13.7323 | 13.5916 | 13.3568 | 13.0609 | 12.7603 | 12.4397 | 12.1368 | 11.7904 | 11.466 | 10.2365 | 9.003 | 8.7571 | 8.4804 | 5.8476 | 1.9883 | -4.4385
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Consumer Transformation | Headroom (MW) | N/A | 9.1509 | 9.0838 | 8.9719 | 8.8757 | 8.7674 | 8.6184 | 8.4135 | 8.2217 | 8.0314 | 7.8424 | 7.6339 | 7.447 | 7.2569 | 7.0812 | 6.8999 | 6.7088 | 5.1631 | 4.0198 | 2.9186
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Leading the Way | Headroom (MW) | N/A | 9.1587 | 9.1247 | 9.0462 | 8.9908 | 8.9311 | 8.8651 | 8.7688 | 8.6803 | 8.5965 | 8.5166 | 8.4434 | 8.3912 | 8.3576 | 8.3174 | 8.2751 | 8.2262 | 7.8207 | 7.2144 | 5.2655
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | Steady Progression | Headroom (MW) | N/A | 9.167 | 9.1247 | 9.0484 | 9.0138 | 8.9709 | 8.9296 | 8.889 | 8.8465 | 8.8062 | 8.7622 | 8.7051 | 8.6583 | 8.6214 | 8.5838 | 8.555 | 8.524 | 8.5008 | 8.4531 | 8.1734
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | System Transformation | Headroom (MW) | N/A | 9.1564 | 9.117 | 9.0351 | 8.97 | 8.9034 | 8.829 | 8.719 | 8.6097 | 8.4988 | 8.3782 | 8.2604 | 8.1589 | 8.072 | 7.9884 | 7.9122 | 7.8425 | 7.5749 | 7.2189 | 6.7679
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | 53.1575 | -1.6161 | WPD Best View | Headroom (MW) | N/A | 9.1509 | 9.0838 | 8.9719 | 8.8757 | 8.7674 | 8.6184 | 8.4135 | 8.2217 | 8.0314 | 7.8424 | 7.6339 | 7.447 | 7.2569 | 7.0812 | 6.8999 | 6.7088 | 5.1631 | 4.0198 | 2.9186