## Battery Calculator
BATTERY CALCULATOR FOR EE SPEC 23/1
Battery Nominal Voltage | 110
Battery Voltage At End Of Duty Cycle | 99.9
Standby Period (Hours) | 24
Design Margin | 1.1
Ageing Factor | 1.25
Temperature Correction Factor | 1.04
Circuit Breakers | Quantity Tripped Simultaneously | Tripping Burden (Watts) | Tripping Duration (Seconds) | Closing Burden (Watts) | Closing Duration (Seconds)
Type 1 | 7 | 300 | 0.06 | 600 | 7
Type 2 | 0 | 300 | 0.06 | 600 | 7
Type 3 | 0 | 300 | 0.06 | 600 | 7
Standing Load (Watts) | 420
Battery Capacity Required (Ah) | 150.5104
Monobloc Type | Number of Parallel Strings | Actual Battery Capacity (Ah)
GNB Marathon M FT M12V100FT | 2 | 200 | BATTERY CAPACITY IS ADEQUATE
Minimum Charger Rating (A) | 22.9246

## Kt_Data_Tables (hidden)
Kt: 1.85V/Cell @ 20degC |  | 1s | 5s | 30s | 60s | 3m | 5m | 10m | 15m | 20m | 30m | 40m | 50m | 1h | 1.5h | 3h | 5h | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
Time | 0 | 0.00032777 | 0.0014389 | 0.0083833 | 0.016717 | 0.05005 | 0.083383 | 0.16672 | 0.25005 | 0.33338 | 0.50005 | 0.66672 | 0.83338 | 1 | 1.5 | 3 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40 | 40.5 | 41 | 41.5 | 42 | 42.5 | 43 | 43.5 | 44 | 44.5 | 45 | 45.5 | 46 | 46.5 | 47 | 47.5 | 48 | 48.5 | 49 | 49.5 | 50 | 50.5 | 51 | 51.5 | 52 | 52.5 | 53 | 53.5 | 54 | 54.5 | 55 | 55.5 | 56 | 56.5 | 57 | 57.5 | 58 | 58.5 | 59 | 59.5 | 60 | 60.5 | 61 | 61.5 | 62 | 62.5 | 63 | 63.5 | 64 | 64.5 | 65 | 65.5 | 66 | 66.5 | 67 | 67.5 | 68 | 68.5 | 69 | 69.5 | 70 | 70.5 | 71 | 71.5 | 72 | 72.5 | 73 | 73.5 | 74 | 74.5 | 75 | 75.5 | 76 | 76.5 | 77 | 77.5 | 78 | 78.5 | 79 | 79.5 | 80 | 80.5 | 81 | 81.5 | 82 | 82.5 | 83 | 83.5 | 84 | 84.5 | 85 | 85.5 | 86 | 86.5 | 87 | 87.5 | 88 | 88.5 | 89 | 89.5 | 90 | 90.5 | 91 | 91.5 | 92 | 92.5 | 93 | 93.5 | 94 | 94.5 | 95 | 95.5 | 96
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200
Enersys Powersafe EON SBS 170F | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.56648 | 0.67114 | 0.76854 | 0.9731 | 1.1588 | 1.3482 | 1.5357 | 2.5764 | 3.617 | 5.6106 | 6.0999 | 6.5891 | 7.0556 | 7.5221 | 8.0111 | 8.5 | 8.9722 | 9.4444 | 9.9051 | 10.3659 | 10.7983 | 11.2308 | 11.6633 | 12.0958 | 12.5283 | 12.9608 | 13.3933 | 13.8258 | 14.2583 | 14.6908 | 15.1232 | 15.5557 | 15.9882 | 16.4207 | 16.8532 | 17.2857 | 17.7182 | 18.1507 | 18.5832 | 19.0157 | 19.4482 | 19.8806 | 20.3131 | 20.7456 | 21.1781 | 21.6106 | 22.0431 | 22.4756 | 22.9081 | 23.3406 | 23.7731 | 24.2055 | 24.638 | 25.0705 | 25.503 | 25.9355 | 26.368 | 26.8005 | 27.233 | 27.6655 | 28.098 | 28.5304 | 28.9629 | 29.3954 | 29.8279 | 30.2604 | 30.6929 | 31.1254 | 31.5579 | 31.9904 | 32.4229 | 32.8554 | 33.2878 | 33.7203 | 34.1528 | 34.5853 | 35.0178 | 35.4503 | 35.8828 | 36.3153 | 36.7478 | 37.1803 | 37.6127 | 38.0452 | 38.4777 | 38.9102 | 39.3427 | 39.7752 | 40.2077 | 40.6402 | 41.0727 | 41.5052 | 41.9376 | 42.3701 | 42.8026 | 43.2351 | 43.6676 | 44.1001 | 44.5326 | 44.9651 | 45.3976 | 45.8301 | 46.2625 | 46.695 | 47.1275 | 47.56 | 47.9925 | 48.425 | 48.8575 | 49.29 | 49.7225 | 50.155 | 50.5875 | 51.0199 | 51.4524 | 51.8849 | 52.3174 | 52.7499 | 53.1824 | 53.6149 | 54.0474 | 54.4799 | 54.9124 | 55.3448 | 55.7773 | 56.2098 | 56.6423 | 57.0748 | 57.5073 | 57.9398 | 58.3723 | 58.8048 | 59.2373 | 59.6697 | 60.1022 | 60.5347 | 60.9672 | 61.3997 | 61.8322 | 62.2647 | 62.6972 | 63.1297 | 63.5622 | 63.9947 | 64.4271 | 64.8596 | 65.2921 | 65.7246 | 66.1571 | 66.5896 | 67.0221 | 67.4546 | 67.8871 | 68.3196 | 68.752 | 69.1845 | 69.617 | 70.0495 | 70.482 | 70.9145 | 71.347 | 71.7795 | 72.212 | 72.6445 | 73.0769 | 73.5094 | 73.9419 | 74.3744 | 74.8069 | 75.2394 | 75.6719 | 76.1044 | 76.5369 | 76.9694 | 77.4019 | 77.8343 | 78.2668 | 78.6993 | 79.1318 | 79.5643 | 79.9968 | 80.4293 | 80.8618 | 81.2943 | 81.7268 | 82.1592 | 82.5917 | 83.0242 | 83.4567 | 83.8892 | 84.3217 | 84.7542
Enersys Powersafe EON SBS B14F | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.31969 | 0.43147 | 0.53652 | 0.63608 | 0.82708 | 1.0098 | 1.2435 | 1.4518 | 2.4117 | 3.3716 | 5.2735 | 5.7592 | 6.2449 | 6.718 | 7.1911 | 7.6601 | 8.1291 | 8.6013 | 9.0735 | 9.5368 | 10 | 10.4581 | 10.9161 | 11.3742 | 11.8323 | 12.2904 | 12.7484 | 13.2065 | 13.6646 | 14.1227 | 14.5807 | 15.0388 | 15.4969 | 15.955 | 16.413 | 16.8711 | 17.3292 | 17.7873 | 18.2453 | 18.7034 | 19.1615 | 19.6196 | 20.0776 | 20.5357 | 20.9938 | 21.4519 | 21.9099 | 22.368 | 22.8261 | 23.2842 | 23.7422 | 24.2003 | 24.6584 | 25.1165 | 25.5745 | 26.0326 | 26.4907 | 26.9488 | 27.4068 | 27.8649 | 28.323 | 28.7811 | 29.2391 | 29.6972 | 30.1553 | 30.6134 | 31.0714 | 31.5295 | 31.9876 | 32.4457 | 32.9037 | 33.3618 | 33.8199 | 34.278 | 34.736 | 35.1941 | 35.6522 | 36.1102 | 36.5683 | 37.0264 | 37.4845 | 37.9425 | 38.4006 | 38.8587 | 39.3168 | 39.7748 | 40.2329 | 40.691 | 41.1491 | 41.6071 | 42.0652 | 42.5233 | 42.9814 | 43.4394 | 43.8975 | 44.3556 | 44.8137 | 45.2717 | 45.7298 | 46.1879 | 46.646 | 47.104 | 47.5621 | 48.0202 | 48.4783 | 48.9363 | 49.3944 | 49.8525 | 50.3106 | 50.7686 | 51.2267 | 51.6848 | 52.1429 | 52.6009 | 53.059 | 53.5171 | 53.9752 | 54.4332 | 54.8913 | 55.3494 | 55.8075 | 56.2655 | 56.7236 | 57.1817 | 57.6398 | 58.0978 | 58.5559 | 59.014 | 59.472 | 59.9301 | 60.3882 | 60.8463 | 61.3043 | 61.7624 | 62.2205 | 62.6786 | 63.1366 | 63.5947 | 64.0528 | 64.5109 | 64.9689 | 65.427 | 65.8851 | 66.3432 | 66.8012 | 67.2593 | 67.7174 | 68.1755 | 68.6335 | 69.0916 | 69.5497 | 70.0078 | 70.4658 | 70.9239 | 71.382 | 71.8401 | 72.2981 | 72.7562 | 73.2143 | 73.6724 | 74.1304 | 74.5885 | 75.0466 | 75.5047 | 75.9627 | 76.4208 | 76.8789 | 77.337 | 77.795 | 78.2531 | 78.7112 | 79.1693 | 79.6273 | 80.0854 | 80.5435 | 81.0016 | 81.4596 | 81.9177 | 82.3758 | 82.8339 | 83.2919 | 83.75 | 84.2081 | 84.6661 | 85.1242 | 85.5823 | 86.0404 | 86.4984 | 86.9565 | 87.4146 | 87.8727 | 88.3307 | 88.7888
Enersys Powersafe EON SBS C11F | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.36895 | 0.49728 | 0.61409 | 0.72619 | 0.93943 | 1.1423 | 1.3349 | 1.5327 | 2.6037 | 3.6747 | 5.6832 | 6.1568 | 6.6304 | 7.0962 | 7.562 | 7.9026 | 8.2432 | 8.6966 | 9.15 | 9.6135 | 10.0771 | 10.5031 | 10.9291 | 11.3552 | 11.7812 | 12.2072 | 12.6332 | 13.0593 | 13.4853 | 13.9113 | 14.3373 | 14.7634 | 15.1894 | 15.6154 | 16.0414 | 16.4674 | 16.8935 | 17.3195 | 17.7455 | 18.1715 | 18.5976 | 19.0236 | 19.4496 | 19.8756 | 20.3017 | 20.7277 | 21.1537 | 21.5797 | 22.0057 | 22.4318 | 22.8578 | 23.2838 | 23.7098 | 24.1359 | 24.5619 | 24.9879 | 25.4139 | 25.84 | 26.266 | 26.692 | 27.118 | 27.5441 | 27.9701 | 28.3961 | 28.8221 | 29.2481 | 29.6742 | 30.1002 | 30.5262 | 30.9522 | 31.3783 | 31.8043 | 32.2303 | 32.6563 | 33.0824 | 33.5084 | 33.9344 | 34.3604 | 34.7865 | 35.2125 | 35.6385 | 36.0645 | 36.4905 | 36.9166 | 37.3426 | 37.7686 | 38.1946 | 38.6207 | 39.0467 | 39.4727 | 39.8987 | 40.3248 | 40.7508 | 41.1768 | 41.6028 | 42.0288 | 42.4549 | 42.8809 | 43.3069 | 43.7329 | 44.159 | 44.585 | 45.011 | 45.437 | 45.8631 | 46.2891 | 46.7151 | 47.1411 | 47.5672 | 47.9932 | 48.4192 | 48.8452 | 49.2712 | 49.6973 | 50.1233 | 50.5493 | 50.9753 | 51.4014 | 51.8274 | 52.2534 | 52.6794 | 53.1055 | 53.5315 | 53.9575 | 54.3835 | 54.8096 | 55.2356 | 55.6616 | 56.0876 | 56.5136 | 56.9397 | 57.3657 | 57.7917 | 58.2177 | 58.6438 | 59.0698 | 59.4958 | 59.9218 | 60.3479 | 60.7739 | 61.1999 | 61.6259 | 62.052 | 62.478 | 62.904 | 63.33 | 63.756 | 64.1821 | 64.6081 | 65.0341 | 65.4601 | 65.8862 | 66.3122 | 66.7382 | 67.1642 | 67.5903 | 68.0163 | 68.4423 | 68.8683 | 69.2943 | 69.7204 | 70.1464 | 70.5724 | 70.9984 | 71.4245 | 71.8505 | 72.2765 | 72.7025 | 73.1286 | 73.5546 | 73.9806 | 74.4066 | 74.8327 | 75.2587 | 75.6847 | 76.1107 | 76.5367 | 76.9628 | 77.3888 | 77.8148 | 78.2408 | 78.6669 | 79.0929 | 79.5189 | 79.9449 | 80.371 | 80.797 | 81.223 | 81.649 | 82.0751 | 82.5011 | 82.9271 | 83.3531
GNB Marathon M FT M12V100FT | 0.37736 | 0.37736 | 0.37736 | 0.37736 | 0.37736 | 0.37736 | 0.40816 | 0.5 | 0.59524 | 0.75216 | 0.90909 | 1.1269 | 1.3447 | 1.5625 | 2.2321 | 3.69 | 5.5866 | 6.0679 | 6.5493 | 7.0306 | 7.5119 | 7.9932 | 8.4746 | 8.9601 | 9.4456 | 9.9311 | 10.4167 | 10.8762 | 11.3358 | 11.7953 | 12.2549 | 12.7088 | 13.1627 | 13.6166 | 14.0704 | 14.5243 | 14.9782 | 15.4321 | 15.886 | 16.3399 | 16.7938 | 17.2476 | 17.7015 | 18.1554 | 18.6093 | 19.0632 | 19.5171 | 19.971 | 20.4248 | 20.8787 | 21.3326 | 21.7865 | 22.2404 | 22.6943 | 23.1481 | 23.602 | 24.0559 | 24.5098 | 24.9637 | 25.4176 | 25.8715 | 26.3253 | 26.7792 | 27.2331 | 27.687 | 28.1409 | 28.5948 | 29.0487 | 29.5025 | 29.9564 | 30.4103 | 30.8642 | 31.3181 | 31.772 | 32.2259 | 32.6797 | 33.1336 | 33.5875 | 34.0414 | 34.4953 | 34.9492 | 35.4031 | 35.8569 | 36.3108 | 36.7647 | 37.2186 | 37.6725 | 38.1264 | 38.5802 | 39.0341 | 39.488 | 39.9419 | 40.3958 | 40.8497 | 41.3036 | 41.7574 | 42.2113 | 42.6652 | 43.1191 | 43.573 | 44.0269 | 44.4808 | 44.9346 | 45.3885 | 45.8424 | 46.2963 | 46.7502 | 47.2041 | 47.658 | 48.1118 | 48.5657 | 49.0196 | 49.4735 | 49.9274 | 50.3813 | 50.8351 | 51.289 | 51.7429 | 52.1968 | 52.6507 | 53.1046 | 53.5585 | 54.0123 | 54.4662 | 54.9201 | 55.374 | 55.8279 | 56.2818 | 56.7357 | 57.1895 | 57.6434 | 58.0973 | 58.5512 | 59.0051 | 59.459 | 59.9129 | 60.3667 | 60.8206 | 61.2745 | 61.7284 | 62.1823 | 62.6362 | 63.0901 | 63.5439 | 63.9978 | 64.4517 | 64.9056 | 65.3595 | 65.8134 | 66.2672 | 66.7211 | 67.175 | 67.6289 | 68.0828 | 68.5367 | 68.9906 | 69.4444 | 69.8983 | 70.3522 | 70.8061 | 71.26 | 71.7139 | 72.1678 | 72.6216 | 73.0755 | 73.5294 | 73.9833 | 74.4372 | 74.8911 | 75.345 | 75.7988 | 76.2527 | 76.7066 | 77.1605 | 77.6144 | 78.0683 | 78.5221 | 78.976 | 79.4299 | 79.8838 | 80.3377 | 80.7916 | 81.2455 | 81.6993 | 82.1532 | 82.6071 | 83.061 | 83.5149 | 83.9688 | 84.4227 | 84.8765 | 85.3304 | 85.7843 | 86.2382 | 86.6921 | 87.146 | 87.5999 | 88.0537 | 88.5076
GNB Marathon M FT M12V190FT | 0.49738 | 0.49738 | 0.49738 | 0.49738 | 0.49738 | 0.49738 | 0.54286 | 0.64846 | 0.75099 | 0.9092 | 1.0674 | 1.2307 | 1.3941 | 1.5574 | 2.0652 | 3.854 | 5.8642 | 6.3262 | 6.7883 | 7.2503 | 7.7123 | 8.1743 | 8.6364 | 9.0729 | 9.5094 | 9.946 | 10.3825 | 10.8318 | 11.281 | 11.7302 | 12.1795 | 12.61 | 13.0405 | 13.471 | 13.9015 | 14.3321 | 14.7626 | 15.1931 | 15.6236 | 16.0541 | 16.4846 | 16.9152 | 17.3457 | 17.7762 | 18.2067 | 18.6372 | 19.0677 | 19.4982 | 19.9288 | 20.3593 | 20.7898 | 21.2203 | 21.6508 | 22.0813 | 22.5118 | 22.9424 | 23.3729 | 23.8034 | 24.2339 | 24.6644 | 25.0949 | 25.5255 | 25.956 | 26.3865 | 26.817 | 27.2475 | 27.678 | 28.1085 | 28.5391 | 28.9696 | 29.4001 | 29.8306 | 30.2611 | 30.6916 | 31.1221 | 31.5527 | 31.9832 | 32.4137 | 32.8442 | 33.2747 | 33.7052 | 34.1358 | 34.5663 | 34.9968 | 35.4273 | 35.8578 | 36.2883 | 36.7188 | 37.1494 | 37.5799 | 38.0104 | 38.4409 | 38.8714 | 39.3019 | 39.7325 | 40.163 | 40.5935 | 41.024 | 41.4545 | 41.885 | 42.3155 | 42.7461 | 43.1766 | 43.6071 | 44.0376 | 44.4681 | 44.8986 | 45.3291 | 45.7597 | 46.1902 | 46.6207 | 47.0512 | 47.4817 | 47.9122 | 48.3428 | 48.7733 | 49.2038 | 49.6343 | 50.0648 | 50.4953 | 50.9258 | 51.3564 | 51.7869 | 52.2174 | 52.6479 | 53.0784 | 53.5089 | 53.9394 | 54.37 | 54.8005 | 55.231 | 55.6615 | 56.092 | 56.5225 | 56.9531 | 57.3836 | 57.8141 | 58.2446 | 58.6751 | 59.1056 | 59.5361 | 59.9667 | 60.3972 | 60.8277 | 61.2582 | 61.6887 | 62.1192 | 62.5497 | 62.9803 | 63.4108 | 63.8413 | 64.2718 | 64.7023 | 65.1328 | 65.5634 | 65.9939 | 66.4244 | 66.8549 | 67.2854 | 67.7159 | 68.1464 | 68.577 | 69.0075 | 69.438 | 69.8685 | 70.299 | 70.7295 | 71.16 | 71.5906 | 72.0211 | 72.4516 | 72.8821 | 73.3126 | 73.7431 | 74.1737 | 74.6042 | 75.0347 | 75.4652 | 75.8957 | 76.3262 | 76.7567 | 77.1873 | 77.6178 | 78.0483 | 78.4788 | 78.9093 | 79.3398 | 79.7703 | 80.2009 | 80.6314 | 81.0619 | 81.4924 | 81.9229 | 82.3534 | 82.784 | 83.2145 | 83.645 | 84.0755 | 84.506
GNB Marathon M FT M12V60FT | 0.38816 | 0.38816 | 0.38816 | 0.38816 | 0.38816 | 0.34706 | 0.38816 | 0.5 | 0.60825 | 0.77312 | 0.938 | 1.1362 | 1.3343 | 1.5325 | 2.13 | 3.758 | 5.7282 | 6.1945 | 6.6608 | 7.1271 | 7.5934 | 8.0597 | 8.526 | 9.0051 | 9.4842 | 9.9634 | 10.4425 | 10.9176 | 11.3928 | 11.8679 | 12.3431 | 12.7966 | 13.2502 | 13.7038 | 14.1573 | 14.6109 | 15.0644 | 15.518 | 15.9715 | 16.4251 | 16.8786 | 17.3322 | 17.7857 | 18.2393 | 18.6928 | 19.1464 | 19.5999 | 20.0535 | 20.507 | 20.9606 | 21.4141 | 21.8677 | 22.3212 | 22.7748 | 23.2283 | 23.6819 | 24.1355 | 24.589 | 25.0426 | 25.4961 | 25.9497 | 26.4032 | 26.8568 | 27.3103 | 27.7639 | 28.2174 | 28.671 | 29.1245 | 29.5781 | 30.0316 | 30.4852 | 30.9387 | 31.3923 | 31.8458 | 32.2994 | 32.7529 | 33.2065 | 33.66 | 34.1136 | 34.5671 | 35.0207 | 35.4743 | 35.9278 | 36.3814 | 36.8349 | 37.2885 | 37.742 | 38.1956 | 38.6491 | 39.1027 | 39.5562 | 40.0098 | 40.4633 | 40.9169 | 41.3704 | 41.824 | 42.2775 | 42.7311 | 43.1846 | 43.6382 | 44.0917 | 44.5453 | 44.9988 | 45.4524 | 45.906 | 46.3595 | 46.8131 | 47.2666 | 47.7202 | 48.1737 | 48.6273 | 49.0808 | 49.5344 | 49.9879 | 50.4415 | 50.895 | 51.3486 | 51.8021 | 52.2557 | 52.7092 | 53.1628 | 53.6163 | 54.0699 | 54.5234 | 54.977 | 55.4305 | 55.8841 | 56.3376 | 56.7912 | 57.2448 | 57.6983 | 58.1519 | 58.6054 | 59.059 | 59.5125 | 59.9661 | 60.4196 | 60.8732 | 61.3267 | 61.7803 | 62.2338 | 62.6874 | 63.1409 | 63.5945 | 64.048 | 64.5016 | 64.9551 | 65.4087 | 65.8622 | 66.3158 | 66.7693 | 67.2229 | 67.6765 | 68.13 | 68.5836 | 69.0371 | 69.4907 | 69.9442 | 70.3978 | 70.8513 | 71.3049 | 71.7584 | 72.212 | 72.6655 | 73.1191 | 73.5726 | 74.0262 | 74.4797 | 74.9333 | 75.3868 | 75.8404 | 76.2939 | 76.7475 | 77.201 | 77.6546 | 78.1081 | 78.5617 | 79.0153 | 79.4688 | 79.9224 | 80.3759 | 80.8295 | 81.283 | 81.7366 | 82.1901 | 82.6437 | 83.0972 | 83.5508 | 84.0043 | 84.4579 | 84.9114 | 85.365 | 85.8185 | 86.2721 | 86.7256 | 87.1792 | 87.6327 | 88.0863 | 88.5398

## Data_Enersys_VRLA (hidden)
Enersys Powersafe EON SBS 170F (12V)
Ref (Ah): | 170
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.083333 | 300.1 | 0.56648
0.16667 | 300.1 | 0.56648
0.25 | 253.3 | 0.67114
0.33333 | 221.2 | 0.76854
0.41667 | 194.4 | 0.87449
0.5 | 174.7 | 0.9731
0.58333 | 160.8 | 1.0572
0.66667 | 146.7 | 1.1588
0.75 | 135.6 | 1.2537
1 | 110.7 | 1.5357
2 | 65.6 | 2.5915
3 | 47 | 3.617
4 | 36.8 | 4.6196
5 | 30.3 | 5.6106
6 | 25.8 | 6.5891
7 | 22.6 | 7.5221
8 | 20 | 8.5
9 | 18 | 9.4444
10 | 16.4 | 10.3659
20 | 8.94 | 19.0157
Enersys Powersafe EON SBS B14F (12V)
Ref (Ah): | 61.7
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.083333 | 193 | 0.31969
0.16667 | 143 | 0.43147
0.25 | 115 | 0.53652
0.33333 | 97 | 0.63608
0.41667 | 84.2 | 0.73278
0.5 | 74.6 | 0.82708
0.58333 | 67.1 | 0.91952
0.66667 | 61.1 | 1.0098
0.75 | 56.1 | 1.0998
1 | 42.5 | 1.4518
2 | 25.9 | 2.3822
3 | 18.3 | 3.3716
4 | 14.2 | 4.3451
5 | 11.7 | 5.2735
6 | 9.88 | 6.2449
7 | 8.58 | 7.1911
8 | 7.59 | 8.1291
9 | 6.8 | 9.0735
10 | 6.17 | 10
20 | 3.22 | 19.1615
Enersys Powersafe EON SBS C11F (12V)
Ref (Ah): | 91.5
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.083333 | 248 | 0.36895
0.16667 | 184 | 0.49728
0.25 | 149 | 0.61409
0.33333 | 126 | 0.72619
0.41667 | 110 | 0.83182
0.5 | 97.4 | 0.93943
0.58333 | 87.8 | 1.0421
0.66667 | 80.1 | 1.1423
0.75 | 73.7 | 1.2415
1 | 59.7 | 1.5327
2 | 34.8 | 2.6293
3 | 24.9 | 3.6747
4 | 19.6 | 4.6684
5 | 16.1 | 5.6832
6 | 13.8 | 6.6304
7 | 12.1 | 7.562
8 | 11.1 | 8.2432
9 | 10 | 9.15
10 | 9.08 | 10.0771
20 | 4.92 | 18.5976

## Data_GNB_VRLA (hidden)
GNB Marathon M FT M12V60FT
Ref (Ah): | 59
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.05 | 170 | 0.34706
0.083333 | 152 | 0.38816
0.16667 | 118 | 0.5
0.25 | 97 | 0.60825
0.5 | 62.9 | 0.938
1 | 38.5 | 1.5325
1.5 | 27.7 | 2.13
2 | 21.8 | 2.7064
3 | 15.7 | 3.758
5 | 10.3 | 5.7282
8 | 6.92 | 8.526
10 | 5.65 | 10.4425
12 | 4.78 | 12.3431
24 | 2.54 | 23.2283
GNB Marathon M FT M12V100FT
Ref (Ah): | 100
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.05 | 265 | 0.37736
0.083333 | 245 | 0.40816
0.16667 | 200 | 0.5
0.25 | 168 | 0.59524
0.5 | 110 | 0.90909
1 | 64 | 1.5625
1.5 | 44.8 | 2.2321
2 | 38.3 | 2.611
3 | 27.1 | 3.69
5 | 17.9 | 5.5866
8 | 11.8 | 8.4746
10 | 9.6 | 10.4167
12 | 8.16 | 12.2549
24 | 4.32 | 23.1481
GNB Marathon M FT M12V190FT
Ref (Ah): | 190
Ref (DegC): | 20oC
Ref (V/Cell): | 1.8V
Time (Hours) | Current (1.85V per cell 20oC) | Kt (1.85V per cell 20oC)
0
0.05 | 382 | 0.49738
0.083333 | 350 | 0.54286
0.16667 | 293 | 0.64846
0.25 | 253 | 0.75099
0.5 | 178 | 1.0674
1 | 122 | 1.5574
1.5 | 92 | 2.0652
2 | 70 | 2.7143
3 | 49.3 | 3.854
5 | 32.4 | 5.8642
8 | 22 | 8.6364
10 | 18.3 | 10.3825
12 | 15.6 | 12.1795
24 | 8.44 | 22.5118

## Calculations (hidden)
NOTE: Column A must be sorted in ascending order!
Monobloc Data |  | Duty Summary |  |  | IEEE 485 Calculation Method (Kt: 1.85V/Cell @ 20degC) | [6 empty] | Switchgear Tripping & Closing
Monobloc Types | Ah Capacity | Description | Current A1…A8 (amps) | Duration M1 ..M8 (hours) | Period | Load (A) | Change in Load (A) | Duration of Period (hours) | Time to end of section (hours) | Capacity Rating Factor Kt | Required Section Size (Ah) | Maximum Tripping Burden (Watts) | Maximum Tripping Duration (hours) | Maximum Closing Burden (Watts) | Maximum Closing Duration (Hours)
Enersys Powersafe EON SBS 170F | 170 | Period 1 | 4.2042 | 24 | Period 1 | [6 empty] | 2100 | 0.06 | 600 | 49
Enersys Powersafe EON SBS B14F | 61.7 | Period 2 | 25.2252 | 1.6667e-05 | 1 | 4.2042 | 4.2042 | 24 | 24 | 23.1481 | 97.3195 | 0 | 0.06 | 0 | 0
Enersys Powersafe EON SBS C11F | 91.5 | Period 3 | 10.2102 | 0.013611 | [5 empty] | Total (1) | 97.3195 | 0 | 0.06 | 0 | 0
GNB Marathon M FT M12V100FT | 100 | Period 4 | 0 | 0 | Period 2 | [6 empty] | 2100 | 1.6667e-05 | 600 | 0.013611
GNB Marathon M FT M12V190FT | 190 | Period 5 | 0 | 0 | 1 | 4.2042 | 4.2042 | 24 | 24 | 23.1481 | 97.3195
GNB Marathon M FT M12V60FT | 59 | Period 6 | 0 | 0 | 2 | 25.2252 | 21.021 | 1.6667e-05 | 1.6667e-05 | 0.37736 | 7.9325
|  | Period 7 | 0 | 0 | [5 empty] | Total (2) | 105.252
|  | Period 8 | 0 | 0 | Period 3
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[10 empty] | Total (3) | 101.4942
Period 4
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[5 empty] | 4 | 10.2102 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (4) | 101.4942
Period 5
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[5 empty] | 4 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 10.2102 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (5) | 101.4942
Period 6
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[5 empty] | 4 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 10.2102 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (6) | 101.4942
Period 7
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[5 empty] | 4 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 10.2102 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (7) | 101.4942
Period 8
[5 empty] | 1 | 4.2042 | 4.2042 | 24 | 24.0136 | 23.602 | 99.2278
[5 empty] | 2 | 25.2252 | 21.021 | 1.6667e-05 | 0.013628 | 0.37736 | 7.9325
[5 empty] | 3 | 10.2102 | -15.015 | 0.013611 | 0.013611 | 0.37736 | -5.666
[5 empty] | 4 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 5 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 6 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 7 | 10.2102 | 0 | 0 | 0 | 0 | 0
[5 empty] | 8 | 10.2102 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total (8) | 101.4942