## Harmonic calculation sheet
Rating (3ph)
| Converter Rating | > 75A / 50kW | Continue with below process
* | Point of Common Coupling (PCC) | LV
* | Type of converter | Active infeed converter
* | Rating of Charger | 135 | kVA
|  | LV PCC |  | HV PCC
* | Required fault level | 7.0312 | MVA | 12.0357 | MVA
* | Add a three phase dummy motor into WinDebut (at the PCC) and run a load flow.
(rating and starting method of motor are irrelevant)
* | Source Impedance (LV 3-ph Ω ) | 0.07314 | R | 0.09242 | X | 0.11786 | Z
| Fault level at PCC (LV 3-ph) | 1.3575 | MVA
Analyse a balanced three phase fault at the PCC within DINIS and enter the current flow in the
below cell
| Fault Current | 6500 | A | Fault Power | 74.305 | MVA
| Nominal Voltage | 6600 | V
For more advice, please contact you regional Power Quality expert.
SWest = Simon Scarbro. WM - Mark Hallam. EM = Wayne Oxborough
Note - Calculation is based on ENA EREC G5/5 using circuit power levels detailed within Table 19 and 21

## Sheet2 (hidden)
< 75A | Follow SD6J process
> 75A | Continue with below process
reference | LV | HV
6 | 22 | 76
12 | 77 | 287
active infeed | 192 | 673
front page | Active infeed converter
used | 192 | 673