## Heat Pump Determination
Power Quality - Harmonics
| Power of Device | 10 | (kVA)
* | Manufacturer states Heat Pump System meets technical requirements of EN/IEC 61000-3-2? | Yes | Proceed to Flicker questions
* | Manufacturer states Heat Pump System complying with EN/IEC 61000-3-12? | No
* | Manufacturer states Heat Pump System complies with EN/IEC 61000-3-12 provided that the short-circuit power Ssc is greater than or equal to xx. | Yes | Enter fault level value provided by manufacturer into Cell D11
| 3-phase supply short circuit level, Ssc, required to allow connection under EN 61000-3-12 | 5000 | (kVA)
| Rsce | 500
| Power Quality - Flicker |  | Proceed to Flicker questions
* | Manufacturer states Heat Pump System meets technical requirements of EN/IEC 61000-3-3? | Yes | Proceed to Impedance Calculator
* | Manufacturer states Heat Pump System complying with EN/IEC 61000-3-11 provided that the source impedance is no more than Zmax? | No
| Z Max provided by manufacturer | 0.05 | Ω
Proceed to Impedance Calculator
* | Manufacturer states Heat Pump System complying with BS EN/IEC 61000-3-11 provided that service current capacity ≥100A per phase? | No
| Configuration of Heat Pump | Single phase

## Impedance Calculator
Impedance calculator for equipment compliant with BSEN 61000 - 3 - 12 (Rsce=33)
Rating of Three phase EV charger (kVA) | Quantity | Short circuit power (MVA)
50 | 0 | 0.11255
Known EV fault level requirement (kVA) |  | Impedance at PCC (Ohms)
0 |  | Three Phase
1.4216
Rating of Single phase HP (kVA) | Quantity
Impedance at Cutout (Ohms)(2)
10 | 1
0.47
Rating of three phase HP (kVA) | Quantity
10 | 0
Notes;
(1) - Cells to be used for the installation of chargers with different rating / capacity
(2) - Impedance is based on phase configuration as per answered questions within Heat Pump Determination chart
Minimum short circuit ratio factor for EV | Sum
29.05 | 1
Summation exponent for EV | Summation exponent for HP
2 | 2
Minimum short circuit ratio factor for HP
33
EV Short circuit power (three ph)
0
Known EV short circuit power
0
HP Short circuit power 1 ph
112553
HP Short circuit power 3 phase
0
Combined Short circuit power (three ph)
112553
(3) - Both Impedance requirements must be satisfied

## Sheet1 (hidden)
| Harmonics | Fault level |  | Flicker | from other sheet
61000-3-2 | 1 |  | 61000-3-3 | 1
61000-3-12 | 0 |  | Zmax | 0 | 0.05
Ssc | 1 |  | >100A | 0 | 0.3536
required F/L | 112553 |  |  | 0.47