|  |
| --- |
| **Form B2-1 Power Generating Module Document for Type B Power Generating Modules****Compliance Statement** This document shall be completed by the **Generator**.Note: For phased installations reference to **PGM** in this form should be read as reference to **Generating Unit**s.and theproject phase noted.  |
| **Power Generating Module (PGM)****PGM Name:****Compliance Contact** (name/tel/email)**:** | **Distribution Network Operator (DNO)**:**DNO Name**: ABC electricity distribution**Compliance Contact** (name/tel/email): |
| **Key to Submission Stage****A – Application:** Submission of the Standard Application Form. **E – Energisation:** Documentation required prior to Energisation.**IS – Initial Submission:** The programme of initial compliance document submission to be agreed between the **Generator** and the **DNO** as soon as possible after acceptance of a Connection Offer. The **Power Generating Module Document** shall be completed as agreed in accordance with paragraph 17.2.2 at least 28 days before the **Generator** wishes to synchronise its **Power Generating Module** for the first time.**FONS – Final Operational Notification Submission:** The **Generator** shall submit post energisation verification test documents within 28 days of synchronising in accordance with paragraph 17.4.2 to obtain **Final Operational Notification** from the **DNO**. |
| **Key to evidence requested**S - Indicates that **DNO** would expect to see the results of a simulation studyP - **Generating Unit** or **Power Generating Module** design dataMI - **Manufacturers’ Information**, generic data or test results as appropriateD - Copies of correspondence or other documents confirming that a requirement has been metT - Indicates that the **DNO** would expect to see results of, and/or witness, tests or monitoring which demonstrates complianceTV - Indicates Type Test reports (if **Generator** pursues this compliance option) | **Key to Compliance**Y = Yes (Compliant), O = Outstanding (outstanding submission)UR= Unresolved issueN = No (Non-Compliant) |
| Note that second part of this form is split into two Parts, the Part 1 is applicable to **Synchronous Power Generating Module**s, Part 2 is applicable to **Power Park Module**s |
| Issue | Date of Issue | Compliance Declaration Signatory Name | Compliance Declaration Signature | Issue Notes |
| Issue # | DD/MM/YY |  | I declare that the details provided in this issue of this **Power Generating Module Document** comply with the requirements of G99  | Insert brief description of amendment |
| 1 |  |  |  |  |
|  |  |  |  |  |
|  |  |  |  |  |
| Final Issue Prior to **FON** |  |  |  |  |
| **Details of Power Generating Module** |
| Connection Voltage |  |
| **Registered Capacity** |  |
| **Manufacturer** / Reference |  |
| Technology Type |  |

|  |  |
| --- | --- |
| **Form B2-1 Part 1 - Compliance Requirements for Synchronous Power Generating Modules** | **Response** |
| **G99 Reference** | **Compliance Requirement of the Power Generating Module** | **Submission Stage** | **Evidence Requested (and / or)** | **Compliance****Y, O, UR, N** | **Generator’s Statement***(Provide document references with any additional comments)* |
| 17.2.1,17.2.3,17.4.1 | Confirmation that a completed Standard Application Form has been submitted to the **DNO**  | A, IS, FONS | P, MI, D |  |  |
| 14.3 | Site Responsibility Schedule | E | D |  |  |
| 9.4.2 | **Power Quality – Voltage fluctuations and Flicker**: The installation shall be designed in accordance with EREC P28 | IS | MI, D, TV |  |  |
| 9.4.3 | **Power Quality – Harmonics**: The installation shall be designed in accordance with EREC G5 | IS | MI, D, TV |  |  |
| 12.5 | **Reactive Power capability**Confirm compliance with Section 12.5 by carrying out simulation study in accordance with B.4.2 and by submission of a report | IS | S, MI, TV |  |  |
| 12.2 | Confirm that the plant and apparatus is able of continue to operate during frequency ranges and to withstand the rate of change of frequency specified in 12.2.1 and 12.2.2 | IS | MI, TV |  |  |
| 12.2.4 | **Limited Frequency Sensitive Mode – Over frequency**Confirm the compliance with 12.2.4 by carrying out simulation study in accordance with B.4.5 and by submission of a report | IS | S, TV |  |  |
| 12.1.3 | Confirm the **Active Power** set point can be adjusted in accordance with instructions issued by the **DNO**  | IS | MI, TV |  |  |
| 12.3 | **Fault Ride Through**Confirm the compliance with 12.3 by carrying out simulation study in accordance with B.4.4 and by submission of a report. Testing of **Fault Ride Through** is not required. | IS | MI, TV, S |  |  |
| Section10 and Form B2-2 | **Interface Protection:*** Over and under voltage protection
* Over and Under Frequency protection
* Loss of mains protection

Other protection:* Details of any special protection, eg Pole Slipping or islanding

As an alternative to demonstrating protection compliance with Section 10 using **Manufacturers’ Information** or type test reports, site tests can be undertaken at the time of commissioning the **Power Generating Module** | IS, FONS | MI, TV, T |  |  |
| 12.2 | **Frequency Response Tests** Confirm the **Synchronous Power Generating Module** meets the requirements of 12.2 by testing in accordance with B.5.2 | FONS | T, MI, TV |  |  |
| 12.2.4 | **Output Power with falling frequency**Confirm the **Synchronous Power Generating Module** meets the requirements of 12.2.3 by testing in accordance with B.5.3 | FONS | T, MI, TV |  |  |
| 10.3.3 | **Automatic reconnection**Confirm by testing that the reconnection sequence starts after a minimum delay of 20 s for restoration of voltage and frequency in accordance with paragraph 10.3.3 | FONS | T, MI, TV |  |  |
| B3 | Installation and Commissioning Form B3 completed with signed acceptance from the **DNO** representative | FONS | D |  |  |

|  |  |
| --- | --- |
| **Form B2-1 Part 2 - Compliance Requirements for Power Park Module** | **Response** |
| **G99 Reference** | **Compliance Requirement of the Power Generating Module** | **Submission Stage** | **Evidence Requested (and / or)** | **Compliance****Y, O, UR, N,** | **Generator’s Statement***(Provide document references with any additional comments)* |
| 17.2.1,17.2.3,17.4.1 | Confirmation that a completed Standard Application Form has been submitted to the **DNO**  | A, IS, FONS | P, MI, D |  |  |
| 14.3 | Site Responsibility Schedule | E | D |  |  |
| 9.4.2 | **Power Quality – Voltage fluctuations and Flicker**: The installation shall be designed in accordance with EREC P28. | IS | MI, D, TV |  |  |
| 9.4.3 | **Power Quality – Harmonics**: The installation shall be designed in accordance with EREC G5 | IS | MI, D, TV |  |  |
| 12.5 | **Reactive Power capability**Confirm compliance with Section 12.5 by carrying out simulation study in accordance with B.4.2 and by submission of a report | IS | S, MI, TV |  |  |
| 12.2.4 | **Limited Frequency Sensitive Mode – Over frequency**Confirm the compliance with 12.2.4 by carrying out simulation study in accordance with B.4.5 and by submission of a report | IS | S, MI, TV |  |  |
| 12.2 | Confirm that the plant and apparatus is able of continue to operate during frequency ranges and to withstand the rate of change of frequency specified in 12.2.1 and 12.2.2 | IS | MI, TV |  |  |
| 12.1.3 | Confirm the **Active Power** set point can be adjusted in accordance with instructions issued by the **DNO**  | IS | MI, TV |  |  |
| 12.3 and 12.6 | **Fault Ride Through and Fast Fault Current Injection**Confirm the compliance with 12.3 and 12.6 by carrying out simulation study in accordance with B.4.4 and by submission of a report. Testing of **Fault Ride Through** is not required. | IS | MI, TV, S |  |  |
| Section 10 and Form B2-2 | **Interface Protection:*** Over and under voltage protection
* Over and Under Frequency protection
* Loss of mains protection

Other protection:* Details of any special protection, eg Pole Slipping or islanding

As an alternative to demonstrating protection compliance with Section 10 using **Manufacturers’ Information** or type test reports, site tests can be undertaken at the time of commissioning the **Power Generating Module** | IS, FONS | MI, TV, T |  |  |
| 12.2 | **Frequency Response Test** Confirm the **Power Park Module** meets the requirements of 12.2 by testing in accordance with B.6.2 | FONS | T, MI, TV |  |  |
| 10.3.3 | **Automatic reconnection**Confirm by testing that the reconnection sequence starts after a minimum delay of 20 s for restoration of voltage and frequency in accordance with paragraph 10.3.3 | FONS | T, MI, TV |  |  |
| B.3 | Installation and Commissioning Form B3 completed with signed acceptance from the **DNO** representative | FONS | D |  |  |